## sel_2440
Device Name | SEL-2440
Connection Name | SEL-2440
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device Name | sel_2440
Device ID String | sel_2440
ip_address | 192.168.112.20
port | 502
Device Port (502 typical)
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address Off by One | Address | Address Original2 | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
SEL-2440 Digital Inputs | [16 empty] | sel_2440 | FALSE |  |  | 200 | 200 | 1000 | 20 | 1
Fuse Monitoring (IN208) |  |  | Discrete Input | [6 empty] | 391 | 392 |  | bool |  |  | fuse_monitoring | [11 empty] | /components/sel_2440 | fuse_monitoring | Yes
Surge Arrester (IN207) |  |  | Discrete Input |  |  |  |  | 1001 |  | 392 | 393 |  | bool |  |  | surge_arrester | [11 empty] | /components/sel_2440 | surge_arrester | Yes
Door Latch (IN206) |  |  | Discrete Input | [6 empty] | 393 | 394 |  | bool |  |  | door_latch | [11 empty] | /components/sel_2440 | door_latch | Yes
DC Disconnect Switch (IN205) |  |  | Discrete Input | [6 empty] | 394 | 395 |  | bool |  |  | disconnect_switch | [11 empty] | /components/sel_2440 | disconnect_switch | Yes
Spare DI 1 (IN204) |  |  | Discrete Input | [6 empty] | 395 | 396 |  | bool |  |  | spare_1 | [11 empty] | /components/sel_2440 | spare_1 | Yes
E-Stop (IN203) |  |  | Discrete Input | [6 empty] | 396 | 397 |  | bool |  |  | e_stop | [11 empty] | /components/sel_2440 | e_stop | Yes
Fire Relay (IN202) |  |  | Discrete Input | [6 empty] | 397 | 398 |  | bool |  |  | fire_relay | [11 empty] | /components/sel_2440 | fire_relay | Yes
Trouble Relay (IN201) |  |  | Discrete Input | [6 empty] | 398 | 399 |  | bool |  |  | trouble_relay | [11 empty] | /components/sel_2440 | trouble_relay | Yes
Heartbeat |  |  | Input Register | [6 empty] | 399 | 400 |  | uint16 |  |  | heartbeat | [11 empty] | /components/sel_2440 | heartbeat | Yes
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A6: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A15: Tony Olivo: Do not add rows below this line, the script will break
Note on A16: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B16: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D16: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E16: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F16: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G16: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H16: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J16: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on M16: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on N16: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on O16: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on P16: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on Q16: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on AA16: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AB16: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AC16: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AD16: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AE16: Tony Olivo: Yes/No whether to include in the client/server config
Note on AF16: Tony Olivo: For humans
Note on AG16: Tony Olivo: For humans
Note on AH16: Tony Olivo: Ranges are for humans only