## FLEXGEN_ESS Controller
Connection Name | FlexGen_ESS_Controller | FlexGen_ESS_Controller
Connection IP Address (if TCP) | 192.168.114.11 | 192.168.114.11
Connection Port (502 typical) | 502 | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Name2 | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | name3
High Speed | [12 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Life | life | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Control_Command | start_stop | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Word 1 |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
Run_mode | run_mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | Run Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid contand power AC, 8 = ongrid contant power DC
On/Off grid mode setting | on_off_grid_mode | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Power_Set_AC | active_power_setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Active_Set_AC | reactive_power_setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active_power_rising_slope | active_power_rising_slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | Yes | Active Power Rising Slope |  | /site/ess_hs
Active_power_droop_slope | active_power_droop_slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | Yes | Active Power Droop Slope |  | /site/ess_hs
Reactive_power_rising_slope | reactive_power_rising_slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | Yes | Reactive Power Rising Slope |  | /site/ess_hs
Reactive_power_droop_slope | reactive_power_droop_slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | Yes | Reactive Power Droop Slope |  | /site/ess_hs
life_signal | life_signal | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Q_charge | chargeable_energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_hs
Q_discharge | dischargeable_energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_hs
W_charge | chargeable_power | chargeable_power | Status | 1 | Input Register | kW |  | 10 | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_hs
W_discharge | dischargeable_power | dischargeable_power | Status | 1 | Input Register | kW |  | 10 | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_hs
System_state | system_state | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_hs
Stop | Stop | Stop | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Stop
Run | Run | Run | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | Run
Fault | Fault | Fault | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | Fault
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | Standby
Com_status | com_status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_hs |  | 0 = online 1 = offline
PCS Communication Offline | PCS Communication Offline | PCS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | PCS Communication Status
BMS Communication Offline | BMS Communication Offline | BMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | BMS Communication Status
EMMU Communication Offline | EMMU Communication Offline | EMMU Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | EMMU Communication Status
EMS Communication Offline | EMS Communication Offline | EMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | EMS Communication Status
PCS under power | pcs_under_power | pcs_under_power | Status | 1 | Input Register |  |  |  | 2008 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS Under Power |  | /site/ess_hs | 0 = normal, 1 = under power
PCS over power | pcs_over_power | pcs_over_power | Status | 1 | Input Register |  |  |  | 2009 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS Over Power |  | /site/ess_hs | 0 = normal, 1 = over power
Uinab_RMS | voltage_l1_l2 | voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_hs
Uinbc_RMS | voltage_l2_l3 | voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_hs
Uinca_RMS | voltage_l3_l1 | voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_hs
Iina_RMS | current_l1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2033 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_hs
Iinb_RMS | current_l2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2034 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_hs
Iinc_RMS | current_l3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2035 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_hs
Frequency | frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2036 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_hs
Active Power | active_power | active_power | Status | 1 | Input Register | kW |  | 10 | 2037 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_hs
Reactive Power | reactive_power | reactive_power | Status | 1 | Input Register | kVar |  | 10 | 2038 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_hs
Power Factor | pf | pf | Status | 1 | Input Register |  |  | 1000 | 2039 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_hs
Ubtra_Ever | voltage_dc | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2040 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_hs
Ibtra_Ever | current_dc | current_dc | Status | 1 | Input Register | A |  | 10 | 2041 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_hs
Pbtra | active_power_dc | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2042 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_hs
Low Speed | [12 empty] | TRUE | life_signal | 200 | life | 1000 | 58 | 10 | ess_ls | yes
PCS_Mode | pcs_mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2043 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) | On-grid constant current (CC) | On-grid constant current (CC) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) | On-grid constant voltage (CV) | On-grid constant voltage (CV) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) | On-grid constant power (AC) | On-grid constant power (AC) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) | On-grid constant power (DC) | On-grid constant power (DC) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode | On-grid Mode | On-grid Mode | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode | Off-grid Mode | Off-grid Mode | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS_State1 | pcs_state | pcs_state | Status | 1 | Input Register |  | 2 |  | 2044 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Overall Work State |  | /site/ess_ls | Refer to PCS Instructions
Running | Running | Running | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Key stop | Key stop | Key stop | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Emergency stop | Emergency stop | Emergency stop | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Start in process | Start in process | Start in process | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop in process | Stop in process | Stop in process | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Fault stop | Fault stop | Fault stop | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Alarm running | Alarm running | Alarm running | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Derating running | Derating running | Derating running | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
DSP communication error | DSP communication error | DSP communication error | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS_State2 | pcs_state2 | pcs_state2 | Status | 1 | Input Register |  |  |  | 2046 | bitfield | 0 | 65535 | [8 empty] | Yes | Overall Charging/Discharging State |  | /site/ess_ls
Charging | Charging | Charging | Status | 1 | Input Register |  |  |  | 2046 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Charging
Discharging | Discharging | Discharging | Status | 1 | Input Register |  |  |  | 2046 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Discharging
Non-operating mode | Non-operating mode | Non-operating mode | Status | 1 | Input Register |  |  |  | 2046 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Non-operating mode
Overall_Fault | faults | faults | Status | 1 | Input Register |  |  |  | 2047 | bitfield | 0 | 65535 | [8 empty] | Yes | Fault Status |  | /site/ess_ls |  | 0 = normal, 1 = fault
Smoke Alarm | Smoke Alarm | Smoke Alarm | Status | 1 | Input Register |  |  |  | 2047 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Smoke Alarm
Door Open Protection | Door Open Protection | Door Open Protection | Status | 1 | Input Register |  |  |  | 2047 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Door Open Protection | 0 = disable, 1 = enable
Overall_Alarm | alarms | alarms | Status | 1 | Input Register |  | 2 |  | 2048 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Alarm Status |  | /site/ess_ls
Temperature & Humidity Board Communication Error | Temperature & Humidity Board Communication Error | Temperature & Humidity Board Communication Error | Status | 1 | Input Register |  |  |  | 2048 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Temperature & Humidity Board Communication Error | 0 = normal 1 = alarm
Switch Board Communication Error | Switch Board Communication Error | Switch Board Communication Error | Status | 1 | Input Register |  |  |  | 2048 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Switch Board Communication Error
Tributary Board Communication Error | Tributary Board Communication Error | Tributary Board Communication Error | Status | 1 | Input Register |  |  |  | 2048 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Tributary Board Communication Error
Overall Maximum charging power limit | overall_maximum_charging_power_limit | overall_maximum_charging_power_limit | Status | 1 | Input Register | kW |  | 10 | 2050 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Maximum Charging Power Limit |  | /site/ess_ls
Overall Maximum discharging power limit | overall_maximum_discharging_power_limit | overall_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  | 10 | 2051 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Maximum Discharging Power Limit |  | /site/ess_ls
Unit1_Uinab_RMS | pcs1_voltage_l1_l2 | pcs1_voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2070 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 AB Line Voltage |  | /site/ess_ls
Unit1_Uinbc_RMS | pcs1_voltage_l2_l3 | pcs1_voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2071 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 BC Line Voltage |  | /site/ess_ls
Unit1_Uinca_RMS | pcs1_voltage_l3_l1 | pcs1_voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2072 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 CA Line Voltage |  | /site/ess_ls
Unit1_Iina_RMS | pcs1_current_l1 | pcs1_current_l1 | Status | 1 | Input Register | A |  | 10 | 2073 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 A Line Current |  | /site/ess_ls
Unit1_Iinb_RMS | pcs1_current_l2 | pcs1_current_l2 | Status | 1 | Input Register | A |  | 10 | 2074 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 B Line Current |  | /site/ess_ls
Unit1_Iinc_RMS | pcs1_current_l3 | pcs1_current_l3 | Status | 1 | Input Register | A |  | 10 | 2075 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 C Line Current |  | /site/ess_ls
Unit1_P | pcs1_active_power | pcs1_active_power | Status | 1 | Input Register | kW | 2 | 10 | 2076-2077 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 1 AC Active Power |  | /site/ess_ls
Unit1_Q | psc1_reactive_power | psc1_reactive_power | Status | 1 | Input Register | kVar | 2 | 10 | 2078-2079 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 1 AC Reactive Power |  | /site/ess_ls
Unit1_Ubtra_Ever | pcs1_voltage_dc | pcs1_voltage_dc | Status | 1 | Input Register | V |  | 10 | 2080 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Voltage |  | /site/ess_ls
Unit1_Ibtra_Ever | pcs1_current_dc | pcs1_current_dc | Status | 1 | Input Register | A |  | 10 | 2081 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Current |  | /site/ess_ls
Unit1_Pbtra | pcs1_active_power_dc | pcs1_active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2082 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Active Power |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarm | pcs1_alarm | Status | 1 | Input Register |  | 2 |  | 2083 | bitfield | 0 | 65535 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
AC Switch Abnormal | AC Switch Abnormal | AC Switch Abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fan 2 abnormal | Fan 2 abnormal | Fan 2 abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
AC main contactor abnormal | AC main contactor abnormal | AC main contactor abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
IO-LCD comm error | IO-LCD comm error | IO-LCD comm error | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Temp abnormal | Temp abnormal | Temp abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
GFRT Running | GFRT Running | GFRT Running | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
DC fuse abnormal | DC fuse abnormal | DC fuse abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
DC sensor abnormal | DC sensor abnormal | DC sensor abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
DC SPD alarm | DC SPD alarm | DC SPD alarm | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
AC SPD alarm | AC SPD alarm | AC SPD alarm | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Chargine condition not met | Chargine condition not met | Chargine condition not met | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Discharging condition not met | Discharging condition not met | Discharging condition not met | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
DC switch abnormal | DC switch abnormal | DC switch abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Fan 1 Abnormal | Fan 1 Abnormal | Fan 1 Abnormal | Status | 1 | Input Register |  |  |  | 2083 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults | pcs1_faults | Status | 1 | Input Register |  | 4 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
Insulation Resistance | Insulation Resistance | Insulation Resistance | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
AC SPD Fault | AC SPD Fault | AC SPD Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Sampling Fault | Sampling Fault | Sampling Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery polarity reversed | Battery polarity reversed | Battery polarity reversed | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
LCD_DSP fault | LCD_DSP fault | LCD_DSP fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
AC current unbalanced | AC current unbalanced | AC current unbalanced | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Host Fault | Host Fault | Host Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
DC SPD Fault | DC SPD Fault | DC SPD Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
DC Injection Fault | DC Injection Fault | DC Injection Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
DC Switch Fault | DC Switch Fault | DC Switch Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Device code repeat fault | Device code repeat fault | Device code repeat fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Parallel communication error | Parallel communication error | Parallel communication error | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
PCS Control cabinet temperature abnormal | PCS Control cabinet temperature abnormal | PCS Control cabinet temperature abnormal | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
AC voltage unbalanced | AC voltage unbalanced | AC voltage unbalanced | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
AC switch fault | AC switch fault | AC switch fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Soft Start Fault | Soft Start Fault | Soft Start Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
DC Voltage sampling fault | DC Voltage sampling fault | DC Voltage sampling fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Fan 2 fault | Fan 2 fault | Fan 2 fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
AC current unbalanced 2 | AC current unbalanced 2 | AC current unbalanced 2 | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
AC current unbalanced 3 | AC current unbalanced 3 | AC current unbalanced 3 | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Drive board fault | Drive board fault | Drive board fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Neutral point potential shift | Neutral point potential shift | Neutral point potential shift | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Carier sync fault | Carier sync fault | Carier sync fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
DC undervoltage | DC undervoltage | DC undervoltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 32 | /site/ess_ls
DC overvoltage | DC overvoltage | DC overvoltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 33 | /site/ess_ls
AC undervoltage | AC undervoltage | AC undervoltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 34 | /site/ess_ls
AC overvoltage | AC overvoltage | AC overvoltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 35 | /site/ess_ls
AC underfrequency | AC underfrequency | AC underfrequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 36 | /site/ess_ls
AC overfrequency | AC overfrequency | AC overfrequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 37 | /site/ess_ls
AC contactor fault | AC contactor fault | AC contactor fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 38 | /site/ess_ls
Islanding portection | Islanding portection | Islanding portection | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 39 | /site/ess_ls
PDP protection | PDP protection | PDP protection | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 41 | /site/ess_ls
Module overtemperature | Module overtemperature | Module overtemperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 42 | /site/ess_ls
Reactor overtemperature | Reactor overtemperature | Reactor overtemperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 43 | /site/ess_ls
Transformer overtemperature | Transformer overtemperature | Transformer overtemperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 44 | /site/ess_ls
Leakage current | Leakage current | Leakage current | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 45 | /site/ess_ls
Overload protection | Overload protection | Overload protection | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 47 | /site/ess_ls
Fan 1 Fault | Fan 1 Fault | Fan 1 Fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 49 | /site/ess_ls
DC fuse fault | DC fuse fault | DC fuse fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 50 | /site/ess_ls
DC overcurrent | DC overcurrent | DC overcurrent | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 52 | /site/ess_ls
AC overcurrent | AC overcurrent | AC overcurrent | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 53 | /site/ess_ls
Ambient temperature abnormal | Ambient temperature abnormal | Ambient temperature abnormal | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 55 | /site/ess_ls
Hardware fault | Hardware fault | Hardware fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 56 | /site/ess_ls
Maximum charging power limit Unit1 | maximum_charging_power_limit_pcs1 | maximum_charging_power_limit_pcs1 | Status | 1 | Input Register | kW |  | 10 | 2089 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 Maximum Charging Power Limit |  | /site/ess_ls
Maximum discharging power limit Unit1 | maximum_discharging_power_limit_pcs1 | maximum_discharging_power_limit_pcs1 | Status | 1 | Input Register | kW |  | 10 | 2090 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 Maximum Discharging Power Limit |  | /site/ess_ls
Unit2_Uinab_RMS | pcs2_voltage_l1_l2 | pcs2_voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2100 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 2 AB Line Voltage |  | /site/ess_ls
Unit2_Uinbc_RMS | pcs2_voltage_l2_l3 | pcs2_voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2101 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 2 BC Line Voltage |  | /site/ess_ls
Unit2_Uinca_RMS | pcs2_voltage_l3_l1 | pcs2_voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2102 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 2 CA Line Voltage |  | /site/ess_ls
Unit2_Iina_RMS | pcs2_current_l1 | pcs2_current_l1 | Status | 1 | Input Register | A |  | 10 | 2103 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 2 A Line Current |  | /site/ess_ls
Unit2_Iinb_RMS | pcs2_current_l2 | pcs2_current_l2 | Status | 1 | Input Register | A |  | 10 | 2104 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 2 B Line Current |  | /site/ess_ls
Unit2_Iinc_RMS | pcs2_current_l3 | pcs2_current_l3 | Status | 1 | Input Register | A |  | 10 | 2105 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 2 C Line Current |  | /site/ess_ls
Unit2_P | pcs2_active_power | pcs2_active_power | Status | 1 | Input Register | kW | 2 | 10 | 2106-2107 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 2 AC Active Power |  | /site/ess_ls
Unit2_Q | pcs2_reactive_power | pcs2_reactive_power | Status | 1 | Input Register | kVar | 2 | 10 | 2108-2109 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 2 AC Reactive Power |  | /site/ess_ls
Unit2_Ubtra_Ever | pcs2_voltage_dc | pcs2_voltage_dc | Status | 1 | Input Register | V |  | 10 | 2110 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 2 DC Voltage |  | /site/ess_ls
Unit2_Ibtra_Ever | pcs2_current_dc | pcs2_current_dc | Status | 1 | Input Register | A |  | 10 | 2111 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 2 DC Current |  | /site/ess_ls
Unit2_Pbtra | pcs2_active_power_dc | pcs2_active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2112 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 2 DC Active Power |  | /site/ess_ls
Unit2_Alarm_state1 | pcs2_alarms | pcs2_alarms | Status | 1 | Input Register |  | 2 |  | 2113 | bitfield | 0 | 65535 | [8 empty] | Yes | PCS 2 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
AC Switch Abnormal | AC Switch Abnormal | AC Switch Abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fan 2 abnormal | Fan 2 abnormal | Fan 2 abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
AC main contactor abnormal | AC main contactor abnormal | AC main contactor abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
IO-LCD comm error | IO-LCD comm error | IO-LCD comm error | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Temp abnormal | Temp abnormal | Temp abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
GFRT Running | GFRT Running | GFRT Running | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
DC fuse abnormal | DC fuse abnormal | DC fuse abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
DC sensor abnormal | DC sensor abnormal | DC sensor abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
DC SPD alarm | DC SPD alarm | DC SPD alarm | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
AC SPD alarm | AC SPD alarm | AC SPD alarm | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Chargine condition not met | Chargine condition not met | Chargine condition not met | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Discharging condition not met | Discharging condition not met | Discharging condition not met | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
DC switch abnormal | DC switch abnormal | DC switch abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Fan 1 Abnormal | Fan 1 Abnormal | Fan 1 Abnormal | Status | 1 | Input Register |  |  |  | 2113 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
Unit2_Fault_state1 | pcs2_faults | pcs2_faults | Status | 1 | Input Register |  | 4 |  | 2115 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 2 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
Insulation Resistance | Insulation Resistance | Insulation Resistance | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
AC SPD Fault | AC SPD Fault | AC SPD Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Sampling Fault | Sampling Fault | Sampling Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery polarity reversed | Battery polarity reversed | Battery polarity reversed | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
LCD_DSP fault | LCD_DSP fault | LCD_DSP fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
AC current unbalanced | AC current unbalanced | AC current unbalanced | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Host Fault | Host Fault | Host Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
DC SPD Fault | DC SPD Fault | DC SPD Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
DC Injection Fault | DC Injection Fault | DC Injection Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
DC Switch Fault | DC Switch Fault | DC Switch Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Device code repeat fault | Device code repeat fault | Device code repeat fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Parallel communication error | Parallel communication error | Parallel communication error | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
PCS Control cabinet temperature abnormal | PCS Control cabinet temperature abnormal | PCS Control cabinet temperature abnormal | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
AC voltage unbalanced | AC voltage unbalanced | AC voltage unbalanced | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
AC switch fault | AC switch fault | AC switch fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Soft Start Fault | Soft Start Fault | Soft Start Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
DC Voltage sampling fault | DC Voltage sampling fault | DC Voltage sampling fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Fan 2 fault | Fan 2 fault | Fan 2 fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
AC current unbalanced 2 | AC current unbalanced 2 | AC current unbalanced 2 | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
AC current unbalanced 3 | AC current unbalanced 3 | AC current unbalanced 3 | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Drive board fault | Drive board fault | Drive board fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Neutral point potential shift | Neutral point potential shift | Neutral point potential shift | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Carier sync fault | Carier sync fault | Carier sync fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
DC undervoltage | DC undervoltage | DC undervoltage | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 32 | /site/ess_ls
DC overvoltage | DC overvoltage | DC overvoltage | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 33 | /site/ess_ls
AC undervoltage | AC undervoltage | AC undervoltage | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 34 | /site/ess_ls
AC overvoltage | AC overvoltage | AC overvoltage | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 35 | /site/ess_ls
AC underfrequency | AC underfrequency | AC underfrequency | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 36 | /site/ess_ls
AC overfrequency | AC overfrequency | AC overfrequency | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 37 | /site/ess_ls
AC contactor fault | AC contactor fault | AC contactor fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 38 | /site/ess_ls
Islanding portection | Islanding portection | Islanding portection | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 39 | /site/ess_ls
PDP protection | PDP protection | PDP protection | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 41 | /site/ess_ls
Module overtemperature | Module overtemperature | Module overtemperature | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 42 | /site/ess_ls
Reactor overtemperature | Reactor overtemperature | Reactor overtemperature | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 43 | /site/ess_ls
Transformer overtemperature | Transformer overtemperature | Transformer overtemperature | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 44 | /site/ess_ls
Leakage current | Leakage current | Leakage current | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 45 | /site/ess_ls
Overload protection | Overload protection | Overload protection | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 47 | /site/ess_ls
Fan 1 Fault | Fan 1 Fault | Fan 1 Fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 49 | /site/ess_ls
DC fuse fault | DC fuse fault | DC fuse fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 50 | /site/ess_ls
DC overcurrent | DC overcurrent | DC overcurrent | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 52 | /site/ess_ls
AC overcurrent | AC overcurrent | AC overcurrent | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 53 | /site/ess_ls
Ambient temperature abnormal | Ambient temperature abnormal | Ambient temperature abnormal | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 55 | /site/ess_ls
Hardware fault | Hardware fault | Hardware fault | Status | 1 | Input Register |  |  |  | 2115 | bit | [10 empty] | Yes |  | 56 | /site/ess_ls
Maximum charging power limit Unit2 | maximum_charging_power_limit_pcs2 | maximum_charging_power_limit_pcs2 | Status | 1 | Input Register | kW |  | 10 | 2119 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 2 Maximum Charging Power Limit |  | /site/ess_ls
Maximum discharging power limit Unit2 | maximum_discharging_power_limit_pcs2 | maximum_discharging_power_limit_pcs2 | Status | 1 | Input Register | kW |  | 10 | 2120 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 2 Maximum Discharging Power Limit |  | /site/ess_ls
BMS maximum cell voltage | bms_maximum_cell_voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2130 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
Stackindex of the BMS maximum cell voltage | stackindex_of_the_bms_maximum_cell_voltage | stackindex_of_the_bms_maximum_cell_voltage | Status | 1 | Input Register |  |  |  | 2131 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage BCMS Location |  | /site/ess_ls
Cluster index of the BMS maximum cell voltage | cluster_index_of_the_bms_maximum_cell_voltage | cluster_index_of_the_bms_maximum_cell_voltage | Status | 1 | Input Register |  |  |  | 2132 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage BMU Location |  | /site/ess_ls
BMS minimum cell voltage | bms_minimum_cell_voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2133 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
Stackindex of the BMS minimum cell voltage | stackindex_of_the_bms_minimum_cell_voltage | stackindex_of_the_bms_minimum_cell_voltage | Status | 1 | Input Register |  |  |  | 2134 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage BCMS Location |  | /site/ess_ls
Cluster index of the BMS minimum cell voltage | cluster_index_of_the_bms_minimum_cell_voltage | cluster_index_of_the_bms_minimum_cell_voltage | Status | 1 | Input Register |  |  |  | 2135 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage BMU Location |  | /site/ess_ls
BMS maximum cell temperature | bms_maximum_cell_temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2136 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
Stackindex of the BMS maximum cell temperature | stackindex_of_the_bms_maximum_cell_temperature | stackindex_of_the_bms_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2137 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature BCMS Location |  | /site/ess_ls
Cluster index of the BMS maximum cell temperature | cluster_index_of_the_bms_maximum_cell_temperature | cluster_index_of_the_bms_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2138 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature BMU Location |  | /site/ess_ls
BMS minimum cell temperature | bms_minimum_cell_temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2139 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
Stackindex of the BMS minimum cell temperature | stackindex_of_the_bms_minimum_cell_temperature | stackindex_of_the_bms_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2140 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature BCMS Location |  | /site/ess_ls
Cluster index of the BMS minimum cell temperature | cluster_index_of_the_bms_minimum_cell_temperature | cluster_index_of_the_bms_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2141 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature BMU Location |  | /site/ess_ls
BMS bus voltage | bms_bus_voltage | bms_bus_voltage | Status | 1 | Input Register | V |  | 10 | 2142 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Bus Voltage |  | /site/ess_ls
BMS bus current | bms_bus_current | bms_bus_current | Status | 1 | Input Register | A |  | 10 | 2143 | int16 | -32768 | 32767 | [8 empty] | Yes | BMS Bus Current |  | /site/ess_ls
BMS SOC | bms_soc | bms_soc | Status | 1 | Input Register | % |  | 10 | 2144 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS power | bms_power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2145 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
Operation status | operation_status | operation_status | Status | 1 | Input Register |  |  |  | 2146 | bitfield | 0 | 65535 | [8 empty] | Yes | Operation Status |  | /site/ess_ls
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2146 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Standby
Charging | Charging | Charging | Status | 1 | Input Register |  |  |  | 2146 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Charging
Discharging | Discharging | Discharging | Status | 1 | Input Register |  |  |  | 2146 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Discharging
BMS current rechargeable capacity | bms_current_chargeable_capacity | bms_current_chargeable_capacity | Status | 1 | Input Register | kWh | 2 | 1000 | 2149 | uint32 | 0 | 4294967295 | [8 empty] | Yes | BMS Rechargeable Capacity |  | /site/ess_ls
BMS current dischargeable capacity | bms_current_dischargeable_capacity | bms_current_dischargeable_capacity | Status | 1 | Input Register | kWh | 2 | 1000 | 2151 | uint32 | 0 | 4294967295 | [8 empty] | Yes | BMS Dischargeable Capacity |  | /site/ess_ls
Circuit breaker control word | circuit_breaker_control_word | circuit_breaker_control_word | Status | 1 | Input Register |  | 2 |  | 2153 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Circuit Breaker Control Word |  | /site/ess_ls | Each bit represents the circuit status of each battery cluster, 0 = Switch Off, 1 = Switch On
Main circuit breaker status | main_circuit_breaker_status | main_circuit_breaker_status | Status | 1 | Input Register |  |  |  | 2155 | uint16 | 0 | 65535 | [8 empty] | Yes | Main Circuit Breaker Status |  | /site/ess_ls | 0 = Switch Off, 1 = Switch On
Control circuit breaker | control_circuit_breaker | control_circuit_breaker | Status | 1 | Input Register |  |  |  | 2156 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Circuit Breaker Status |  | /site/ess_ls | 0 = Switch Off, 1 = Switch On
BMS Maximum charging power limit | bms_maximum_charging_power_limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2157 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2158 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Maximum Discharging Power Limit |  | /site/ess_ls
Power limit state | power_limit_state | power_limit_state | Status | 1 | Input Register |  | 4 |  | 2159 | bitfield | 0 | 1.8447e+19 | [8 empty] | Yes | Power Limit Status |  | /site/ess_ls
Charge overvoltage half power limit of cell | Charge overvoltage half power limit of cell | Charge overvoltage half power limit of cell | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Charge overvoltage half power limit of cluster | Charge overvoltage half power limit of cluster | Charge overvoltage half power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Charge under-temp half power limit | Charge under-temp half power limit | Charge under-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge over-temp half power limit | Charge over-temp half power limit | Charge over-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge undervoltage half power limit of cell | Discharge undervoltage half power limit of cell | Discharge undervoltage half power limit of cell | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Discharge undervoltage half power limit of cluster | Discharge undervoltage half power limit of cluster | Discharge undervoltage half power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Discharge under-temp half power limit | Discharge under-temp half power limit | Discharge under-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Discharge over-temp half power limit | Discharge over-temp half power limit | Discharge over-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Charge overvoltage zero power limit of cell | Charge overvoltage zero power limit of cell | Charge overvoltage zero power limit of cell | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 33 | /site/ess_ls
Charge overvoltage zero power limit of cluster | Charge overvoltage zero power limit of cluster | Charge overvoltage zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 34 | /site/ess_ls
Charge overcurrent zero power limit of cluster | Charge overcurrent zero power limit of cluster | Charge overcurrent zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 35 | /site/ess_ls
Charge overcurrent zero power limit of array | Charge overcurrent zero power limit of array | Charge overcurrent zero power limit of array | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 36 | /site/ess_ls
Charge under-temp zero power limit | Charge under-temp zero power limit | Charge under-temp zero power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 37 | /site/ess_ls
Charge over-temp zero power limit | Charge over-temp zero power limit | Charge over-temp zero power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 38 | /site/ess_ls
Discharge undervoltage zero power limit of cell | Discharge undervoltage zero power limit of cell | Discharge undervoltage zero power limit of cell | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 49 | /site/ess_ls
Discharge undervoltage zero power limit of cluster | Discharge undervoltage zero power limit of cluster | Discharge undervoltage zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 50 | /site/ess_ls
Discharge overcurrent zero power limit of cluster | Discharge overcurrent zero power limit of cluster | Discharge overcurrent zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 51 | /site/ess_ls
Discharge overcurrent zero power limit of array | Discharge overcurrent zero power limit of array | Discharge overcurrent zero power limit of array | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 52 | /site/ess_ls
Discharge under-temp zero power limit | Discharge under-temp zero power limit | Discharge under-temp zero power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 53 | /site/ess_ls
Discharge over-temp zero power limit | Discharge over-temp zero power limit | Discharge over-temp zero power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 54 | /site/ess_ls
BMS alarm state | bms_alarms | bms_alarms | Status | 1 | Input Register |  | 4 |  | 2163 | bitfield | 0 | 1.8447e+19 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Discharge undervoltage warning of cell | Discharge undervoltage warning of cell | Discharge undervoltage warning of cell | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Charge overvoltage warning of cell | Charge overvoltage warning of cell | Charge overvoltage warning of cell | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Discharge undervoltage warning of cluster | Discharge undervoltage warning of cluster | Discharge undervoltage warning of cluster | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge overvoltage warning of cluster | Charge overvoltage warning of cluster | Charge overvoltage warning of cluster | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge overcurrent warning of cluster | Discharge overcurrent warning of cluster | Discharge overcurrent warning of cluster | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Charge overcurrent warning of cluster | Charge overcurrent warning of cluster | Charge overcurrent warning of cluster | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Discharge overcurrent warning of array | Discharge overcurrent warning of array | Discharge overcurrent warning of array | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Charge overcurrent warning of array | Charge overcurrent warning of array | Charge overcurrent warning of array | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Low-temp warning | Low-temp warning | Low-temp warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
High-temp warning | High-temp warning | High-temp warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
High voltage-difference warning | High voltage-difference warning | High voltage-difference warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
High temp-difference warning | High temp-difference warning | High temp-difference warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS communication abnormal warning | PCS communication abnormal warning | PCS communication abnormal warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
BMU communication abnormal warning | BMU communication abnormal warning | BMU communication abnormal warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
BCMS communication abnormal warning | BCMS communication abnormal warning | BCMS communication abnormal warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
BAMS abnormal warning | BAMS abnormal warning | BAMS abnormal warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
BCMS abnormal warning | BCMS abnormal warning | BCMS abnormal warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
High SOC warning | High SOC warning | High SOC warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Low SOC warning | Low SOC warning | Low SOC warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
EMMU abnormal warning | EMMU abnormal warning | EMMU abnormal warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
BMS fault state | bms_faults | bms_faults | Status | 1 | Input Register |  | 4 |  | 2167 | bitfield | 0 | 1.8447e+19 | [8 empty] | Yes | BMS Fault Status |  | /site/ess_ls
Insulation error protection | Insulation error protection | Insulation error protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Discharge undervoltage LV1 protection of cell | Discharge undervoltage LV1 protection of cell | Discharge undervoltage LV1 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Charge overvoltage LV1 protection of cell | Charge overvoltage LV1 protection of cell | Charge overvoltage LV1 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Discharge undervoltage LV1 protection of cluster | Discharge undervoltage LV1 protection of cluster | Discharge undervoltage LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge overvoltage LV1 protection of cluster | Charge overvoltage LV1 protection of cluster | Charge overvoltage LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge overcurrent LV1 protection of cluster | Discharge overcurrent LV1 protection of cluster | Discharge overcurrent LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Charge overcurrent LV1 protection of cluster | Charge overcurrent LV1 protection of cluster | Charge overcurrent LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Discharge overcurrent LV1 protection of array | Discharge overcurrent LV1 protection of array | Discharge overcurrent LV1 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Charge overcurrent LV1 protection of array | Charge overcurrent LV1 protection of array | Charge overcurrent LV1 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Low-temp LV1 protection | Low-temp LV1 protection | Low-temp LV1 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
High-temp LV1 protection | High-temp LV1 protection | High-temp LV1 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Self-protection of BMS | Self-protection of BMS | Self-protection of BMS | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
E-stop fault | E-stop fault | E-stop fault | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Self-protection of EMMU | Self-protection of EMMU | Self-protection of EMMU | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Discharge undervoltage LV2 protection of cell | Discharge undervoltage LV2 protection of cell | Discharge undervoltage LV2 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 33 | /site/ess_ls
Charge overvoltage LV2 protection of cell | Charge overvoltage LV2 protection of cell | Charge overvoltage LV2 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 34 | /site/ess_ls
Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 35 | /site/ess_ls
Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 36 | /site/ess_ls
Discharge overcurrent LV2 protection of cluster | Discharge overcurrent LV2 protection of cluster | Discharge overcurrent LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 37 | /site/ess_ls
Charge overcurrent LV2 protection of cluster | Charge overcurrent LV2 protection of cluster | Charge overcurrent LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 38 | /site/ess_ls
Discharge overcurrent LV2 protection of array | Discharge overcurrent LV2 protection of array | Discharge overcurrent LV2 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 39 | /site/ess_ls
Charge overcurrent LV2 protection of array | Charge overcurrent LV2 protection of array | Charge overcurrent LV2 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 40 | /site/ess_ls
Low-temp LV2 protection | Low-temp LV2 protection | Low-temp LV2 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 41 | /site/ess_ls
High-temp LV2 protection | High-temp LV2 protection | High-temp LV2 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 42 | /site/ess_ls
Cluster No. 1 battery cluster voltage | cluster_no_1_battery_cluster_voltage | cluster_no_1_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Voltage |  | /site/ess_ls
Cluster No. 2 battery cluster voltage | cluster_no_2_battery_cluster_voltage | cluster_no_2_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Voltage |  | /site/ess_ls
Cluster No. 3 battery cluster voltage | cluster_no_3_battery_cluster_voltage | cluster_no_3_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Voltage |  | /site/ess_ls
Cluster No. 4 battery cluster voltage | cluster_no_4_battery_cluster_voltage | cluster_no_4_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2203 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Voltage |  | /site/ess_ls
Cluster No. 5 battery cluster voltage | cluster_no_5_battery_cluster_voltage | cluster_no_5_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2204 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Voltage |  | /site/ess_ls
Cluster No. 6 battery cluster voltage | cluster_no_6_battery_cluster_voltage | cluster_no_6_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2205 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Voltage |  | /site/ess_ls
Cluster No. 7 battery cluster voltage | cluster_no_7_battery_cluster_voltage | cluster_no_7_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Voltage |  | /site/ess_ls
Cluster No. 8 battery cluster voltage | cluster_no_8_battery_cluster_voltage | cluster_no_8_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Voltage |  | /site/ess_ls
Cluster No. 9 battery cluster voltage | cluster_no_9_battery_cluster_voltage | cluster_no_9_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Voltage |  | /site/ess_ls
Cluster No. 10 battery cluster voltage | cluster_no_10_battery_cluster_voltage | cluster_no_10_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2209 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Voltage |  | /site/ess_ls
Cluster No. 11 battery cluster voltage | cluster_no_11_battery_cluster_voltage | cluster_no_11_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2210 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Voltage |  | /site/ess_ls
Cluster No. 12 battery cluster voltage | cluster_no_12_battery_cluster_voltage | cluster_no_12_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2211 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Voltage |  | /site/ess_ls
Cluster No. 13 battery cluster voltage | cluster_no_13_battery_cluster_voltage | cluster_no_13_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2212 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Voltage |  | /site/ess_ls
Cluster No. 14 battery cluster voltage | cluster_no_14_battery_cluster_voltage | cluster_no_14_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2213 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Voltage |  | /site/ess_ls
Cluster No. 15 battery cluster voltage | cluster_no_15_battery_cluster_voltage | cluster_no_15_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Voltage |  | /site/ess_ls
Cluster No. 16 battery cluster voltage | cluster_no_16_battery_cluster_voltage | cluster_no_16_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2215 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Voltage |  | /site/ess_ls
Cluster No. 17 battery cluster voltage | cluster_no_17_battery_cluster_voltage | cluster_no_17_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2216 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Voltage |  | /site/ess_ls
Cluster No. 18 battery cluster voltage | cluster_no_18_battery_cluster_voltage | cluster_no_18_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2217 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Voltage |  | /site/ess_ls
Cluster No. 19 battery cluster voltage | cluster_no_19_battery_cluster_voltage | cluster_no_19_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2218 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Voltage |  | /site/ess_ls
Cluster No. 20 battery cluster voltage | cluster_no_20_battery_cluster_voltage | cluster_no_20_battery_cluster_voltage | Status | 1 | Input Register | V |  | 10 | 2219 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Voltage |  | /site/ess_ls
Cluster No. 1 battery cluster current | cluster_no_1_battery_cluster_current | cluster_no_1_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2220 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 1 Current |  | /site/ess_ls
Cluster No. 2 battery cluster current | cluster_no_2_battery_cluster_current | cluster_no_2_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2221 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 2 Current |  | /site/ess_ls
Cluster No. 3 battery cluster current | cluster_no_3_battery_cluster_current | cluster_no_3_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2222 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 3 Current |  | /site/ess_ls
Cluster No. 4 battery cluster current | cluster_no_4_battery_cluster_current | cluster_no_4_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2223 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 4 Current |  | /site/ess_ls
Cluster No. 5 battery cluster current | cluster_no_5_battery_cluster_current | cluster_no_5_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2224 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 5 Current |  | /site/ess_ls
Cluster No. 6 battery cluster current | cluster_no_6_battery_cluster_current | cluster_no_6_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2225 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 6 Current |  | /site/ess_ls
Cluster No. 7 battery cluster current | cluster_no_7_battery_cluster_current | cluster_no_7_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2226 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 7 Current |  | /site/ess_ls
Cluster No. 8 battery cluster current | cluster_no_8_battery_cluster_current | cluster_no_8_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2227 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 8 Current |  | /site/ess_ls
Cluster No. 9 battery cluster current | cluster_no_9_battery_cluster_current | cluster_no_9_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2228 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 9 Current |  | /site/ess_ls
Cluster No. 10 battery cluster current | cluster_no_10_battery_cluster_current | cluster_no_10_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2229 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 10 Current |  | /site/ess_ls
Cluster No. 11 battery cluster current | cluster_no_11_battery_cluster_current | cluster_no_11_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2230 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 11 Current |  | /site/ess_ls
Cluster No. 12 battery cluster current | cluster_no_12_battery_cluster_current | cluster_no_12_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2231 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 12 Current |  | /site/ess_ls
Cluster No. 13 battery cluster current | cluster_no_13_battery_cluster_current | cluster_no_13_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2232 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 13 Current |  | /site/ess_ls
Cluster No. 14 battery cluster current | cluster_no_14_battery_cluster_current | cluster_no_14_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2233 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 14 Current |  | /site/ess_ls
Cluster No. 15 battery cluster current | cluster_no_15_battery_cluster_current | cluster_no_15_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2234 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 15 Current |  | /site/ess_ls
Cluster No. 16 battery cluster current | cluster_no_16_battery_cluster_current | cluster_no_16_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2235 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 16 Current |  | /site/ess_ls
Cluster No. 17 battery cluster current | cluster_no_17_battery_cluster_current | cluster_no_17_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2236 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 17 Current |  | /site/ess_ls
Cluster No. 18 battery cluster current | cluster_no_18_battery_cluster_current | cluster_no_18_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2237 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 18 Current |  | /site/ess_ls
Cluster No. 19 battery cluster current | cluster_no_19_battery_cluster_current | cluster_no_19_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2238 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 19 Current |  | /site/ess_ls
Cluster No. 20 battery cluster current | cluster_no_20_battery_cluster_current | cluster_no_20_battery_cluster_current | Status | 1 | Input Register | A |  | 10 | 2239 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Cluster 20 Current |  | /site/ess_ls
Cluster No. 1 max cell voltage | cluster_no_1_max_cell_voltage | cluster_no_1_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2240 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 1 max cell voltage pack num. | cluster_no_1_max_cell_voltage_pack_num | cluster_no_1_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2241 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 2 max cell voltage | cluster_no_2_max_cell_voltage | cluster_no_2_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2242 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 2 max cell voltage pack num. | cluster_no_2_max_cell_voltage_pack_num | cluster_no_2_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2243 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 3 max cell voltage | cluster_no_3_max_cell_voltage | cluster_no_3_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2244 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 3 max cell voltage pack num. | cluster_no_3_max_cell_voltage_pack_num | cluster_no_3_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2245 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 4 max cell voltage | cluster_no_4_max_cell_voltage | cluster_no_4_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2246 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 4 max cell voltage pack num. | cluster_no_4_max_cell_voltage_pack_num | cluster_no_4_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2247 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 5 max cell voltage | cluster_no_5_max_cell_voltage | cluster_no_5_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2248 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 5 max cell voltage pack num. | cluster_no_5_max_cell_voltage_pack_num | cluster_no_5_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2249 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 6 max cell voltage | cluster_no_6_max_cell_voltage | cluster_no_6_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2250 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 6 max cell voltage pack num. | cluster_no_6_max_cell_voltage_pack_num | cluster_no_6_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2251 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 7 max cell voltage | cluster_no_7_max_cell_voltage | cluster_no_7_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2252 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 7 max cell voltage pack num. | cluster_no_7_max_cell_voltage_pack_num | cluster_no_7_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2253 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 8 max cell voltage | cluster_no_8_max_cell_voltage | cluster_no_8_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2254 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 8 max cell voltage pack num. | cluster_no_8_max_cell_voltage_pack_num | cluster_no_8_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2255 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 9 max cell voltage | cluster_no_9_max_cell_voltage | cluster_no_9_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2256 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 9 max cell voltage pack num. | cluster_no_9_max_cell_voltage_pack_num | cluster_no_9_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2257 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 10 max cell voltage | cluster_no_10_max_cell_voltage | cluster_no_10_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2258 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 10 max cell voltage pack num. | cluster_no_10_max_cell_voltage_pack_num | cluster_no_10_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2259 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 11 max cell voltage | cluster_no_11_max_cell_voltage | cluster_no_11_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2260 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 11 max cell voltage pack num. | cluster_no_11_max_cell_voltage_pack_num | cluster_no_11_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2261 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 12 max cell voltage | cluster_no_12_max_cell_voltage | cluster_no_12_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2262 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 12 max cell voltage pack num. | cluster_no_12_max_cell_voltage_pack_num | cluster_no_12_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2263 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 13 max cell voltage | cluster_no_13_max_cell_voltage | cluster_no_13_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2264 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 13 max cell voltage pack num. | cluster_no_13_max_cell_voltage_pack_num | cluster_no_13_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2265 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 14 max cell voltage | cluster_no_14_max_cell_voltage | cluster_no_14_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2266 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 14 max cell voltage pack num. | cluster_no_14_max_cell_voltage_pack_num | cluster_no_14_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2267 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 15 max cell voltage | cluster_no_15_max_cell_voltage | cluster_no_15_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2268 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 15 max cell voltage pack num. | cluster_no_15_max_cell_voltage_pack_num | cluster_no_15_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2269 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 16 max cell voltage | cluster_no_16_max_cell_voltage | cluster_no_16_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2270 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 16 max cell voltage pack num. | cluster_no_16_max_cell_voltage_pack_num | cluster_no_16_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2271 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 17 max cell voltage | cluster_no_17_max_cell_voltage | cluster_no_17_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2272 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 17 max cell voltage pack num. | cluster_no_17_max_cell_voltage_pack_num | cluster_no_17_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2273 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 18 max cell voltage | cluster_no_18_max_cell_voltage | cluster_no_18_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2274 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 18 max cell voltage pack num. | cluster_no_18_max_cell_voltage_pack_num | cluster_no_18_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2275 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 19 max cell voltage | cluster_no_19_max_cell_voltage | cluster_no_19_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2276 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 19 max cell voltage pack num. | cluster_no_19_max_cell_voltage_pack_num | cluster_no_19_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2277 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 20 max cell voltage | cluster_no_20_max_cell_voltage | cluster_no_20_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2278 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 20 max cell voltage pack num. | cluster_no_20_max_cell_voltage_pack_num | cluster_no_20_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2279 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 1 second max cell voltage | cluster_no_1_second_max_cell_voltage | cluster_no_1_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2280 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 1 second max cell voltage pack num. | cluster_no_1_second_max_cell_voltage_pack_num | cluster_no_1_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2281 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 2 second max cell voltage | cluster_no_2_second_max_cell_voltage | cluster_no_2_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2282 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 2 second max cell voltage pack num. | cluster_no_2_second_max_cell_voltage_pack_num | cluster_no_2_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2283 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 3 second max cell voltage | cluster_no_3_second_max_cell_voltage | cluster_no_3_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2284 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 3 second max cell voltage pack num. | cluster_no_3_second_max_cell_voltage_pack_num | cluster_no_3_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2285 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 4 second max cell voltage | cluster_no_4_second_max_cell_voltage | cluster_no_4_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2286 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 4 second max cell voltage pack num. | cluster_no_4_second_max_cell_voltage_pack_num | cluster_no_4_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2287 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 5 second max cell voltage | cluster_no_5_second_max_cell_voltage | cluster_no_5_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2288 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 5 second max cell voltage pack num. | cluster_no_5_second_max_cell_voltage_pack_num | cluster_no_5_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2289 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 6 second max cell voltage | cluster_no_6_second_max_cell_voltage | cluster_no_6_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2290 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 6 second max cell voltage pack num. | cluster_no_6_second_max_cell_voltage_pack_num | cluster_no_6_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2291 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 7 second max cell voltage | cluster_no_7_second_max_cell_voltage | cluster_no_7_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2292 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 7 second max cell voltage pack num. | cluster_no_7_second_max_cell_voltage_pack_num | cluster_no_7_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2293 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 8 second max cell voltage | cluster_no_8_second_max_cell_voltage | cluster_no_8_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2294 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 8 second max cell voltage pack num. | cluster_no_8_second_max_cell_voltage_pack_num | cluster_no_8_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2295 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 9 second max cell voltage | cluster_no_9_second_max_cell_voltage | cluster_no_9_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2296 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 9 second max cell voltage pack num. | cluster_no_9_second_max_cell_voltage_pack_num | cluster_no_9_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2297 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 10 second max cell voltage | cluster_no_10_second_max_cell_voltage | cluster_no_10_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2298 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 10 second max cell voltage pack num. | cluster_no_10_second_max_cell_voltage_pack_num | cluster_no_10_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2299 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 11 second max cell voltage | cluster_no_11_second_max_cell_voltage | cluster_no_11_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2300 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 11 second max cell voltage pack num. | cluster_no_11_second_max_cell_voltage_pack_num | cluster_no_11_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2301 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 12 second max cell voltage | cluster_no_12_second_max_cell_voltage | cluster_no_12_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2302 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 12 second max cell voltage pack num. | cluster_no_12_second_max_cell_voltage_pack_num | cluster_no_12_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2303 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 13 second max cell voltage | cluster_no_13_second_max_cell_voltage | cluster_no_13_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2304 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 13 second max cell voltage pack num. | cluster_no_13_second_max_cell_voltage_pack_num | cluster_no_13_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2305 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 14 second max cell voltage | cluster_no_14_second_max_cell_voltage | cluster_no_14_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2306 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 14 second max cell voltage pack num. | cluster_no_14_second_max_cell_voltage_pack_num | cluster_no_14_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2307 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 15 second max cell voltage | cluster_no_15_second_max_cell_voltage | cluster_no_15_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2308 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 15 second max cell voltage pack num. | cluster_no_15_second_max_cell_voltage_pack_num | cluster_no_15_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2309 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 16 second max cell voltage | cluster_no_16_second_max_cell_voltage | cluster_no_16_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2310 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 16 second max cell voltage pack num. | cluster_no_16_second_max_cell_voltage_pack_num | cluster_no_16_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2311 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 17 second max cell voltage | cluster_no_17_second_max_cell_voltage | cluster_no_17_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2312 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 17 second max cell voltage pack num. | cluster_no_17_second_max_cell_voltage_pack_num | cluster_no_17_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2313 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 18 second max cell voltage | cluster_no_18_second_max_cell_voltage | cluster_no_18_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2314 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 18 second max cell voltage pack num. | cluster_no_18_second_max_cell_voltage_pack_num | cluster_no_18_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2315 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 19 second max cell voltage | cluster_no_19_second_max_cell_voltage | cluster_no_19_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2316 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 19 second max cell voltage pack num. | cluster_no_19_second_max_cell_voltage_pack_num | cluster_no_19_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2317 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 20 second max cell voltage | cluster_no_20_second_max_cell_voltage | cluster_no_20_second_max_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2318 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Maximum Cell Voltage |  | /site/ess_ls
Cluster No. 20 second max cell voltage pack num. | cluster_no_20_second_max_cell_voltage_pack_num | cluster_no_20_second_max_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2319 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Maximum Cell Voltage Location |  | /site/ess_ls
Cluster No. 1 min cell voltage | cluster_no_1_min_cell_voltage | cluster_no_1_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2320 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 1 min cell voltage pack num. | cluster_no_1_min_cell_voltage_pack_num | cluster_no_1_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2321 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 2 min cell voltage | cluster_no_2_min_cell_voltage | cluster_no_2_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2322 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 2 min cell voltage pack num. | cluster_no_2_min_cell_voltage_pack_num | cluster_no_2_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2323 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 3 min cell voltage | cluster_no_3_min_cell_voltage | cluster_no_3_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2324 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 3 min cell voltage pack num. | cluster_no_3_min_cell_voltage_pack_num | cluster_no_3_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2325 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 4 min cell voltage | cluster_no_4_min_cell_voltage | cluster_no_4_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2326 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 4 min cell voltage pack num. | cluster_no_4_min_cell_voltage_pack_num | cluster_no_4_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2327 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 5 min cell voltage | cluster_no_5_min_cell_voltage | cluster_no_5_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2328 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 5 min cell voltage pack num. | cluster_no_5_min_cell_voltage_pack_num | cluster_no_5_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2329 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 6 min cell voltage | cluster_no_6_min_cell_voltage | cluster_no_6_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2330 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 6 min cell voltage pack num. | cluster_no_6_min_cell_voltage_pack_num | cluster_no_6_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2331 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 7 min cell voltage | cluster_no_7_min_cell_voltage | cluster_no_7_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2332 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 7 min cell voltage pack num. | cluster_no_7_min_cell_voltage_pack_num | cluster_no_7_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2333 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 8 min cell voltage | cluster_no_8_min_cell_voltage | cluster_no_8_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2334 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 8 min cell voltage pack num. | cluster_no_8_min_cell_voltage_pack_num | cluster_no_8_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2335 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 9 min cell voltage | cluster_no_9_min_cell_voltage | cluster_no_9_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2336 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 9 min cell voltage pack num. | cluster_no_9_min_cell_voltage_pack_num | cluster_no_9_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2337 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 10 min cell voltage | cluster_no_10_min_cell_voltage | cluster_no_10_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2338 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 10 min cell voltage pack num. | cluster_no_10_min_cell_voltage_pack_num | cluster_no_10_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2339 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 11 min cell voltage | cluster_no_11_min_cell_voltage | cluster_no_11_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2340 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 11 min cell voltage pack num. | cluster_no_11_min_cell_voltage_pack_num | cluster_no_11_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2341 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 12 min cell voltage | cluster_no_12_min_cell_voltage | cluster_no_12_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2342 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 12 min cell voltage pack num. | cluster_no_12_min_cell_voltage_pack_num | cluster_no_12_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2343 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 13 min cell voltage | cluster_no_13_min_cell_voltage | cluster_no_13_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2344 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 13 min cell voltage pack num. | cluster_no_13_min_cell_voltage_pack_num | cluster_no_13_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2345 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 14 min cell voltage | cluster_no_14_min_cell_voltage | cluster_no_14_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2346 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 14 min cell voltage pack num. | cluster_no_14_min_cell_voltage_pack_num | cluster_no_14_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2347 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 15 min cell voltage | cluster_no_15_min_cell_voltage | cluster_no_15_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2348 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 15 min cell voltage pack num. | cluster_no_15_min_cell_voltage_pack_num | cluster_no_15_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2349 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 16 min cell voltage | cluster_no_16_min_cell_voltage | cluster_no_16_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2350 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 16 min cell voltage pack num. | cluster_no_16_min_cell_voltage_pack_num | cluster_no_16_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2351 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 17 min cell voltage | cluster_no_17_min_cell_voltage | cluster_no_17_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2352 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 17 min cell voltage pack num. | cluster_no_17_min_cell_voltage_pack_num | cluster_no_17_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2353 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 18 min cell voltage | cluster_no_18_min_cell_voltage | cluster_no_18_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2354 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 18 min cell voltage pack num. | cluster_no_18_min_cell_voltage_pack_num | cluster_no_18_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2355 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 19 min cell voltage | cluster_no_19_min_cell_voltage | cluster_no_19_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2356 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 19 min cell voltage pack num. | cluster_no_19_min_cell_voltage_pack_num | cluster_no_19_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2357 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 20 min cell voltage | cluster_no_20_min_cell_voltage | cluster_no_20_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2358 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 20 min cell voltage pack num. | cluster_no_20_min_cell_voltage_pack_num | cluster_no_20_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2359 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 1 second min cell voltage | cluster_no_1_second_min_cell_voltage | cluster_no_1_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2360 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 1 second min cell voltage pack num. | cluster_no_1_second_min_cell_voltage_pack_num | cluster_no_1_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2361 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 2 second min cell voltage | cluster_no_2_second_min_cell_voltage | cluster_no_2_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2362 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 2 second min cell voltage pack num. | cluster_no_2_second_min_cell_voltage_pack_num | cluster_no_2_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2363 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 3 second min cell voltage | cluster_no_3_second_min_cell_voltage | cluster_no_3_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2364 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 3 second min cell voltage pack num. | cluster_no_3_second_min_cell_voltage_pack_num | cluster_no_3_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2365 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 4 second min cell voltage | cluster_no_4_second_min_cell_voltage | cluster_no_4_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2366 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 4 second min cell voltage pack num. | cluster_no_4_second_min_cell_voltage_pack_num | cluster_no_4_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2367 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 5 second min cell voltage | cluster_no_5_second_min_cell_voltage | cluster_no_5_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2368 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 5 second min cell voltage pack num. | cluster_no_5_second_min_cell_voltage_pack_num | cluster_no_5_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2369 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 6 second min cell voltage | cluster_no_6_second_min_cell_voltage | cluster_no_6_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2370 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 6 second min cell voltage pack num. | cluster_no_6_second_min_cell_voltage_pack_num | cluster_no_6_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2371 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 7 second min cell voltage | cluster_no_7_second_min_cell_voltage | cluster_no_7_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2372 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 7 second min cell voltage pack num. | cluster_no_7_second_min_cell_voltage_pack_num | cluster_no_7_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2373 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 8 second min cell voltage | cluster_no_8_second_min_cell_voltage | cluster_no_8_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2374 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 8 second min cell voltage pack num. | cluster_no_8_second_min_cell_voltage_pack_num | cluster_no_8_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2375 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 9 second min cell voltage | cluster_no_9_second_min_cell_voltage | cluster_no_9_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2376 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 9 second min cell voltage pack num. | cluster_no_9_second_min_cell_voltage_pack_num | cluster_no_9_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2377 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 10 second min cell voltage | cluster_no_10_second_min_cell_voltage | cluster_no_10_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2378 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 10 second min cell voltage pack num. | cluster_no_10_second_min_cell_voltage_pack_num | cluster_no_10_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2379 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 11 second min cell voltage | cluster_no_11_second_min_cell_voltage | cluster_no_11_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2380 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 11 second min cell voltage pack num. | cluster_no_11_second_min_cell_voltage_pack_num | cluster_no_11_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2381 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 12 second min cell voltage | cluster_no_12_second_min_cell_voltage | cluster_no_12_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2382 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 12 second min cell voltage pack num. | cluster_no_12_second_min_cell_voltage_pack_num | cluster_no_12_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2383 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 13 second min cell voltage | cluster_no_13_second_min_cell_voltage | cluster_no_13_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2384 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 13 second min cell voltage pack num. | cluster_no_13_second_min_cell_voltage_pack_num | cluster_no_13_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2385 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 14 second min cell voltage | cluster_no_14_second_min_cell_voltage | cluster_no_14_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2386 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 14 second min cell voltage pack num. | cluster_no_14_second_min_cell_voltage_pack_num | cluster_no_14_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2387 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 15 second min cell voltage | cluster_no_15_second_min_cell_voltage | cluster_no_15_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2388 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 15 second min cell voltage pack num. | cluster_no_15_second_min_cell_voltage_pack_num | cluster_no_15_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2389 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 16 second min cell voltage | cluster_no_16_second_min_cell_voltage | cluster_no_16_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2390 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 16 second min cell voltage pack num. | cluster_no_16_second_min_cell_voltage_pack_num | cluster_no_16_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2391 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 17 second min cell voltage | cluster_no_17_second_min_cell_voltage | cluster_no_17_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2392 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 17 second min cell voltage pack num. | cluster_no_17_second_min_cell_voltage_pack_num | cluster_no_17_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2393 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 18 second min cell voltage | cluster_no_18_second_min_cell_voltage | cluster_no_18_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2394 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 18 second min cell voltage pack num. | cluster_no_18_second_min_cell_voltage_pack_num | cluster_no_18_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2395 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 19 second min cell voltage | cluster_no_19_second_min_cell_voltage | cluster_no_19_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2396 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 19 second min cell voltage pack num. | cluster_no_19_second_min_cell_voltage_pack_num | cluster_no_19_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2397 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 20 second min cell voltage | cluster_no_20_second_min_cell_voltage | cluster_no_20_second_min_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2398 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Minimum Cell Voltage |  | /site/ess_ls
Cluster No. 20 second min cell voltage pack num. | cluster_no_20_second_min_cell_voltage_pack_num | cluster_no_20_second_min_cell_voltage_pack_num | Status | 1 | Input Register |  |  |  | 2399 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Minimum Cell Voltage Location |  | /site/ess_ls
Cluster No. 1 max cell temperature | cluster_no_1_max_cell_temperature | cluster_no_1_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2400 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 1 max cell temperature pack num. | cluster_no_1_max_cell_temperature_pack_num | cluster_no_1_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2401 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 2 max cell temperature | cluster_no_2_max_cell_temperature | cluster_no_2_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2402 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 2 max cell temperature pack num. | cluster_no_2_max_cell_temperature_pack_num | cluster_no_2_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2403 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 3 max cell temperature | cluster_no_3_max_cell_temperature | cluster_no_3_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2404 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 3 max cell temperature pack num. | cluster_no_3_max_cell_temperature_pack_num | cluster_no_3_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2405 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 4 max cell temperature | cluster_no_4_max_cell_temperature | cluster_no_4_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2406 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 4 max cell temperature pack num. | cluster_no_4_max_cell_temperature_pack_num | cluster_no_4_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2407 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 5 max cell temperature | cluster_no_5_max_cell_temperature | cluster_no_5_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2408 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 5 max cell temperature pack num. | cluster_no_5_max_cell_temperature_pack_num | cluster_no_5_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2409 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 6 max cell temperature | cluster_no_6_max_cell_temperature | cluster_no_6_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2410 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 6 max cell temperature pack num. | cluster_no_6_max_cell_temperature_pack_num | cluster_no_6_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2411 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 7 max cell temperature | cluster_no_7_max_cell_temperature | cluster_no_7_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2412 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 7 max cell temperature pack num. | cluster_no_7_max_cell_temperature_pack_num | cluster_no_7_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2413 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 8 max cell temperature | cluster_no_8_max_cell_temperature | cluster_no_8_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2414 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 8 max cell temperature pack num. | cluster_no_8_max_cell_temperature_pack_num | cluster_no_8_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2415 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 9 max cell temperature | cluster_no_9_max_cell_temperature | cluster_no_9_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2416 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 9 max cell temperature pack num. | cluster_no_9_max_cell_temperature_pack_num | cluster_no_9_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2417 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 10 max cell temperature | cluster_no_10_max_cell_temperature | cluster_no_10_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2418 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 10 max cell temperature pack num. | cluster_no_10_max_cell_temperature_pack_num | cluster_no_10_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2419 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 11 max cell temperature | cluster_no_11_max_cell_temperature | cluster_no_11_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2420 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 11 max cell temperature pack num. | cluster_no_11_max_cell_temperature_pack_num | cluster_no_11_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2421 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 12 max cell temperature | cluster_no_12_max_cell_temperature | cluster_no_12_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2422 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 12 max cell temperature pack num. | cluster_no_12_max_cell_temperature_pack_num | cluster_no_12_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2423 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 13 max cell temperature | cluster_no_13_max_cell_temperature | cluster_no_13_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2424 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 13 max cell temperature pack num. | cluster_no_13_max_cell_temperature_pack_num | cluster_no_13_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2425 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 14 max cell temperature | cluster_no_14_max_cell_temperature | cluster_no_14_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2426 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 14 max cell temperature pack num. | cluster_no_14_max_cell_temperature_pack_num | cluster_no_14_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2427 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 15 max cell temperature | cluster_no_15_max_cell_temperature | cluster_no_15_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2428 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 15 max cell temperature pack num. | cluster_no_15_max_cell_temperature_pack_num | cluster_no_15_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2429 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 16 max cell temperature | cluster_no_16_max_cell_temperature | cluster_no_16_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2430 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 16 max cell temperature pack num. | cluster_no_16_max_cell_temperature_pack_num | cluster_no_16_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2431 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 17 max cell temperature | cluster_no_17_max_cell_temperature | cluster_no_17_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2432 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 17 max cell temperature pack num. | cluster_no_17_max_cell_temperature_pack_num | cluster_no_17_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2433 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 18 max cell temperature | cluster_no_18_max_cell_temperature | cluster_no_18_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2434 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 18 max cell temperature pack num. | cluster_no_18_max_cell_temperature_pack_num | cluster_no_18_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2435 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 19 max cell temperature | cluster_no_19_max_cell_temperature | cluster_no_19_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2436 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 19 max cell temperature pack num. | cluster_no_19_max_cell_temperature_pack_num | cluster_no_19_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2437 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 20 max cell temperature | cluster_no_20_max_cell_temperature | cluster_no_20_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2438 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 20 max cell temperature pack num. | cluster_no_20_max_cell_temperature_pack_num | cluster_no_20_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2439 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 1 second max cell temperature | cluster_no_1_second_max_cell_temperature | cluster_no_1_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2440 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 1 second max cell temperature pack num. | cluster_no_1_second_max_cell_temperature_pack_num | cluster_no_1_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2441 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 2 second max cell temperature | cluster_no_2_second_max_cell_temperature | cluster_no_2_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2442 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 2 second max cell temperature pack num. | cluster_no_2_second_max_cell_temperature_pack_num | cluster_no_2_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2443 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 3 second max cell temperature | cluster_no_3_second_max_cell_temperature | cluster_no_3_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2444 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 3 second max cell temperature pack num. | cluster_no_3_second_max_cell_temperature_pack_num | cluster_no_3_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2445 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 4 second max cell temperature | cluster_no_4_second_max_cell_temperature | cluster_no_4_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2446 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 4 second max cell temperature pack num. | cluster_no_4_second_max_cell_temperature_pack_num | cluster_no_4_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2447 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 5 second max cell temperature | cluster_no_5_second_max_cell_temperature | cluster_no_5_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2448 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 5 second max cell temperature pack num. | cluster_no_5_second_max_cell_temperature_pack_num | cluster_no_5_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2449 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 6 second max cell temperature | cluster_no_6_second_max_cell_temperature | cluster_no_6_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2450 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 6 second max cell temperature pack num. | cluster_no_6_second_max_cell_temperature_pack_num | cluster_no_6_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2451 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 7 second max cell temperature | cluster_no_7_second_max_cell_temperature | cluster_no_7_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2452 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 7 second max cell temperature pack num. | cluster_no_7_second_max_cell_temperature_pack_num | cluster_no_7_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2453 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 8 second max cell temperature | cluster_no_8_second_max_cell_temperature | cluster_no_8_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2454 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 8 second max cell temperature pack num. | cluster_no_8_second_max_cell_temperature_pack_num | cluster_no_8_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2455 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 9 second max cell temperature | cluster_no_9_second_max_cell_temperature | cluster_no_9_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2456 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 9 second max cell temperature pack num. | cluster_no_9_second_max_cell_temperature_pack_num | cluster_no_9_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2457 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 10 second max cell temperature | cluster_no_10_second_max_cell_temperature | cluster_no_10_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2458 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 10 second max cell temperature pack num. | cluster_no_10_second_max_cell_temperature_pack_num | cluster_no_10_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2459 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 11 second max cell temperature | cluster_no_11_second_max_cell_temperature | cluster_no_11_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2460 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 11 second max cell temperature pack num. | cluster_no_11_second_max_cell_temperature_pack_num | cluster_no_11_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2461 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 12 second max cell temperature | cluster_no_12_second_max_cell_temperature | cluster_no_12_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2462 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 12 second max cell temperature pack num. | cluster_no_12_second_max_cell_temperature_pack_num | cluster_no_12_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2463 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 13 second max cell temperature | cluster_no_13_second_max_cell_temperature | cluster_no_13_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2464 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 13 second max cell temperature pack num. | cluster_no_13_second_max_cell_temperature_pack_num | cluster_no_13_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2465 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 14 second max cell temperature | cluster_no_14_second_max_cell_temperature | cluster_no_14_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2466 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 14 second max cell temperature pack num. | cluster_no_14_second_max_cell_temperature_pack_num | cluster_no_14_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2467 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 15 second max cell temperature | cluster_no_15_second_max_cell_temperature | cluster_no_15_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2468 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 15 second max cell temperature pack num. | cluster_no_15_second_max_cell_temperature_pack_num | cluster_no_15_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2469 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 16 second max cell temperature | cluster_no_16_second_max_cell_temperature | cluster_no_16_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2470 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 16 second max cell temperature pack num. | cluster_no_16_second_max_cell_temperature_pack_num | cluster_no_16_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2471 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 17 second max cell temperature | cluster_no_17_second_max_cell_temperature | cluster_no_17_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2472 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 17 second max cell temperature pack num. | cluster_no_17_second_max_cell_temperature_pack_num | cluster_no_17_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2473 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 18 second max cell temperature | cluster_no_18_second_max_cell_temperature | cluster_no_18_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2474 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 18 second max cell temperature pack num. | cluster_no_18_second_max_cell_temperature_pack_num | cluster_no_18_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2475 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 19 second max cell temperature | cluster_no_19_second_max_cell_temperature | cluster_no_19_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2476 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 19 second max cell temperature pack num. | cluster_no_19_second_max_cell_temperature_pack_num | cluster_no_19_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2477 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 20 second max cell temperature | cluster_no_20_second_max_cell_temperature | cluster_no_20_second_max_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2478 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Maximum Cell Temperature |  | /site/ess_ls
Cluster No. 20 second max cell temperature pack num. | cluster_no_20_second_max_cell_temperature_pack_num | cluster_no_20_second_max_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2479 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Maximum Cell Temperature Location |  | /site/ess_ls
Cluster No. 1 min cell temperature | cluster_no_1_min_cell_temperature | cluster_no_1_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2480 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 1 min cell temperature pack num. | cluster_no_1_min_cell_temperature_pack_num | cluster_no_1_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2481 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 2 min cell temperature | cluster_no_2_min_cell_temperature | cluster_no_2_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2482 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 2 min cell temperature pack num. | cluster_no_2_min_cell_temperature_pack_num | cluster_no_2_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2483 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 3 min cell temperature | cluster_no_3_min_cell_temperature | cluster_no_3_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2484 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 3 min cell temperature pack num. | cluster_no_3_min_cell_temperature_pack_num | cluster_no_3_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2485 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 4 min cell temperature | cluster_no_4_min_cell_temperature | cluster_no_4_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2486 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 4 min cell temperature pack num. | cluster_no_4_min_cell_temperature_pack_num | cluster_no_4_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2487 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 5 min cell temperature | cluster_no_5_min_cell_temperature | cluster_no_5_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2488 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 5 min cell temperature pack num. | cluster_no_5_min_cell_temperature_pack_num | cluster_no_5_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2489 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 6 min cell temperature | cluster_no_6_min_cell_temperature | cluster_no_6_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2490 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 6 min cell temperature pack num. | cluster_no_6_min_cell_temperature_pack_num | cluster_no_6_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2491 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 7 min cell temperature | cluster_no_7_min_cell_temperature | cluster_no_7_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2492 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 7 min cell temperature pack num. | cluster_no_7_min_cell_temperature_pack_num | cluster_no_7_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2493 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 8 min cell temperature | cluster_no_8_min_cell_temperature | cluster_no_8_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2494 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 8 min cell temperature pack num. | cluster_no_8_min_cell_temperature_pack_num | cluster_no_8_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2495 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 9 min cell temperature | cluster_no_9_min_cell_temperature | cluster_no_9_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2496 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 9 min cell temperature pack num. | cluster_no_9_min_cell_temperature_pack_num | cluster_no_9_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2497 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 10 min cell temperature | cluster_no_10_min_cell_temperature | cluster_no_10_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2498 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 10 min cell temperature pack num. | cluster_no_10_min_cell_temperature_pack_num | cluster_no_10_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2499 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 11 min cell temperature | cluster_no_11_min_cell_temperature | cluster_no_11_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2500 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 11 min cell temperature pack num. | cluster_no_11_min_cell_temperature_pack_num | cluster_no_11_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2501 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 12 min cell temperature | cluster_no_12_min_cell_temperature | cluster_no_12_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2502 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 12 min cell temperature pack num. | cluster_no_12_min_cell_temperature_pack_num | cluster_no_12_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2503 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 13 min cell temperature | cluster_no_13_min_cell_temperature | cluster_no_13_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2504 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 13 min cell temperature pack num. | cluster_no_13_min_cell_temperature_pack_num | cluster_no_13_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2505 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 14 min cell temperature | cluster_no_14_min_cell_temperature | cluster_no_14_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2506 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 14 min cell temperature pack num. | cluster_no_14_min_cell_temperature_pack_num | cluster_no_14_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2507 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 15 min cell temperature | cluster_no_15_min_cell_temperature | cluster_no_15_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2508 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 15 min cell temperature pack num. | cluster_no_15_min_cell_temperature_pack_num | cluster_no_15_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2509 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 16 min cell temperature | cluster_no_16_min_cell_temperature | cluster_no_16_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2510 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 16 min cell temperature pack num. | cluster_no_16_min_cell_temperature_pack_num | cluster_no_16_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2511 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 17 min cell temperature | cluster_no_17_min_cell_temperature | cluster_no_17_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2512 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 17 min cell temperature pack num. | cluster_no_17_min_cell_temperature_pack_num | cluster_no_17_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2513 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 18 min cell temperature | cluster_no_18_min_cell_temperature | cluster_no_18_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2514 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 18 min cell temperature pack num. | cluster_no_18_min_cell_temperature_pack_num | cluster_no_18_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2515 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 19 min cell temperature | cluster_no_19_min_cell_temperature | cluster_no_19_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2516 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 19 min cell temperature pack num. | cluster_no_19_min_cell_temperature_pack_num | cluster_no_19_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2517 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 20 min cell temperature | cluster_no_20_min_cell_temperature | cluster_no_20_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2518 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 20 min cell temperature pack num. | cluster_no_20_min_cell_temperature_pack_num | cluster_no_20_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2519 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 1 second min cell temperature | cluster_no_1_second_min_cell_temperature | cluster_no_1_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2520 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 1 second min cell temperature pack num. | cluster_no_1_second_min_cell_temperature_pack_num | cluster_no_1_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2521 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 2 second min cell temperature | cluster_no_2_second_min_cell_temperature | cluster_no_2_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2522 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 2 second min cell temperature pack num. | cluster_no_2_second_min_cell_temperature_pack_num | cluster_no_2_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2523 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 3 second min cell temperature | cluster_no_3_second_min_cell_temperature | cluster_no_3_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2524 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 3 second min cell temperature pack num. | cluster_no_3_second_min_cell_temperature_pack_num | cluster_no_3_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2525 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 4 second min cell temperature | cluster_no_4_second_min_cell_temperature | cluster_no_4_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2526 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 4 second min cell temperature pack num. | cluster_no_4_second_min_cell_temperature_pack_num | cluster_no_4_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2527 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 5 second min cell temperature | cluster_no_5_second_min_cell_temperature | cluster_no_5_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2528 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 5 second min cell temperature pack num. | cluster_no_5_second_min_cell_temperature_pack_num | cluster_no_5_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2529 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 6 second min cell temperature | cluster_no_6_second_min_cell_temperature | cluster_no_6_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2530 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 6 second min cell temperature pack num. | cluster_no_6_second_min_cell_temperature_pack_num | cluster_no_6_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2531 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 7 second min cell temperature | cluster_no_7_second_min_cell_temperature | cluster_no_7_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2532 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 7 second min cell temperature pack num. | cluster_no_7_second_min_cell_temperature_pack_num | cluster_no_7_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2533 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 8 second min cell temperature | cluster_no_8_second_min_cell_temperature | cluster_no_8_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2534 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 8 second min cell temperature pack num. | cluster_no_8_second_min_cell_temperature_pack_num | cluster_no_8_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2535 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 9 second min cell temperature | cluster_no_9_second_min_cell_temperature | cluster_no_9_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2536 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 9 second min cell temperature pack num. | cluster_no_9_second_min_cell_temperature_pack_num | cluster_no_9_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2537 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 10 second min cell temperature | cluster_no_10_second_min_cell_temperature | cluster_no_10_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2538 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 10 second min cell temperature pack num. | cluster_no_10_second_min_cell_temperature_pack_num | cluster_no_10_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2539 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 11 second min cell temperature | cluster_no_11_second_min_cell_temperature | cluster_no_11_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2540 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 11 second min cell temperature pack num. | cluster_no_11_second_min_cell_temperature_pack_num | cluster_no_11_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2541 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 12 second min cell temperature | cluster_no_12_second_min_cell_temperature | cluster_no_12_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2542 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 12 second min cell temperature pack num. | cluster_no_12_second_min_cell_temperature_pack_num | cluster_no_12_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2543 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 13 second min cell temperature | cluster_no_13_second_min_cell_temperature | cluster_no_13_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2544 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 13 second min cell temperature pack num. | cluster_no_13_second_min_cell_temperature_pack_num | cluster_no_13_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2545 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 14 second min cell temperature | cluster_no_14_second_min_cell_temperature | cluster_no_14_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2546 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 14 second min cell temperature pack num. | cluster_no_14_second_min_cell_temperature_pack_num | cluster_no_14_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2547 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 15 second min cell temperature | cluster_no_15_second_min_cell_temperature | cluster_no_15_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2548 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 15 second min cell temperature pack num. | cluster_no_15_second_min_cell_temperature_pack_num | cluster_no_15_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2549 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 16 second min cell temperature | cluster_no_16_second_min_cell_temperature | cluster_no_16_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2550 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 16 second min cell temperature pack num. | cluster_no_16_second_min_cell_temperature_pack_num | cluster_no_16_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2551 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 17 second min cell temperature | cluster_no_17_second_min_cell_temperature | cluster_no_17_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2552 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 17 second min cell temperature pack num. | cluster_no_17_second_min_cell_temperature_pack_num | cluster_no_17_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2553 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 18 second min cell temperature | cluster_no_18_second_min_cell_temperature | cluster_no_18_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2554 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 18 second min cell temperature pack num. | cluster_no_18_second_min_cell_temperature_pack_num | cluster_no_18_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2555 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 19 second min cell temperature | cluster_no_19_second_min_cell_temperature | cluster_no_19_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2556 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 19 second min cell temperature pack num. | cluster_no_19_second_min_cell_temperature_pack_num | cluster_no_19_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2557 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 20 second min cell temperature | cluster_no_20_second_min_cell_temperature | cluster_no_20_second_min_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2558 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Minimum Cell Temperature |  | /site/ess_ls
Cluster No. 20 second min cell temperature pack num. | cluster_no_20_second_min_cell_temperature_pack_num | cluster_no_20_second_min_cell_temperature_pack_num | Status | 1 | Input Register |  |  |  | 2559 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Second Minimum Cell Temperature Location |  | /site/ess_ls
Cluster No. 1 battery cluster average voltage | cluster_no_1_battery_cluster_average_voltage | cluster_no_1_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2560 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 1 Average Voltage |  | /site/ess_ls
Cluster No. 2 battery cluster average voltage | cluster_no_2_battery_cluster_average_voltage | cluster_no_2_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2561 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 2 Average Voltage |  | /site/ess_ls
Cluster No. 3 battery cluster average voltage | cluster_no_3_battery_cluster_average_voltage | cluster_no_3_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2562 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 3 Average Voltage |  | /site/ess_ls
Cluster No. 4 battery cluster average voltage | cluster_no_4_battery_cluster_average_voltage | cluster_no_4_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2563 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 4 Average Voltage |  | /site/ess_ls
Cluster No. 5 battery cluster average voltage | cluster_no_5_battery_cluster_average_voltage | cluster_no_5_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2564 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 5 Average Voltage |  | /site/ess_ls
Cluster No. 6 battery cluster average voltage | cluster_no_6_battery_cluster_average_voltage | cluster_no_6_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2565 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 6 Average Voltage |  | /site/ess_ls
Cluster No. 7 battery cluster average voltage | cluster_no_7_battery_cluster_average_voltage | cluster_no_7_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2566 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 7 Average Voltage |  | /site/ess_ls
Cluster No. 8 battery cluster average voltage | cluster_no_8_battery_cluster_average_voltage | cluster_no_8_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2567 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 8 Average Voltage |  | /site/ess_ls
Cluster No. 9 battery cluster average voltage | cluster_no_9_battery_cluster_average_voltage | cluster_no_9_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2568 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 9 Average Voltage |  | /site/ess_ls
Cluster No. 10 battery cluster average voltage | cluster_no_10_battery_cluster_average_voltage | cluster_no_10_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2569 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 10 Average Voltage |  | /site/ess_ls
Cluster No. 11 battery cluster average voltage | cluster_no_11_battery_cluster_average_voltage | cluster_no_11_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2570 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 11 Average Voltage |  | /site/ess_ls
Cluster No. 12 battery cluster average voltage | cluster_no_12_battery_cluster_average_voltage | cluster_no_12_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2571 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 12 Average Voltage |  | /site/ess_ls
Cluster No. 13 battery cluster average voltage | cluster_no_13_battery_cluster_average_voltage | cluster_no_13_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2572 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 13 Average Voltage |  | /site/ess_ls
Cluster No. 14 battery cluster average voltage | cluster_no_14_battery_cluster_average_voltage | cluster_no_14_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2573 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 14 Average Voltage |  | /site/ess_ls
Cluster No. 15 battery cluster average voltage | cluster_no_15_battery_cluster_average_voltage | cluster_no_15_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2574 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 15 Average Voltage |  | /site/ess_ls
Cluster No. 16 battery cluster average voltage | cluster_no_16_battery_cluster_average_voltage | cluster_no_16_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2575 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 16 Average Voltage |  | /site/ess_ls
Cluster No. 17 battery cluster average voltage | cluster_no_17_battery_cluster_average_voltage | cluster_no_17_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2576 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 17 Average Voltage |  | /site/ess_ls
Cluster No. 18 battery cluster average voltage | cluster_no_18_battery_cluster_average_voltage | cluster_no_18_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2577 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 18 Average Voltage |  | /site/ess_ls
Cluster No. 19 battery cluster average voltage | cluster_no_19_battery_cluster_average_voltage | cluster_no_19_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2578 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 19 Average Voltage |  | /site/ess_ls
Cluster No. 20 battery cluster average voltage | cluster_no_20_battery_cluster_average_voltage | cluster_no_20_battery_cluster_average_voltage | Status | 1 | Input Register | V |  | 1000 | 2579 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Cluster 20 Average Voltage |  | /site/ess_ls
Stack overall average cell temperature | stack_overall_average_cell_temperature | stack_overall_average_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2800 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
Average ambient temperature inside the container | average_ambient_temperature_inside_the_container | average_ambient_temperature_inside_the_container | Status | 1 | Input Register | °C |  | 100 | 2801 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Ambient Temperature |  | /site/ess_ls
Average ambient humidity inside the container | average_ambient_humidity_inside_the_container | average_ambient_humidity_inside_the_container | Status | 1 | Input Register | %RH |  | 100 | 2802 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Ambient Humidity |  | /site/ess_ls
Maximum cell temperature | maximum_cell_temperature | maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2803 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
Stack index of maximum cell temperature | stack_index_of_maximum_cell_temperature | stack_index_of_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2804 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature Stack Location |  | /site/ess_ls
Cluster index of maximum cell temperature | cluster_index_of_maximum_cell_temperature | cluster_index_of_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2805 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature Cluster Location |  | /site/ess_ls
Pack index of maximum cell temperature | pack_index_of_maximum_cell_temperature | pack_index_of_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2806 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature Pack Location |  | /site/ess_ls
Minimum cell temperature | minimum_cell_temperature | minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2807 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
Stack index of Minimum cell temperature | stack_index_of_minimum_cell_temperature | stack_index_of_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2808 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature Stack Location |  | /site/ess_ls
Cluster index of Minimum cell temperature | cluster_index_of_minimum_cell_temperature | cluster_index_of_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2809 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature Cluster Location |  | /site/ess_ls
Pack index of Minimum cell temperature | pack_index_of_minimum_cell_temperature | pack_index_of_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2810 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature Pack Location |  | /site/ess_ls
BAMS online status |  | offline_bams | Status | 1 | Input Register |  |  |  | 2811 | bitfield | 0 | 65535 | [8 empty] | Yes | BAMS Status |  | /site/ess_ls |  | 0 = online 1 = offline
BAMS 1 |  | BAMS 1 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | BAMS 1
BAMS 2 |  | BAMS 2 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BAMS 2
BAMS 3 |  | BAMS 3 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | BAMS 3
BAMS 4 |  | BAMS 4 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | BAMS 4
Air conditioner online status |  | offline_air_conditioners | Status | 1 | Input Register |  |  |  | 2812 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner Status |  | /site/ess_ls |  | 0 = online 1 = offline
Air Conditioner 1 |  | Air Conditioner 1 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Air Conditioner 1
Air Conditioner 2 |  | Air Conditioner 2 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Air Conditioner 2
Air Conditioner 3 |  | Air Conditioner 3 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Air Conditioner 3
Air Conditioner 4 |  | Air Conditioner 4 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Air Conditioner 4
Air Conditioner 5 |  | Air Conditioner 5 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Air Conditioner 5
Air Conditioner 6 |  | Air Conditioner 6 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls | Air Conditioner 6
Air Conditioner 7 |  | Air Conditioner 7 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls | Air Conditioner 7
Air Conditioner 8 |  | Air Conditioner 8 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls | Air Conditioner 8
Air Conditioner 9 |  | Air Conditioner 9 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls | Air Conditioner 9
Air Conditioner 10 |  | Air Conditioner 10 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls | Air Conditioner 10
Air Conditioner 11 |  | Air Conditioner 11 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls | Air Conditioner 11
Air Conditioner 12 |  | Air Conditioner 12 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls | Air Conditioner 12
Air Conditioner 13 |  | Air Conditioner 13 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls | Air Conditioner 13
Air Conditioner 14 |  | Air Conditioner 14 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls | Air Conditioner 14
Temperature and humidity sensor online status |  | offline_temperature_and_humidity_sensors | Status | 1 | Input Register |  |  |  | 2813 | bitfield | 0 | 65535 | [8 empty] | Yes | Temperature and Humidty Sensor Status |  | /site/ess_ls |  | 0 = online 1 = offline
Sensor 1 |  | Sensor 1 | Status | 1 | Input Register |  |  |  | 2813 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Sensor 1
Sensor 2 |  | Sensor 2 | Status | 1 | Input Register |  |  |  | 2813 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Sensor 2
Sensor 3 |  | Sensor 3 | Status | 1 | Input Register |  |  |  | 2813 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Sensor 3
Meter online status |  | meter_online_status | Status | 1 | Input Register |  |  |  | 2814 | uint16 | 0 | 65535 | [8 empty] | Yes | Meter Status |  | /site/ess_ls
Gas sensor online status |  | gas_sensor_online_status | Status | 1 | Input Register |  |  |  | 2815 | uint16 | 0 | 65535 | [8 empty] | Yes | Gas Sensor Status |  | /site/ess_ls
Number of online BAMS |  | number_of_online_bams | Status | 1 | Input Register |  |  |  | 2816 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of BAMS Online |  | /site/ess_ls
Number of online air conditioners |  | number_of_online_air_conditioners | Status | 1 | Input Register |  |  |  | 2817 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Air Conditioners Online |  | /site/ess_ls
Number of online temperature and humidity |  | number_of_online_temperature_and_humidity | Status | 1 | Input Register |  |  |  | 2818 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Temperature and Humidity Sensors Online |  | /site/ess_ls
Number of online Meters |  | number_of_online_meters | Status | 1 | Input Register |  |  |  | 2819 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Meters Online |  | /site/ess_ls
Number of online gas sensors |  | number_of_online_gas_sensors | Status | 1 | Input Register |  |  |  | 2820 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Gas Sensors Online |  | /site/ess_ls
Environmental alarm status |  | emmu_alarms | Status | 1 | Input Register |  | 4 |  | 2821 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Environmental Alarm Status |  | /site/ess_ls |  | 0 = return 1 = occur
Access control state of AC panel |  | Access control state of AC panel | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Access control state of DC panel |  | Access control state of DC panel | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Access control state of SYS panel |  | Access control state of SYS panel | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
SPD fault (AC) |  | SPD fault (AC) | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
FSS fault |  | FSS fault | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single fire alarm warning |  | Single fire alarm warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Gas detector H2-1 abnormal |  | Gas detector H2-1 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Gas detector H2-2 abnormal |  | Gas detector H2-2 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Gas detector CO-1 abnormal |  | Gas detector CO-1 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Gas detector CO-2 abnormal |  | Gas detector CO-2 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVAC high-temp warning |  | HVAC high-temp warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
HVAC low-temp warning |  | HVAC low-temp warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
HVAC high humidity warning |  | HVAC high humidity warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
HVAC low humidity warning |  | HVAC low humidity warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
HVAC high pressure warning |  | HVAC high pressure warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Exhaust air high-temp warning |  | Exhaust air high-temp warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
HVAC communication error warning |  | HVAC communication error warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 38 | /site/ess_ls
UPS communication error warning |  | UPS communication error warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 41 | /site/ess_ls
Emmu fault status |  | emmu_faults | Status | 1 | Input Register |  | 2 |  | 2825 | bitfield | 0 | 4294967295 | [8 empty] | Yes | DIdevice Alarm Status |  | /site/ess_ls |  | 0 = return 1 = occur
Fire composite alarm protection |  | Fire composite alarm protection | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
E-stop of AC panel |  | E-stop of AC panel | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
E-stop of system |  | E-stop of system | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Remote E-stop |  | Remote E-stop | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Water flood sensor |  | Water flood sensor | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Gas detector H2-1 abnormal |  | Gas detector H2-1 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Gas detector H2-2 abnormal |  | Gas detector H2-2 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Gas detector CO-1 abnormal |  | Gas detector CO-1 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Gas detector CO-2 abnormal |  | Gas detector CO-2 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Carbon monoxide concentration |  | carbon_monoxide_concentration | Status | 1 | Input Register | ppm | 2 | 100 | 2900 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Carbon Monoxide Concentration |  | /site/ess_ls
Hydrogen concentration |  | hydrogen_concentration | Status | 1 | Input Register | ppm | 2 | 100 | 2902 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Hydrogen Concentration |  | /site/ess_ls
Oxygen concentration |  | oxygen_concentration | Status | 1 | Input Register | ppm | 2 | 100 | 2904 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Oxygen Concentration |  | /site/ess_ls
Carbon monoxide alarm status |  | carbon_monoxide_alarm_status | Status | 1 | Input Register |  |  |  | 2906 | uint16 | 0 | 65535 | [8 empty] | Yes | Carbon Monoxide Alarm Status |  | /site/ess_ls | 0 = normal state, 1 = alarm state
Hydrogen alarm status |  | hydrogen_alarm_status | Status | 1 | Input Register |  |  |  | 2907 | uint16 | 0 | 65535 | [8 empty] | Yes | Hydrogen Alarm Status |  | /site/ess_ls | 0 = normal state, 1 = alarm state
Oxygen alarm status |  | oxygen_alarm_status | Status | 1 | Input Register |  |  |  | 2908 | uint16 | 0 | 65535 | [8 empty] | Yes | Oxygen Alarm Status |  | /site/ess_ls | 0 = normal state, 1 = alarm state
Temperature reading of temperature and humidty sensor No. 1 |  | temperature_reading_of_temperature_and_humidty_sensor_no_1 | Status | 1 | Input Register | °C |  | 100 | 2930 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 1 Temperature |  | /site/ess_ls
Temperature reading of temperature and humidty sensor No. 2 |  | temperature_reading_of_temperature_and_humidty_sensor_no_2 | Status | 1 | Input Register | °C |  | 100 | 2931 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 2 Temperature |  | /site/ess_ls
Temperature reading of temperature and humidty sensor No. 3 |  | temperature_reading_of_temperature_and_humidty_sensor_no_3 | Status | 1 | Input Register | °C |  | 100 | 2932 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 3 Temperature |  | /site/ess_ls
Humidity reading of temperature and humidty sensor No. 1 |  | humidity_reading_of_temperature_and_humidty_sensor_no_1 | Status | 1 | Input Register | %RH |  | 100 | 2933 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 1 Humidity |  | /site/ess_ls
Humidity reading of temperature and humidty sensor No. 2 |  | humidity_reading_of_temperature_and_humidty_sensor_no_2 | Status | 1 | Input Register | %RH |  | 100 | 2934 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 2 Humidity |  | /site/ess_ls
Humidity reading of temperature and humidty sensor No. 3 |  | humidity_reading_of_temperature_and_humidty_sensor_no_3 | Status | 1 | Input Register | %RH |  | 100 | 2935 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 3 Humidity |  | /site/ess_ls
Air conditioner temperature limit 1 |  | air_conditioner_temperature_limit_1 | Status | 1 | Input Register | °C |  | 100 | 3000 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner Temperature Limit 1 |  | /site/ess_ls
Air conditioner temperature limit 2 |  | air_conditioner_temperature_limit_2 | Status | 1 | Input Register | °C |  | 100 | 3001 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner Temperature Limit 2 |  | /site/ess_ls
Air conditioner temperature limit 3 |  | air_conditioner_temperature_limit_3 | Status | 1 | Input Register | °C |  | 100 | 3002 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner Temperature Limit 3 |  | /site/ess_ls
Air conditioner1 current mode |  | air_conditioner_1_current_mode | Status | 1 | Input Register |  |  |  | 3003 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 1 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner1 temperature |  | air_conditioner_1_temperature | Status | 1 | Input Register | °C |  | 100 | 3004 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 1 Temperature |  | /site/ess_ls
Air conditioner1 humidity |  | air_conditioner_1_humidity | Status | 1 | Input Register | %RH |  | 100 | 3005 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 1 Humidity |  | /site/ess_ls
Air conditioner2 current mode |  | air_conditioner_2_current_mode | Status | 1 | Input Register |  |  |  | 3006 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 2 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3006 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner2 temperature |  | air_conditioner_2_temperature | Status | 1 | Input Register | °C |  | 100 | 3007 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 2 Temperature |  | /site/ess_ls
Air conditioner2 humidity |  | air_conditioner_2_humidity | Status | 1 | Input Register | %RH |  | 100 | 3008 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 2 Humidity |  | /site/ess_ls
Air conditioner3 current mode |  | air_conditioner_3_current_mode | Status | 1 | Input Register |  |  |  | 3009 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 3 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner3 temperature |  | air_conditioner_3_temperature | Status | 1 | Input Register | °C |  | 100 | 3010 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 3 Temperature |  | /site/ess_ls
Air conditioner3 humidity |  | air_conditioner_3_humidity | Status | 1 | Input Register | %RH |  | 100 | 3011 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 3 Humidity |  | /site/ess_ls
Air conditioner4 current mode |  | air_conditioner_4_current_mode | Status | 1 | Input Register |  |  |  | 3012 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 4 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3012 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3012 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3012 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3012 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3012 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner4 temperature |  | air_conditioner_4_temperature | Status | 1 | Input Register | °C |  | 100 | 3013 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 4 Temperature |  | /site/ess_ls
Air conditioner4 humidity |  | air_conditioner_4_humidity | Status | 1 | Input Register | %RH |  | 100 | 3014 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 4 Humidity |  | /site/ess_ls
Air conditioner5 current mode |  | air_conditioner_5_current_mode | Status | 1 | Input Register |  |  |  | 3015 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 5 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3015 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3015 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3015 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3015 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3015 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner5 temperature |  | air_conditioner_5_temperature | Status | 1 | Input Register | °C |  | 100 | 3016 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 5 Temperature |  | /site/ess_ls
Air conditioner5 humidity |  | air_conditioner_5_humidity | Status | 1 | Input Register | %RH |  | 100 | 3017 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 5 Humidity |  | /site/ess_ls
Air conditioner6 current mode |  | air_conditioner_6_current_mode | Status | 1 | Input Register |  |  |  | 3018 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 6 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3018 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3018 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3018 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3018 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3018 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner6 temperature |  | air_conditioner_6_temperature | Status | 1 | Input Register | °C |  | 100 | 3019 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 6 Temperature |  | /site/ess_ls
Air conditioner6 humidity |  | air_conditioner_6_humidity | Status | 1 | Input Register | %RH |  | 100 | 3020 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 6 Humidity |  | /site/ess_ls
Air conditioner7 current mode |  | air_conditioner_7_current_mode | Status | 1 | Input Register |  |  |  | 3021 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 7 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3021 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3021 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3021 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3021 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3021 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner7 temperature |  | air_conditioner_7_temperature | Status | 1 | Input Register | °C |  | 100 | 3022 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 7 Temperature |  | /site/ess_ls
Air conditioner7 humidity |  | air_conditioner_7_humidity | Status | 1 | Input Register | %RH |  | 100 | 3023 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 7 Humidity |  | /site/ess_ls
Air conditioner8 current mode |  | air_conditioner_8_current_mode | Status | 1 | Input Register |  |  |  | 3024 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 8 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3024 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3024 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3024 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3024 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3024 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner8 temperature |  | air_conditioner_8_temperature | Status | 1 | Input Register | °C |  | 100 | 3025 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 8 Temperature |  | /site/ess_ls
Air conditioner8 humidity |  | air_conditioner_8_humidity | Status | 1 | Input Register | %RH |  | 100 | 3026 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 8 Humidity |  | /site/ess_ls
Air conditioner9 current mode |  | air_conditioner_9_current_mode | Status | 1 | Input Register |  |  |  | 3027 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 9 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3027 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3027 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3027 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3027 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3027 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner9 temperature |  | air_conditioner_9_temperature | Status | 1 | Input Register | °C |  | 100 | 3028 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 9 Temperature |  | /site/ess_ls
Air conditioner9 humidity |  | air_conditioner_9_humidity | Status | 1 | Input Register | %RH |  | 100 | 3029 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 9 Humidity |  | /site/ess_ls
Air conditioner10 current mode |  | air_conditioner_10_current_mode | Status | 1 | Input Register |  |  |  | 3030 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 10 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3030 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3030 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3030 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3030 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3030 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner10 temperature |  | air_conditioner_10_temperature | Status | 1 | Input Register | °C |  | 100 | 3031 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 10 Temperature |  | /site/ess_ls
Air conditioner10 humidity |  | air_conditioner_10_humidity | Status | 1 | Input Register | %RH |  | 100 | 3032 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 10 Humidity |  | /site/ess_ls
Air conditioner11 current mode |  | air_conditioner_11_current_mode | Status | 1 | Input Register |  |  |  | 3033 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 11 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3033 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3033 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3033 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3033 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3033 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner11 temperature |  | air_conditioner_11_temperature | Status | 1 | Input Register | °C |  | 100 | 3034 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 11 Temperature |  | /site/ess_ls
Air conditioner11 humidity |  | air_conditioner_11_humidity | Status | 1 | Input Register | %RH |  | 100 | 3035 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 11 Humidity |  | /site/ess_ls
Air conditioner12 current mode |  | air_conditioner_12_current_mode | Status | 1 | Input Register |  |  |  | 3036 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 12 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3036 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3036 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3036 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3036 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3036 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner12 temperature |  | air_conditioner_12_temperature | Status | 1 | Input Register | °C |  | 100 | 3037 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 12 Temperature |  | /site/ess_ls
Air conditioner12 humidity |  | air_conditioner_12_humidity | Status | 1 | Input Register | %RH |  | 100 | 3038 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 12 Humidity |  | /site/ess_ls
Air conditioner13 current mode |  | air_conditioner_13_current_mode | Status | 1 | Input Register |  |  |  | 3039 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 13 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3039 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3039 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3039 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3039 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3039 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner13 temperature |  | air_conditioner_13_temperature | Status | 1 | Input Register | °C |  | 100 | 3040 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 13 Temperature |  | /site/ess_ls
Air conditioner13 humidity |  | air_conditioner_13_humidity | Status | 1 | Input Register | %RH |  | 100 | 3041 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 13 Humidity |  | /site/ess_ls
Air conditioner14 current mode |  | air_conditioner_14_current_mode | Status | 1 | Input Register |  |  |  | 3042 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 14 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3042 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3042 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3042 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3042 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3042 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner14 temperature |  | air_conditioner_14_temperature | Status | 1 | Input Register | °C |  | 100 | 3043 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 14 Temperature |  | /site/ess_ls
Air conditioner14 humidity |  | air_conditioner_14_humidity | Status | 1 | Input Register | %RH |  | 100 | 3044 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 14 Humidity |  | /site/ess_ls
Air conditioner15 current mode |  | air_conditioner_15_current_mode | Status | 1 | Input Register |  |  |  | 3045 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 15 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3045 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3045 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3045 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3045 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3045 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner15 temperature |  | air_conditioner_15_temperature | Status | 1 | Input Register | °C |  | 100 | 3046 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 15 Temperature |  | /site/ess_ls
Air conditioner15 humidity |  | air_conditioner_15_humidity | Status | 1 | Input Register | %RH |  | 100 | 3047 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 15 Humidity |  | /site/ess_ls
Air conditioner16 current mode |  | air_conditioner_16_current_mode | Status | 1 | Input Register |  |  |  | 3048 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 16 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3048 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3048 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3048 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3048 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3048 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner16 temperature |  | air_conditioner_16_temperature | Status | 1 | Input Register | °C |  | 100 | 3049 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 16 Temperature |  | /site/ess_ls
Air conditioner16 humidity |  | air_conditioner_16_humidity | Status | 1 | Input Register | %RH |  | 100 | 3050 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 16 Humidity |  | /site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls
/site/ess_ls