## Tx100 Range(100)
Device Name | FlexGen Tx100 Ess | Customer | Broad Reach Power
Device Protocol | Modbus | Location | BRP ERCOT NOC
Device Protocol Version | 0.3
Device ID String | FPS_FM |  |  | modbus < -> dnp3 Register Type equivalents:
Device IP Address (if TCP) |  |  |  | Holding Register | AnOPF32
Device Port (502 typical) |  |  |  | Input Register | analog
Serial Device (if RTU) |  |  |  | Discrete Input | binary
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical) |  |  |  | Coil | AnOPInt16
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical) | [16 empty] | only required for modbus server configs
Name | Source Device | Type | Version | Register Type | Unit | Words | Bus Scale | Address | Data Type | Range Start | Range End | Engineering Range Start | Engineering Range End | Description | Control Narrative for Register | Reg ID | URI | ID | Include | Stripped Address | Address2 | Repeat | Bit | FIMS Scale | Scale
life |  |  |  | Holding Register |  | 2 |  | 1000 | signed |  |  |  |  | HeartBeat |  | life | /site/ess | life | yes
Control_Command | [7 empty] | 1002 | [5 empty] | Control 0: Idle 1:Start 2:Stop 3:StandBy |  | start_stop | /site/ess_hs | start_stop | yes
Run_Mode | [7 empty] | 1003 | [5 empty] | ?? |  | run_mode | /site/ess_hs |  | yes
On/Off Grid Mode | [7 empty] | 1004 | [5 empty] | Control 0:Idle 1:On Grid 2:OffGrid |  | on_off_grid_mode | /site/ess_hs | on_off_grid_mode | yes
Active Power Setpoint | [7 empty] | 1005 | signed |  |  |  |  | Active Power Setpoint |  | active_power_setpoint | /site/ess_hs | active_power_setpoint | yes | [5 empty] | 10
Reactive Power Setpoint | [7 empty] | 1006 | signed |  |  |  |  | Reactive Power Setpoint |  | reactive_power_setpoint | /site/ess_hs | reactive_power_setpoint | yes | [5 empty] | 10
Active Power Rising Slope | [7 empty] | 1007 | signed |  |  |  |  | Active Power Rsing Slope |  | active_power_rising_slope | /site/ess_hs | active_power_rising_slope | yes | [5 empty] | 10
Active Power Droop Slope | [7 empty] | 1008 | signed |  |  |  |  | Active Power Droop Slope |  | active_power_droop_slope | /site/ess_hs | active_power_droop_slope | yes | [5 empty] | 10
Reactive Power Rising Slope | [7 empty] | 1009 | signed |  |  |  |  | Reactive Power Rsing Slope |  | reactive_power_rising_slope | /site/ess_hs | reactive_power_rising_slope | yes | [5 empty] | 10
Reactive Power Droop Slope | [7 empty] | 1010 | signed |  |  |  |  | Reactive Power Droop Slope |  | reactive_power_droop_slope | /site/ess_hs | reactive_power_droop_slope | yes | [5 empty] | 10
life signal |  |  |  | Input Register |  |  |  | 2000
Q Charge | [7 empty] | 2002 | [7 empty] | chargeable_energy |  | chargeable_energy
Q Discharge | [7 empty] | 2003 | [7 empty] | dischargeable_energy |  | dischargeable_energy | [6 empty] | 10
W Charge | [7 empty] | 2004 | [7 empty] | chargeable_power |  | chargeable_power | [6 empty] | -10
Q Discharge | [15 empty] | dischargeable_power |  | dischargeable_power | [6 empty] | 10
W discsharge | [24 empty] | -10
system state | [7 empty] | 2006 | [5 empty] | enum bit strings Stop Run Run Fault Standby |  | System State
comm_status | [7 empty] | 2007 | [5 empty] | bit string BMS,Dcs,… |  | Comm Status
pcs_under_power | [7 empty] | 2008
pcs_over_power | [7 empty] | 2009
voltage L1 L2 | [7 empty] | 2030 | [16 empty] | 10
voltage L2 L3 | [7 empty] | 2031 | [16 empty] | 10
voltage L3 L1 | [7 empty] | 2032 | [16 empty] | 10
current L1 | [7 empty] | 2033 | [7 empty] | current_l1 | /site/ess | current_l1 | [6 empty] | 10
current L2 | [7 empty] | 2034 | [7 empty] | current_l2 | /site/ess | current_l2 | [6 empty] | 10
current L3 | [7 empty] | 2035 | [7 empty] | current_l3 | /site/ess | current_l3 | [6 empty] | 10
frequency | [7 empty] | 2036 | [16 empty] | 100
active_power | [7 empty] | 2037 | [16 empty] | 10
reactive_power | [7 empty] | 2038 | [16 empty] | 10
pf | [7 empty] | 2039
voltage_dc | [7 empty] | 2040
current_dc | [7 empty] | 2041
active_power_dc
reactive_power_dc
pcs_mode | [7 empty] | 2043 | [5 empty] | bitstrings
On-grid constant current (CC)
On-grid constant voltage (CV)
On-grid constant power (AC)
On-grid constant power (DC)
res:4
res:5
res:6
res:7
res:8
On-grid Mode
Off-grid Mode
pcs_state | [7 empty] | 2044 | [5 empty] | bitfiel
Running
Reserved Address:2044 Bit:1,
"Reserved Address:2044 Bit:2",
"Key stop",
"Standby",
"Emergency stop",
"Start in process",
"Stop in process",
"Reserved Address:2044 Bit:8",
"Fault stop",
"Alarm running",
"Derating running",
"Reserved Address:2044 Bit:12",
"Reserved Address:2044 Bit:13",
"Reserved Address:2044 Bit:14",
"DSP communication error"
pcs_state_2 | [7 empty] | 2046 | [5 empty] | bit field
Charging
Discharging
Not Operating
faults_overall | [7 empty] | 2047 | [5 empty] | bit field
Smoke Alarm
Door Open Protection
alarms_overall | [7 empty] | 2048 | [5 empty] | Temperature & Humidity Board Communication Error
"Switch Board Communication Error",
"Tributary Board Communication Error"
overall_max_charge_power_limit | [7 empty] | 2050
overall_max_discharge_power_limit | [7 empty] | 2051
overall Apparent Power | [7 empty] | 2052
bms_state | [7 empty] | 2053 | [5 empty] | stop run fault standby
Mbmu_state | [7 empty] | 2054 | [5 empty] | stop run fault standby
pcs_voltage_l1_l2 | [7 empty] | 2070
pcs_voltage_l2_l3 | [7 empty] | 2071
pcs_voltage_l3_l1 | [7 empty] | 2072
pcs_current_l1 | [7 empty] | 2073
pcs_current_l2 | [7 empty] | 2074
pcs_current_l3 | [7 empty] | 2075
pcs_active_power
pcs_reactive_power
pcs_voltage_dc
pcs_current_dc
pcs_voltage_dc
pcs_active_power_dc
pcs_alarm | [7 empty] | 2083
Reserved Address:2083 Bit:0",
"AC Switch Abnormal",
"Fan 2 abnormal",
"AC main contactor abnormal",
"Reserved Address:2083 Bit:4",
"IO-LCD comm error",
"Reserved Address:2083 Bit:6",
"Reserved Address:2083 Bit:7",
"Reserved Address:2083 Bit:8",
"Reserved Address:2083 Bit:9",
"Reserved Address:2083 Bit:10",
"Reserved Address:2083 Bit:11",
"Reserved Address:2083 Bit:12",
"Reserved Address:2083 Bit:13",
"Reserved Address:2083 Bit:14",
"Reserved Address:2083 Bit:15",
"Temp abnormal",
"Reserved Address:2083 Bit:17",
"GFRT Running",
"Reserved Address:2083 Bit:19",
"DC fuse abnormal",
"Reserved Address:2083 Bit:21",
"DC sensor abnormal",
"DC SPD alarm",
"AC SPD alarm",
"Chargine condition not met",
"Discharging condition not met",
"Reserved Address:2083 Bit:27",
"DC switch abnormal",
"Fan 1 Abnormal"
pcs_faults | [7 empty] | 2085
Insulation Resistance",
"AC SPD Fault",
"Sampling Fault",
"Battery polarity reversed",
"Reserved Address:2085 Bit:4",
"LCD_DSP fault",
"AC current unbalanced",
"Host Fault",
"DC SPD Fault",
"Reserved Address:2085 Bit:9",
"DC Injection Fault",
"DC Switch Fault",
"Device code repeat fault",
"Parallel communication error",
"PCS Control cabinet temperature abnormal",
"Reserved Address:2085 Bit:15",
"AC voltage unbalanced",
"Reserved Address:2085 Bit:17",
"Reserved Address:2085 Bit:18",
"AC switch fault",
"Soft Start Fault",
"DC Voltage sampling fault",
"Fan 2 fault",
"AC current unbalanced 2",
"AC current unbalanced 3",
"Drive board fault",
"Neutral point potential shift",
"Carier sync fault",
"Reserved Address:2085 Bit:28",
"Reserved Address:2085 Bit:29",
"Reserved Address:2085 Bit:30",
"Reserved Address:2085 Bit:31",
"DC undervoltage",
"DC overvoltage",
"AC undervoltage",
"AC overvoltage",
"AC underfrequency",
"AC overfrequency",
"AC contactor fault",
"Islanding portection",
"Reserved Address:2085 Bit:40",
"PDP protection",
"Module overtemperature",
"Reactor overtemperature",
"Transformer overtemperature",
"Leakage current",
"Reserved Address:2085 Bit:46",
"Overload protection",
"Reserved Address:2085 Bit:48",
"Fan 1 Fault",
"DC fuse fault",
"Reserved Address:2085 Bit:51",
"DC overcurrent",
"AC overcurrent",
"Reserved Address:2085 Bit:54",
"Ambient temperature abnormal",
"Hardware fault"
pcs_max_charge_power_limit | mbmu_max_charge_allowed | [6 empty] | 2089
mbmu_max_charge_current
pcs_max_discharge_power_limit | mbmu_max_discharge_allowed
mbmu_max_discharge_current
bms_max_cell_voltage | mbmu_max_cell_voltage | [6 empty] | 2130
module_index_max_cell_voltage | [7 empty] | 2131
cluster_index_max_cell_voltage | [7 empty] | 2132
bms_min_cell_voltage | mbmu_min_cell_voltage | [6 empty] | 2133
module_index_min_cell_voltage | [7 empty] | 2134
cluster_index_min_cell_voltage | [7 empty] | 2135
bms_max_cell_temp | mbmu_max_cell_temp | [6 empty] | 2136
module_index_max_cell_temp | [7 empty] | 2137
cluster_index_max_cell_temp | [7 empty] | 2138
bms_min_cell_temp | mbmu_min_cell_temp | [6 empty] | 2139
module_index_min_cell_temp | [7 empty] | 2140
cluster_index_min_cell_temp | [7 empty] | 2141
bms_bus_voltage | mbmu_voltage | [6 empty] | 2143
bms_bus_current | mbmu_current | [6 empty] | 2144
bms_soc | mbmu_soc
mbmu_soh
fault_clear_cmd
bms_power
operational_status | bms_status | [6 empty] | 2146 | [5 empty] | enum
| Initialize | [12 empty] | xxbit_strings: [
| Normal", | [12 empty] | "Initialize",
| Full Charge", | [12 empty] | "Normal",
| Full Discharge", | [12 empty] | "Full Charge",
| Warning Status", | [12 empty] | "Full Discharge",
| Fault Status" | [12 empty] | "Warning Status",
"Fault Status"
bms_current_chargeable_capacity | bms_remain_charge_energy | [6 empty] | 2149
bms_current_dischargeable_capacity | bms_remain_discharge_energy | [6 empty] | 2151
racks_in_service | [7 empty] | 2153
num_hv_subsystem
circuit_breaker_control_word | [7 empty] | 2154
main_circuit_breaker_status | [7 empty] | 2155
bms_maximum_charging_power_limit | bms_remain_charge_energy | [6 empty] | 2157
bms_maximum_discharging_power_limit | bms_remain_discharge_energy | [6 empty] | 2158
power_limit_state | [7 empty] | 2159 | [5 empty] | bit field
Reserved Address:2159 Bit:0,
"Charge overvoltage half power limit of cell",
"Charge overvoltage half power limit of cluster",
"Reserved Address:2159 Bit:3",
"Reserved Address:2159 Bit:4",
"Charge under-temp half power limit",
"Charge over-temp half power limit",
"Reserved Address:2159 Bit:7",
"Reserved Address:2159 Bit:8",
"Reserved Address:2159 Bit:9",
"Reserved Address:2159 Bit:10",
"Reserved Address:2159 Bit:11",
"Reserved Address:2159 Bit:12",
"Reserved Address:2159 Bit:13",
"Reserved Address:2159 Bit:14",
"Reserved Address:2159 Bit:15",
"Reserved Address:2159 Bit:16",
"Discharge undervoltage half power limit of cell",
"Discharge undervoltage half power limit of cluster",
"Reserved Address:2159 Bit:19",
"Reserved Address:2159 Bit:20",
"Discharge under-temp half power limit",
"Discharge over-temp half power limit",
"Reserved Address:2159 Bit:23",
"Reserved Address:2159 Bit:24",
"Reserved Address:2159 Bit:25",
"Reserved Address:2159 Bit:26",
"Reserved Address:2159 Bit:27",
"Reserved Address:2159 Bit:28",
"Reserved Address:2159 Bit:29",
"Reserved Address:2159 Bit:30",
"Reserved Address:2159 Bit:31",
"Reserved Address:2159 Bit:32",
"Charge overvoltage zero power limit of cell",
"Charge overvoltage zero power limit of cluster",
"Charge overcurrent zero power limit of cluster",
"Charge overcurrent zero power limit of array",
"Charge under-temp zero power limit",
"Charge over-temp zero power limit",
"Reserved Address:2159 Bit:39",
"Reserved Address:2159 Bit:40",
"Reserved Address:2159 Bit:41",
"Reserved Address:2159 Bit:42",
"Reserved Address:2159 Bit:43",
"Reserved Address:2159 Bit:44",
"Reserved Address:2159 Bit:45",
"Reserved Address:2159 Bit:46",
"Reserved Address:2159 Bit:47",
"Reserved Address:2159 Bit:48",
"Discharge undervoltage zero power limit of cell",
"Discharge undervoltage zero power limit of cluster",
"Discharge overcurrent zero power limit of cluster",
"Discharge overcurrent zero power limit of array",
"Discharge under-temp zero power limit",
"Discharge over-temp zero power limit"
bms_alarms | [7 empty] | 2163 | [5 empty] | bit_strings": [
"Reserved Address:2163 Bit:0",
"Reserved Address:2163 Bit:1",
"Reserved Address:2163 Bit:2",
[14 empty] | "Discharge undervoltage warning of cell", |  | mbmu_warning_1
[14 empty] | "Charge overvoltage warning of cell", |  | mbmu_warning_1
[14 empty] | "Discharge undervoltage warning of cluster", |  | mbmu_warning_1
[14 empty] | "Charge overvoltage warning of cluster", |  | mbmu_warning_1
[14 empty] | "Discharge overcurrent warning of cluster", |  | mbmu_warning_1
[14 empty] | "Charge overcurrent warning of cluster", |  | mbmu_warning_1
[14 empty] | "Discharge overcurrent warning of array", |  | mbmu_warning_1
[14 empty] | "Charge overcurrent warning of array", |  | mbmu_warning_1
"Low-temp warning",
"High-temp warning",
"Reserved Address:2163 Bit:13",
"High voltage-difference warning",
"High temp-difference warning",
"PCS communication abnormal warning",
"BMU communication abnormal warning",
"BCMS communication abnormal warning",
"BAMS abnormal warning",
"BCMS abnormal warning",
"High SOC warning",
"Low SOC warning",
"Reserved Address:2163 Bit:23",
"Reserved Address:2163 Bit:24",
"EMMU abnormal warning"
bms_faults | [7 empty] | 2167 | [5 empty] | bit_strings: [
"Reserved Address:2167 Bit:0",
"Reserved Address:2167 Bit:1",
"Insulation error protection",
"Discharge undervoltage LV1 protection of cell",
"Charge overvoltage LV1 protection of cell",
"Discharge undervoltage LV1 protection of cluster",
"Charge overvoltage LV1 protection of cluster",
"Discharge overcurrent LV1 protection of cluster",
"Charge overcurrent LV1 protection of cluster",
"Discharge overcurrent LV1 protection of array",
"Charge overcurrent LV1 protection of array",
"Low-temp LV1 protection",
"High-temp LV1 protection",
"Reserved Address:2167 Bit:13",
"Reserved Address:2167 Bit:14",
"Reserved Address:2167 Bit:15",
"Reserved Address:2167 Bit:16",
"Reserved Address:2167 Bit:17",
"Reserved Address:2167 Bit:18",
"Reserved Address:2167 Bit:19",
"Self-protection of BMS",
"Reserved Address:2167 Bit:21",
"E-stop fault",
"Reserved Address:2167 Bit:23",
"Reserved Address:2167 Bit:24",
"Reserved Address:2167 Bit:25",
"Reserved Address:2167 Bit:26",
"Self-protection of EMMU",
"Reserved Address:2167 Bit:28",
"Reserved Address:2167 Bit:29",
"Reserved Address:2167 Bit:30",
"Reserved Address:2167 Bit:31",
"Reserved Address:2167 Bit:32",
"Discharge undervoltage LV2 protection of cell",
"Charge overvoltage LV2 protection of cell",
"Discharge undervoltage LV2 protection of cluster",
"Discharge undervoltage LV2 protection of cluster",
"Discharge overcurrent LV2 protection of cluster",
Charge overcurrent LV2 protection of cluster",
Discharge overcurrent LV2 protection of array",
Charge overcurrent LV2 protection of array",
Low-temp LV2 protection"
High-temp LV2 protection
sbmu1_voltage
sbmu1_current
sbmu1_soc
sbmu1_soh
sbmu1_max_cell_voltage
sbmu1_min_cell_voltage
sbmu1_avg_cell_voltage
sbmu1_max_cell_temp
sbmu1_min_cell_temp
sbmu1_avg_cell_temp
sbmu1_max_charge_current
sbmu1_max_discharge_current
sbmu1_max_cell_voltage_positions
sbmu1_min_cell_voltage_positions
sbmu1_max_cell_temp_positions
sbmu1_min_cell_temp_positions
sbmu1_sum_cells
sbmu1_tms_mode_command
sbmu1_tms_temp_setting
sbmu1_tms_real_mode
| sbmu1_rack_inlet_temp | [12 empty] | ,
sbmu1_rack_outlet_temp
sbmu1_ambient_temp
sbmu1_tms_demand_power
sbmu1_tms_fault_code
sbmu1_door_state
sbmu_fan_in_box
cluster_no_1_battery_cluster_voltage | [7 empty] | 2200
cluster_no_2_battery_cluster_voltage | [7 empty] | 2201
cluster_no_11_battery_cluster_voltage | [7 empty] | 2210
cluster_no_1_battery_cluster_current | [7 empty] | 2220
cluster_no_11_battery_cluster_current | [7 empty] | 2230