## Modified_060721
Connection Name | Risen BMS 340
Device Name | Risen BMS 340
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device ID String | risen_bms_340
ip_address | 192.168.112.10
port | 502
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical) | [23 empty] | OPTIONAL for web_ui configs only |  | required for modbus server configs only
Name | Type | Ref | Register Type | Unit | Words | Bus Scale | FIMS Scale | hexAddress | Scale | Address | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
System Run Information | [14 empty] | ems_running_info | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
System Status | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0101 |  | 257 | uint16 |  |  | sys_status | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
BMS Alarm | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0102 |  | 266 | uint16 |  |  | bms_alarms | [11 empty] | /components/ems_running_info |  | Yes
Heartbeat | Status | 2.sys_run_info | Input Register |  | 2 |  |  | 0x0116 |  | 278 | uint16 |  |  | heartbeat | [11 empty] | /components/ems_running_info |  | Yes | [0, 2^32 - 1]
EMS Communication State | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0118 |  | 280 | uint16 |  |  | ems_comms_state | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal
BMS Communication State | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0119 |  | 281 | uint16 |  |  | bms_comms_state | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal By bits bit0: BMS2
AC Communication State 1 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011B |  | 283 | uint16 |  |  | ac_comms_state_1 | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal By bits bit0: HVAC1, bit1: HVAC3
AC Communication State 2 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011C |  | 284 | uint16 |  |  | ac_comms_state_2 | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal
AC Communication State 3 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011D |  | 285 | uint16 |  |  | ac_comms_state_3 | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal
FSS Communication State | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011F |  | 287 | uint16 |  |  | fss_comms_state | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal By bits bit0: FSS comms state
Year | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012A |  | 298 | uint16 |  |  | year | [11 empty] | /components/ems_running_info |  | Yes | [0-99]
Month | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012B |  | 299 | uint16 |  |  | month | [11 empty] | /components/ems_running_info |  | Yes | [1-12]
Day | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012C |  | 300 | uint16 |  |  | day | [11 empty] | /components/ems_running_info |  | Yes | [1-31]
Hour | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012D |  | 301 | uint16 |  |  | hour | [11 empty] | /components/ems_running_info |  | Yes | [0-23]
Minute | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012E |  | 302 | uint16 |  |  | minute | [11 empty] | /components/ems_running_info |  | Yes | [0-59]
Second | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012F |  | 303 | uint16 |  |  | second | [11 empty] | /components/ems_running_info |  | Yes | [0-59]
Environment Alarms 1 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0140 |  | 320 | uint16 |  |  | env_alarms_1 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 1 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 1 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 1 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 1 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 1 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 1 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 2 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 2 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 2 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 2 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 2 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 2 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 2 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0141 |  | 321 | uint16 |  |  | env_alarms_2 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 3 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 3 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 3 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 3 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 3 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 3 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 4 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 4 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 4 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 4 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 4 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 4 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 3 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0142 |  | 322 | uint16 |  |  | env_alarms_3 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 5 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 5 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 5 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 5 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 5 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 5 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 6 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 6 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 6 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 6 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 6 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 6 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 4 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0143 |  | 323 | uint16 |  |  | env_alarms_4 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 7 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 7 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 7 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 7 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 7 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 7 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 8 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 8 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 8 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 8 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 8 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 8 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 5 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0144 |  | 324 | uint16 |  |  | env_alarms_5 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 9 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 9 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 9 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 9 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 9 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 9 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 10 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 10 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 10 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 10 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 10 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 10 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 6 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0145 |  | 325 | uint16 |  |  | env_alarms_6 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 11 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 11 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 11 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 11 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 11 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 11 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 12 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 12 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 12 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 12 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 12 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 12 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 7 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0146 |  | 326 | uint16 |  |  | env_alarms_7 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 13 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 13 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 13 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 13 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 13 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 13 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 14 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 14 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 14 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 14 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 14 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 14 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 8 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0147 |  | 327 | uint16 |  |  | env_alarms_8 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 15 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 15 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 15 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 15 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 15 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 15 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 16 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 16 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 16 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 16 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 16 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 16 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 9 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0148 |  | 328 | uint16 |  |  | env_alarms_9 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 17 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 17 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 17 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 17 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 17 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 17 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 18 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 18 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 18 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 18 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 18 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 18 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Battery Cabinet Air Conditioning Relay | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0180 |  | 384 | uint16 |  |  | batt_cabinet_air_conditioning_relay | [11 empty] | /components/ems_running_info |  | Yes |  | 1: relay close, 0: relay open
BCP Cabinet Air Conditioning Relay | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0181 |  | 385 | uint16 |  |  | bcp_cabinet_air_conditioning_relay | [11 empty] | /components/ems_running_info |  | Yes |  | 1: relay close, 0: relay open
Shunt Trip Control of DC Load Switch | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0187 |  | 391 | uint16 |  |  | dc_load_switch_shunt_trip_ctrl | [11 empty] | /components/ems_running_info |  | Yes |  | 1: relay close, 0: relay open
Maintenance Start | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0200 |  | 512 | uint16 |  |  | maint_start | [11 empty] | /components/ems_running_info |  | No |  | 0: not maintenance, 1: maintenance
SOC Protect Enable | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0201 |  | 513 | uint16 |  |  | soc_protect_enable | [11 empty] | /components/ems_running_info |  | No |  | 0: disable, 1: enable
SOC Protect Delay | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0202 |  | 514 | uint16 |  |  | soc_protect_delay | [11 empty] | /components/ems_running_info |  | No | S, 0-200
SOCH2 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0203 |  | 515 | uint16 |  |  | soc_h2_alarm | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCH2 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0204 |  | 516 | uint16 |  |  | soc_h2_recovery | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCH1 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0205 |  | 517 | uint16 |  |  | soc_h1_alarm | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCH1 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0206 |  | 518 | uint16 |  |  | soc_h1_recovery | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCL1 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0207 |  | 519 | uint16 |  |  | soc_l1_recovery | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
SOCL1 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0208 |  | 520 | uint16 |  |  | soc_l1_alarm | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
SOCL2 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0209 |  | 521 | uint16 |  |  | soc_l2_recovery | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
SOCL2 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x020A |  | 522 | uint16 |  |  | soc_l2_alarm | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
EMS Timeout of Loss of Communication | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x020B |  | 523 | uint16 |  |  | ems_comms_loss_timeout_enable | [11 empty] | /components/ems_running_info |  | Yes |  | 0: disable, 1: enable
EMS Loss of Communication Timeout | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x020C |  | 524 | uint16 |  |  | ems_comms_loss_timeout | [11 empty] | /components/ems_running_info |  | Yes | second, if 0 default 10 [1, 120]
HVAC (Air-Conditioning) Information | [14 empty] | hvac_info | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Unit Running Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0300 |  | 768 | uint16 |  |  | hvac_1_unit_running_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Internal Fan Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0301 |  | 769 | uint16 |  |  | hvac_1_internal_fan_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
External Fan Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0302 |  | 770 | uint16 |  |  | hvac_1_external_fan_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Compressor Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0303 |  | 771 | uint16 |  |  | hvac_1_compressor_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Inside Return Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x0304 |  | 772 | int16 |  |  | hvac_1_inside_return_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Reserved 1 | Status | 3.AC_info | Input Register |  |  |  |  | 0z0305 |  | 773 | uint16 |  |  | hvac_1_reserved_1 | [11 empty] | /components/hvac_info |  | No
Outside Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x0306 |  | 774 | int16 |  |  | hvac_1_outside_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Condenser Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x0307 |  | 775 | int16 |  |  | hvac_1_condenser_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Reserved 2 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 776 | uint16 |  |  | hvac_1_reserved_2 | [11 empty] | /components/hvac_info |  | No
Reserved 3 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 777 | uint16 |  |  | hvac_1_reserved_3 | [11 empty] | /components/hvac_info |  | No
Reserved 4 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 778 | uint16 |  |  | hvac_1_reserved_4 | [11 empty] | /components/hvac_info |  | No
AC Input Voltage | Status | 3.AC_info | Input Register |  |  |  |  | 0x030B |  | 779 | int16 |  |  | hvac_1_ac_input_voltage | [11 empty] | /components/hvac_info |  | Yes | 1V
Reserved 5 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 780 | uint16 |  |  | hvac_1_reserved_5 | [11 empty] | /components/hvac_info |  | No
Reserved 6 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 781 | uint16 |  |  | hvac_1_reserved_6 | [11 empty] | /components/hvac_info |  | No
Emergency Air Fan State | Status | 3.AC_info | Input Register |  |  |  |  | 0x030E |  | 782 | uint16 |  |  | hvac_1_emergency_air_fan_state | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Heat Exchanger Coil (Tubing) Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x030F |  | 783 | int16 |  |  | hvac_1_heat_exchanger_coil_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Reserved 7 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 784 | uint16 |  |  | hvac_1_reserved_7 | [11 empty] | /components/hvac_info |  | No
Reserved 8 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 785 | uint16 |  |  | hvac_1_reserved_8 | [11 empty] | /components/hvac_info |  | No
Reserved 9 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 786 | uint16 |  |  | hvac_1_reserved_9 | [11 empty] | /components/hvac_info |  | No
Inside Return Humidity | Status | 3.AC_info | Input Register |  |  |  |  | 0x0313 |  | 787 | uint16 |  |  | hvac_1_inside_return_humidity | [11 empty] | /components/hvac_info |  | Yes | 1%
Electrical Heating Running Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0314 |  | 788 | uint16 |  |  | hvac_1_electrical_heating_running_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
HVAC Alarms 1 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0315 |  | 789 | uint16 |  |  | hvac_1_alarms_1 | [11 empty] | /components/hvac_info |  | Yes |  | bit0 High Temperature Waning bit1 Low Temperature Warning bit2 High Humidity Warning bit3 Low Humidity Warning bit4 Heat Exchanger Coil (Tubing) Frost Warning bit5 Exhaust Temperature High Warning bit6 Heat Exchanger Coil (Tubing) Temperature sensing failure Warning bit7 Exterior Temperature sensing failure Warning bit8 Condensation Temperature sensing failure warning bit9 Interior Temperature sensing failure warning bit10 Exhaust Temperature sensing failure warning bit11 Humidity sensing failure warning bit12 Interior fan failure warning bit13 Exterior fan failure warning bit14 Compressor failure warning bit15 Electric hearing failure warning
HVAC Alarms 2 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0316 |  | 790 | uint16 |  |  | hvac_1_alarms_2 | [11 empty] | /components/hvac_info |  | Yes |  | bit0 Emergency air fan failure warning bit1 High air pressure warning bit2 Low air pressure warning bit3 Flood warning bit4 Smoke warning bit5 Door open warning bit6 High air pressure lockdown warning bit7 Low air Pressure lockdown warning bit8 Exhaust lockdown warning bit9 AC high voltage warning bit10 AC low voltage warning bit11 AC drop out warning bit12 Phase loss warning bit13 Freq. abnormal warning bit14 Phase reversal warning bit15 DC high voltage warning
HVAC Alarms 3 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0317 |  | 791 | uint16 |  |  | hvac_1_alarms_3 | [11 empty] | /components/hvac_info |  | Yes |  | bit0 DC low voltage warning
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 800 | repeat |  | 768 | hvac_2 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 832 | repeat |  | 768 | hvac_3 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 864 | repeat |  | 768 | hvac_4 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 896 | repeat |  | 768 | hvac_5 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 928 | repeat |  | 768 | hvac_6 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 960 | repeat |  | 768 | hvac_7 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 992 | repeat |  | 768 | hvac_8 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1024 | repeat |  | 768 | hvac_9 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1056 | repeat |  | 768 | hvac_10 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1088 | repeat |  | 768 | hvac_11 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1120 | repeat |  | 768 | hvac_12 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1152 | repeat |  | 768 | hvac_13 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1184 | repeat |  | 768 | hvac_14 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1216 | repeat |  | 768 | hvac_15 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1248 | repeat |  | 768 | hvac_16 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1280 | repeat |  | 768 | hvac_17 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1312 | repeat |  | 768 | hvac_18 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1344 | repeat |  | 768 | hvac_19 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1376 | repeat |  | 768 | hvac_20 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1408 | repeat |  | 768 | hvac_21 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1440 | repeat |  | 768 | hvac_22 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1472 | repeat |  | 768 | hvac_23 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1504 | repeat |  | 768 | hvac_24 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1536 | repeat |  | 768 | hvac_25 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1568 | repeat |  | 768 | hvac_26 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1600 | repeat |  | 768 | hvac_27 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1632 | repeat |  | 768 | hvac_28 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1664 | repeat |  | 768 | hvac_29 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1696 | repeat |  | 768 | hvac_30 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1728 | repeat |  | 768 | hvac_31 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1760 | repeat |  | 768 | hvac_32 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1792 | repeat |  | 768 | hvac_33 | [11 empty] | /components/hvac_info |  | Yes
HVAC (Air-Conditioning) Parameters | [14 empty] | hvac_params | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Remote AC On | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0801 |  | 2049 | uint16 |  |  | hvac_1_remote_ac_on | [11 empty] | /components/hvac_params |  | Yes |  | 0:off, 1:on, The reset is NULL
Cooling Temp Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0802 |  | 2050 | uint16 |  |  | hvac_1_cooling_temp_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Cooling Set-point Upper Limit | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0803 |  | 2051 | uint16 |  |  | hvac_1_cooling_setpoint_upper_limit | [11 empty] | /components/hvac_params |  | Yes | 1°C
HT Warning Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0804 |  | 2052 | uint16 |  |  | hvac_1_ht_warning_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
LT Warning Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0805 |  | 2053 | uint16 |  |  | hvac_1_lt_warning_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Interior Air Fan Stop Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0806 |  | 2054 | uint16 |  |  | hvac_1_interior_air_fan_stop_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Heating Temp Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x080B |  | 2059 | uint16 |  |  | hvac_1_heating_temp_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Heating Setpoint Lower Limit | Control | 4.ACParam | Holding Register |  |  |  |  | 0x080C |  | 2060 | uint16 |  |  | hvac_1_heating_setpoint_lower_limit | [11 empty] | /components/hvac_params |  | Yes | 1°C
De-humidify Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x080D |  | 2061 | uint16 |  |  | hvac_1_dehumidify_setting | [11 empty] | /components/hvac_params |  | Yes | 1%
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2081 | repeat |  | 2049 | hvac_2 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2091 | repeat |  | 2059 | hvac_2 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2113 | repeat |  | 2049 | hvac_3 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2123 | repeat |  | 2059 | hvac_3 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2145 | repeat |  | 2049 | hvac_4 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2155 | repeat |  | 2059 | hvac_4 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2177 | repeat |  | 2049 | hvac_5 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2187 | repeat |  | 2059 | hvac_5 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2209 | repeat |  | 2049 | hvac_6 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2219 | repeat |  | 2059 | hvac_6 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2241 | repeat |  | 2049 | hvac_7 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2251 | repeat |  | 2059 | hvac_7 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2273 | repeat |  | 2049 | hvac_8 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2283 | repeat |  | 2059 | hvac_8 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2305 | repeat |  | 2049 | hvac_9 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2315 | repeat |  | 2059 | hvac_9 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2337 | repeat |  | 2049 | hvac_10 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2347 | repeat |  | 2059 | hvac_10 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2369 | repeat |  | 2049 | hvac_11 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2379 | repeat |  | 2059 | hvac_11 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2401 | repeat |  | 2049 | hvac_12 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2411 | repeat |  | 2059 | hvac_12 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2433 | repeat |  | 2049 | hvac_13 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2443 | repeat |  | 2059 | hvac_13 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2465 | repeat |  | 2049 | hvac_14 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2475 | repeat |  | 2059 | hvac_14 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2497 | repeat |  | 2049 | hvac_15 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2507 | repeat |  | 2059 | hvac_15 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2529 | repeat |  | 2049 | hvac_16 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2539 | repeat |  | 2059 | hvac_16 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2561 | repeat |  | 2049 | hvac_17 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2571 | repeat |  | 2059 | hvac_17 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2593 | repeat |  | 2049 | hvac_18 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2603 | repeat |  | 2059 | hvac_18 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2625 | repeat |  | 2049 | hvac_19 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2635 | repeat |  | 2059 | hvac_19 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2657 | repeat |  | 2049 | hvac_20 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2667 | repeat |  | 2059 | hvac_20 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2689 | repeat |  | 2049 | hvac_21 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2699 | repeat |  | 2059 | hvac_21 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2721 | repeat |  | 2049 | hvac_22 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2731 | repeat |  | 2059 | hvac_22 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2753 | repeat |  | 2049 | hvac_23 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2763 | repeat |  | 2059 | hvac_23 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2785 | repeat |  | 2049 | hvac_24 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2795 | repeat |  | 2059 | hvac_24 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2817 | repeat |  | 2049 | hvac_25 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2827 | repeat |  | 2059 | hvac_25 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2849 | repeat |  | 2049 | hvac_26 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2859 | repeat |  | 2059 | hvac_26 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2881 | repeat |  | 2049 | hvac_27 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2891 | repeat |  | 2059 | hvac_27 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2913 | repeat |  | 2049 | hvac_28 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2923 | repeat |  | 2059 | hvac_28 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2945 | repeat |  | 2049 | hvac_29 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2955 | repeat |  | 2059 | hvac_29 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2977 | repeat |  | 2049 | hvac_30 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2987 | repeat |  | 2059 | hvac_30 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 3009 | repeat |  | 2049 | hvac_31 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 3019 | repeat |  | 2059 | hvac_31 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 3041 | repeat |  | 2049 | hvac_32 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 3051 | repeat |  | 2059 | hvac_32 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 3073 | repeat |  | 2049 | hvac_33 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 3083 | repeat |  | 2059 | hvac_33 | [11 empty] | /components/hvac_params |  | Yes
BMS Information | [14 empty] | bms_info | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Status of Connection Process | Status | 5.BMS_info | Input Register |  |  |  |  | 0x1200 |  | 4608 | uint16 |  |  | connection_status | [11 empty] | /components/bms_info | connection_status | Yes |  | 0x1: Start Connection 0x2: Connection Successful 0x3: Process End
Rack Enable Status | Status | 5.BMS_info | Holding Register |  |  |  |  | 0x1201 |  | 4609 | uint16 |  |  | rack_enable_status | [11 empty] | /components/bms_info | rack_enable_status | Yes
Rack Request Step in | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1202 |  | 4610 | uint16 |  |  | rack_request_step_in | [11 empty] | /components/bms_info | rack_request_step_in | Yes
Rack Request Step out | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1203 |  | 4611 | uint16 |  |  | rack_request_quit_out | [11 empty] | /components/bms_info | rack_request_quit_out | Yes
Allow Quit out Step in Status | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1204 |  | 4612 | uint16 |  |  | rack_request_status | [11 empty] | /components/bms_info | rack_request_status | Yes
System Operation State | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1205 |  | 4613 | uint16 |  |  | system_operation_state | [11 empty] | /components/bms_info | system_operation_state | Yes |  | 0: Normal (the system can be discharged and can be charged);-The self-test is completed and the BMS transition status is normal 1: No charge (the system can be discharged and cannot be charged); 2: No discharge (the system can be charged and cannot be discharged); 3: Standby (system cannot be charged and discharged);-PCS needs standby processing 4.PCS shall stop working, BMS also will trip protection by open contactor, after crtical alarm.
System Charge State | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1206 |  | 4614 | uint16 |  |  | system_charge_state | [11 empty] | /components/bms_info | system_charge_state | Yes |  | 0x0: Idle; 0x1: Discharging; 0x2: Charging
BAU Alarm State | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1207 |  | 4615 | uint16 |  |  | bau_alarm_state | [11 empty] | /components/bms_info | bau_alarm_state | Yes |  | 0: 正常, 1: 报警; note the chinese we may need to remember (0: Normal, 1: Alarm; ) Bit0:BMS internal communication failure Bit1: Reserved Bit2: Reserved Bit3: Reserved Bit4: Racks vol diff over large warning; Bit5: Racks current diff over large warning; Bit6: Emergency stop Bit7~Bit15: Reserved
Rack Warning | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1208 |  | 4616 | uint16 |  |  | rack_warning | [11 empty] | /components/bms_info | rack_warning | Yes |  | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh warn bit1: RackVolLow warn bit2 CellVolHigh Warn bit3: CellVolLow Warn Bit4：DsgOverCurr Warn Bit5：ChgOverCurr Warn bit6: DsgTempHigh Warn bit7: DsgTempLow Warn Bit8: ChgTempHigh Warn Bit9: ChgTempLow Warn Bit10: InsulationLow warn Bit11: TerminalTempHigh Warn Bit12: HVBTempHigh warn Bit13: CellVolDiffHigh warn Bit14: CellTempDiffHigh warn
Rack Alarm | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1209 |  | 4617 | uint16 |  |  | rack_alarm | [11 empty] | /components/bms_info | rack_alarm | Yes |  | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh Alarm bit1: RackVolLow Alarm bit2: CellVolHigh Alarm bit3: CellVolLow Alarm Bit4：DsgOverCurr Alarm Bit5：ChgOverCurr Alarm bit6: DsgTempHigh Alarm bit7: DsgTempLow Alarm Bit8: ChgTempHigh Alarm Bit9: ChgTempLow Alarm Bit10: InsulationLow Alarm Bit11: TerminalTempHigh Warn Bit12: HVBTempHigh Alarm Bit13:CellVolDiffHigh Alarm Bit14:CellTempDiffHigh Alarm
Rack Critical Alarm | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120A |  | 4618 | uint16 |  |  | rack_critical_alarm | [11 empty] | /components/bms_info | rack_critical_alarm | Yes |  | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh CriticalAlarm bit1: RackVolLowCritical Alarm bit2: CellVolHigh Critical Alarm bit3: CellVolLow Critical Alarm Bit4：DsgOverCurr Critical Alarm Bit5：ChgOverCurr Critical Alarm bit6: DsgTempHigh Critical Alarm bit7: DsgTempLow Critical Alarm Bit8: ChgTempHigh Critical Alarm Bit9: ChgTempLow Critical Alarm Bit10: InsulationLow CriticalAlarm Bit11: TerminalTempHigh Critical Alarm Bit12: HVBTempHigh Critical Alarm Bit13: CellVolDiffHigh Critical Alarm Bit14: CellTempDiffHigh Critical Alarm
System Total Voltage | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120B | 10 | 4619 | uint16 |  |  | system_total_voltage | [11 empty] | /components/bms_info | system_total_voltage | Yes |  | 0.1 volt
System Total Current | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120C | 10 | 4620 | int16 |  |  | system_total_current | [11 empty] | /components/bms_info | system_total_current | Yes |  | 101 if all racks disabled
System SOC | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120D | 10 | 4621 | uint16 |  |  | system_soc | [11 empty] | /components/bms_info | system_soc | Yes
System SOH | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120E | 10 | 4622 | uint16 |  |  | system_soh | [11 empty] | /components/bms_info | system_soh | Yes
System Insulation | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120F |  | 4623 | uint16 |  |  | system_insulation | [11 empty] | /components/bms_info | system_insulation | Yes
System Enable Charge Energy | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1210 |  | 4624 | uint16 |  |  | system_enable_charge_energy | [11 empty] | /components/bms_info | system_enable_charge_energy | Yes
System Enable Discharge Energy | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1211 |  | 4625 | uint16 |  |  | system_enable_discharge_energy | [11 empty] | /components/bms_info | system_enable_discharge_energy | Yes
System Enable Max Charge Current | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1212 |  | 4626 | uint16 |  |  | system_max_charge_current | [11 empty] | /components/bms_info | system_max_charge_current | Yes
System Enable Max Discharge Current | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1213 |  | 4627 | int16 |  |  | system_max_discharge_current | [11 empty] | /components/bms_info | system_max_discharge_current | Yes
Rack Current Difference | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1214 | 10 | 4628 | int16 |  |  | rack_cell_current_difference | [11 empty] | /components/bms_info | rack_cell_current_difference | Yes |  | the current diff between enabled racks' Max and Min current
Rack Voltage Difference | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1215 | 10 | 4629 | uint16 |  |  | rack_cell_voltage_difference | [11 empty] | /components/bms_info | rack_cell_voltage_difference | Yes |  | the rack voltage diff between enabled racks' Max and Min voltage
System Max Vol Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1216 |  | 4630 | uint16 |  |  | system_max_volt_cell_rack_id | [11 empty] | /components/bms_info | system_max_volt_cell_rack_id | Yes
System Max Vol Cell Slave ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1217 |  | 4631 | uint16 |  |  | system_max_volt_cell_module_id | [11 empty] | /components/bms_info | system_max_volt_cell_module_id | Yes
System Max Vol Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1218 |  | 4632 | uint16 |  |  | system_max_volt_cell_id | [11 empty] | /components/bms_info | system_max_volt_cell_id | Yes
System Max Cell Voltage | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1219 | 1000 | 4633 | uint16 |  |  | system_max_cell_voltage | [11 empty] | /components/bms_info | system_max_cell_voltage | Yes |  | mV
System Min Vol Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121A |  | 4634 | uint16 |  |  | system_min_volt_cell_rack_id | [11 empty] | /components/bms_info | system_min_volt_cell_rack_id | Yes
System Min Vol Cell Slave ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121B |  | 4635 | uint16 |  |  | system_min_volt_cell_module_id | [11 empty] | /components/bms_info | system_min_volt_cell_module_id | Yes
System Min Vol Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121C |  | 4636 | uint16 |  |  | system_min_volt_cell_id | [11 empty] | /components/bms_info | system_min_volt_cell_id | Yes
System Min Cell Voltage | Control | 5.BMS_info | Holding Register | % |  | 100 |  | 0x121D | 1000 | 4637 | uint16 |  |  | system_min_cell_voltage | [11 empty] | /components/bms_info | system_min_cell_voltage | Yes |  | mV
System Average voltage | Control | 5.BMS_info | Holding Register | % |  | 100 |  | 0x121E | 1000 | 4638 | uint16 |  |  | system_avg_voltage | [11 empty] | /components/bms_info | system_avg_voltage | Yes |  | mV
System Max Temp Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121F |  | 4639 | uint16 |  |  | system_max_temp_cell_rack_id | [11 empty] | /components/bms_info | system_max_temp_cell_rack_id | Yes
System Max Temp Cell Slave ID | Control | 5.BMS_info | Holding Register |  |  | 100 |  | 0x1220 |  | 4640 | uint16 |  |  | system_max_temp_cell_module_id | [11 empty] | /components/bms_info | system_max_temp_cell_module_id | Yes
System Max Temp Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1221 |  | 4641 | uint16 |  |  | system_max_temp_cell_id | [11 empty] | /components/bms_info | system_max_temp_cell_id | Yes
System Max Cell Temperature | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1222 | 10 | 4642 | int16 |  |  | system_max_cell_temperature | [11 empty] | /components/bms_info | system_max_cell_temperature | Yes |  | deg
System Min Temp Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1223 |  | 4643 | uint16 |  |  | system_min_temp_cell_rack_id | [11 empty] | /components/bms_info | system_min_temp_cell_rack_id | Yes
System Min Temp Cell Slave ID | Control | 5.BMS_info | Holding Register | V |  |  |  | 0x1224 |  | 4644 | uint16 |  |  | system_min_temp_cell_module_id | [11 empty] | /components/bms_info | system_min_temp_cell_module_id | Yes
System Min Temp Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1225 |  | 4645 | uint16 |  |  | system_min_temp_cell_id | [11 empty] | /components/bms_info | system_min_temp_cell_id | Yes
System Min Cell Temperature | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1226 | 10 | 4646 | int16 |  |  | system_min_cell_temperature | [11 empty] | /components/bms_info | system_min_cell_temperature | Yes |  | deg
System Average Temperature | Control | 5.BMS_info | Holding Register | % |  | 10 |  | 0x1227 | 10 | 4647 | int16 |  |  | system_avg_temperature | [11 empty] | /components/bms_info | system_avg_temperature | Yes
BAU BCU Communication Fault Alarm 1 | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1228 |  | 4648 | uint16 |  |  | bau_bcu_comm_fault_alarm_1 | [11 empty] | /components/bms_info | bau_bcu_comm_fault_alarm_1 | Yes |  | bit0:BCU1 … bit15: bcu16
BAU BCU Communication Fault Alarm 2 | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x1229 |  | 4649 | uint16 |  |  | bau_bcu_comm_fault_alarm_2 | [11 empty] | /components/bms_info | bau_bcu_comm_fault_alarm_2 | Yes |  | bit0:BCU17 … bit15: bcu32
BAU output dry contact status | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x122A |  | 4650 | uint16 |  |  | bau_output_dry_contact_status | [7 empty] | 0：closed,1:opend Bit0: Dry contact1 state; Bit1: Dry contact2 statet; |  |  |  | /components/bms_info | bau_output_dry_contact_status | Yes
Rack enable / disable status 2 Rack Enable Status2 | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x122B |  | 4651 | uint16 |  |  | rack_enable_disable_status_1 | [11 empty] | /components/bms_info | rack_enable_disable_status_1 | Yes
Rack Request Step-in 2 | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x122C |  | 4652 | uint16 |  |  | rack_request_step_in_1 | [11 empty] | /components/bms_info | rack_request_step_in_1 | Yes
RACK request quit-in 2 Rack Request Quit-out 2 | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x122D |  | 4653 | uint16 |  |  | rack_request_quit_in_1 | [11 empty] | /components/bms_info | rack_request_quit_in_1 | Yes
RACK xxxx step-in quit-in status2 Status of Allow Quit-out /Step-in 2 | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x122E |  | 4654 | uint16 |  |  | rack_request_status_quit_in_1 | [11 empty] | /components/bms_info | rack_request_status_quit_in_1 | Yes
Accum Charge Energy MSB | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x122F |  | 4655 | uint16 |  |  | accumulation_charge_energy_msb | [11 empty] | /components/bms_info | accumulation_charge_energy_msb | Yes
Accum Charge Energy LSB | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1230 |  | 4656 | uint16 |  |  | accumulation_charge_energy_lsb | [11 empty] | /components/bms_info | accumulation_charge_energy_lsb | Yes
Accum Discharge Energy MSB | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1231 |  | 4657 | uint16 |  |  | accumulation_discharge_energy_msb | [11 empty] | /components/bms_info | accumulation_discharge_energy_msb | Yes
Accum Discharge Energy LSB | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1232 |  | 4658 | uint16 |  |  | accumulation_discharge_energy_lsb | [11 empty] | /components/bms_info | accumulation_discharge_energy_lsb | Yes
Number of Racks in Service | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1233 |  | 4659 | uint16 |  |  | number_of_racks_inservice | [11 empty] | /components/bms_info | number_of_racks_inservice | Yes
Number ot Total Racks | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1234 |  | 4660 | uint16 |  |  | number_of_racks_total | [11 empty] | /components/bms_info | number_of_racks_total | Yes
Min Number of Parallel Racks | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1235 |  | 4661 | uint16 |  |  | min_number_of_parallel_racks | [11 empty] | /components/bms_info | min_number_of_parallel_racks | Yes
Max discharge power | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1236 |  | 4662 | uint16 |  |  | max_discharge_power | [11 empty] | /components/bms_info | max_discharge_power | Yes
Max charge power | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1237 |  | 4663 | uint16 |  |  | max_charge_power | [11 empty] | /components/bms_info | max_charge_power | Yes
BMS heart beat | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1238 |  | 4664 | uint16 |  |  | bms_heartbeat | [11 empty] | /components/bms_info | bms_heartbeat | Yes | 15 acc every second
Start Connection | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1300 |  | 4864 | uint16 |  |  | start_connection | [11 empty] | /components/bms_info | start_connection | Yes | 0.1 to 15 s , 0 to 150
Insulation sampling function switch | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1301 |  | 4865 | uint16 |  |  | Insulation_sampling_function_switch | [11 empty] | /components/bms_info | Insulation_sampling_function_switch | Yes
reset PCS control fail alarm | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1302 |  | 4866 | uint16 |  |  | reset_pcs_control fail_alarm | [11 empty] | /components/bms_info | reset_pcs_control fail_alarm | Yes
Minimum number of parallel racks | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1303 |  | 4867 | uint16 |  |  | minimum_number_of_parallel_racks | [11 empty] | /components/bms_info | minimum_number_of_parallel_racks | Yes
BMS Rack | [14 empty] | bms_rack | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Rack Run State | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0000 |  | 0 | uint16 |  |  | rack_run_state | [11 empty] | /components/bms_rack |  | Yes | 0: Normal (Can charge & discharge) 1: NO Charge (Can discharge) 2: NO Discharge (Can charge) 3: Standby (Not charge or discharge) 4: Stop (System stop operation, open contactors, breakers)
Rack Precharge Phase | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0001 |  | 1 | uint16 |  |  | rack_precharge_phase | [11 empty] | /components/bms_rack |  | Yes | 0: Disconnected (positive contactor, negative contactor, precharge coontactor open) 1: Start connection (precharge contactor closed, negative contactor closed, positive contactor open) 2: Connecting (precharge contactor closed, negative contactor closed, positive contactor closed) 3:Connected(precharge contactoropen, negative contactor closed, positive contactor closed) 4:Connection fail
Rack Connection State | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0002 |  | 2 | uint16 |  |  | rack_connection_state | [11 empty] | /components/bms_rack |  | Yes | 0x0: Opened, 0x1: Closed: Bit0: Positive contactor state; Bit1: PreContactor state; Bit2: Negative contactor state; Bit3: Disconnector state;
Rack Alarm Info | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0003 |  | 3 | uint16 |  |  | rack_alarm_info | [11 empty] | /components/bms_rack |  | Yes | 0x0: Normal, 0x1: Fault; Bit0: BMU hardware fault; Bit1: Bcu hardware; Bit2: Fuse protector fault; Bit3: Contactor adhesion fault; Bit4: BMU communication fault; Bit5: BAU communication fault; Bit6: Current sensor fault; Bit7: IMD fault; Bit8: Disconnector Open when Rack Enabled; Bit9-bit15: reserve;
Rack Warning | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0004 |  | 4 | uint16 |  |  | rack_warning | [11 empty] | /components/bms_rack |  | Yes | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh warn bit1: RackVolLow warn bit2: CellVolHigh Warn bit3: CellVolLow Warn Bit4: DsgOverCurr Warn Bit5: ChgOverCurr Warn bit6: DsgTempHigh Warn bit7: DsgTempLow Warn Bit8: ChgTempHigh Warn Bit9: ChgTempLow Warn Bit10: InsulationLow warn Bit11: TerminalTempHigh Warn Bit12: HVBTempHigh warn Bit13: CellVolDiffHigh warn Bit14: CellTempDiffHigh warn
Rack Alarm | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0005 |  | 5 | uint16 |  |  | rack_alarm | [11 empty] | /components/bms_rack |  | Yes | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh Alarm bit1: RackVolLow Alarm bit2: CellVolHigh Alarm bit3: CellVolLow Alarm Bit4: DsgOverCurr Alarm Bit5: ChgOverCurr Alarm bit6: DsgTempHigh Alarm bit7: DsgTempLow Alarm Bit8: ChgTempHigh Alarm Bit9: ChgTempLow Alarm Bit10: InsulationLow Alarm Bit11: TerminalTempHigh Warn Bit12: HVBTempHigh Alarm Bit13: CellVolDiffHigh Alarm Bit14: CellTempDiffHigh Alarm
Rack Critical Alarm | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0006 |  | 6 | uint16 |  |  | rack_critical_alarm | [11 empty] | /components/bms_rack |  | Yes | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh CriticalAlarm bit1: RackVolLowCritical Alarm bit2: CellVolHigh Critical Alarm bit3: CellVolLow Critical Alarm Bit4: DsgOverCurr Critical Alarm Bit5: ChgOverCurr Critical Alarm bit6: DsgTempHigh Critical Alarm bit7: DsgTempLow Critical Alarm Bit8: ChgTempHigh Critical Alarm Bit9: ChgTempLow Critical Alarm Bit10: InsulationLow CriticalAlarm Bit11: TerminalTempHigh Critical Alarm Bit12: HVBTempHigh Critical Alarm Bit13: CellVolDiffHigh Critical Alarm Bit14: CellTempDiffHigh Critical Alarm
Reason of Rack 1 Step-in Failure | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0007 |  | 7 | uint16 |  |  | rack_step_in_failure | [11 empty] | /components/bms_rack |  | Yes | 0:normal,1:warning Bit0: Rack Vol Diff Large Bit1: SMS Confirmation Overtime
Reserved 1 | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0008 |  | 8 | uint16 |  |  | reserved_1 | [11 empty] | /components/bms_rack |  | No
Precharge Total Voltage | Status | 6.bms_rack | Input Register | 0.1V |  |  |  | 0x0009 |  | 9 | uint16 |  |  | precharge_total_vol | [11 empty] | /components/bms_rack |  | Yes
Rack Voltage | Status | 6.bms_rack | Input Register | 0.1V |  |  |  | 0x000A |  | 10 | uint16 |  |  | rack_voltage | [11 empty] | /components/bms_rack |  | Yes
Rack Current | Status | 6.bms_rack | Input Register | 0.1A |  |  |  | 0x000B |  | 11 | int16 |  |  | rack_current | [11 empty] | /components/bms_rack |  | Yes | Charge current is negative and discharge is positive.
Rack Charge/Discharge State | Status | 6.bms_rack | Input Register |  |  |  |  | 0x000C |  | 12 | uint16 |  |  | rack_state | [11 empty] | /components/bms_rack |  | Yes | 0x0: IDle; 0x1: Discharging; 0x2: Charging
Rack SOC | Status | 6.bms_rack | Input Register | % |  |  |  | 0x000D |  | 13 | uint16 |  |  | rack_soc | [11 empty] | /components/bms_rack |  | Yes | 0 - 1000
Rack SOH | Status | 6.bms_rack | Input Register | % |  |  |  | 0x000E |  | 14 | uint16 |  |  | rack_soh | [11 empty] | /components/bms_rack |  | Yes | 0 - 1000
Rack Insulation Value | Status | 6.bms_rack | Input Register | kΩ |  |  |  | 0x000F |  | 15 | uint16 |  |  | rack_insulation | [11 empty] | /components/bms_rack |  | Yes | Fixed value before contactor close; BMS IMD Disabled after contactor close.
Rack Positive Insulation Value | Status | 6.bms_rack | Input Register | kΩ |  |  |  | 0x0010 |  | 16 | uint16 |  |  | rack_positive_insulation | [11 empty] | /components/bms_rack |  | Yes | Fixed value before contactor close; BMS IMD Disabled after contactor close.
Rack Negative Insulation Value | Status | 6.bms_rack | Input Register | kΩ |  |  |  | 0x0011 |  | 17 | uint16 |  |  | rack_negative_insulation | [11 empty] | /components/bms_rack |  | Yes | Fixed value before contactor close; BMS IMD Disabled after contactor close.
Rack Max Charge Current | Status | 6.bms_rack | Input Register | 0.1A |  |  |  | 0x0012 |  | 18 | uint16 |  |  | rack_max_charge_current | [11 empty] | /components/bms_rack |  | Yes | Fixed Value depends on project, same as threshold of rack over current alarm
Rack Max Discharge Current | Status | 6.bms_rack | Input Register | 0.1A |  |  |  | 0x0013 |  | 19 | uint16 |  |  | rack_max_discharge_current | [11 empty] | /components/bms_rack |  | Yes | Fixed Value depends on project, same as threshold of rack over current alarm
Rack Max Vol Cell ID | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0014 |  | 20 | uint16 |  |  | rack_max_cell_id | [11 empty] | /components/bms_rack |  | Yes | 1#～N#（N is Cell number)
Rack Max Cell Voltage | Status | 6.bms_rack | Input Register | mV |  |  |  | 0x0015 |  | 21 | uint16 |  |  | rack_max_cell_voltage | [11 empty] | /components/bms_rack |  | Yes
Rack Min Vol Cell ID | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0016 |  | 22 | uint16 |  |  | rack_min_cell_id | [11 empty] | /components/bms_rack |  | Yes | 1#～N#（N is Cell number)
Rack Min Cell Voltage | Status | 6.bms_rack | Input Register | mV |  |  |  | 0x0017 |  | 23 | uint16 |  |  | rack_min_cell_voltage | [11 empty] | /components/bms_rack |  | Yes
Rack Max Temperature Cell ID | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0018 |  | 24 | uint16 |  |  | rack_max_cell_temperature_id | [11 empty] | /components/bms_rack |  | Yes | 1#～N#（N is Cell number)
Rack Max Cell Temperature | Status | 6.bms_rack | Input Register | 0.1°C |  |  |  | 0x0019 |  | 25 | int16 |  |  | rack_max_cell_temperature | [11 empty] | /components/bms_rack |  | Yes
Rack Min Temperature Cell ID | Status | 6.bms_rack | Input Register |  |  |  |  | 0x001A |  | 26 | uint16 |  |  | rack_min_cell_temperature_id | [11 empty] | /components/bms_rack |  | Yes | 1#～N#（N is Cell number)
Rack Min Cell Temperature | Status | 6.bms_rack | Input Register | 0.1°C |  |  |  | 0x001B |  | 27 | int16 |  |  | rack_min_cell_temperature | [11 empty] | /components/bms_rack |  | Yes
Rack Average Voltage | Status | 6.bms_rack | Input Register | mV |  |  |  | 0x001C |  | 28 | uint16 |  |  | rack_avg_voltage | [11 empty] | /components/bms_rack |  | Yes
Rack Average Temperature | Status | 6.bms_rack | Input Register | 0.1°C |  |  |  | 0x001D |  | 29 | int16 |  |  | rack_avg_temperature | [11 empty] | /components/bms_rack |  | Yes
BMS Rack Controls | [14 empty] | bms_rack_controls | TRUE | life_signal | life | 200 | 200 |  | 20 | 98
Rack Enable/Disable | Control | 6.bms_rack | Holding Register |  |  |  |  | 0x0200 |  | 512 | uint16 |  |  | rack_enable | [11 empty] | /components/bms_rack |  | Yes | "BMS I/O List shall be strongly according to physical racks; If use 4 Battery Rack I/O list to test 1 Battery rack, must only enable one rack, otherwise, calculation will be wrong. Two racks connected, enable rack 1 and rack 2, can't to enable rack 1 and rack 4, must exactly follow digtal sequence. ""Disable"" is only for disable battery rack which can't be used at moment; It shall not be applied to disconnect battery rack, otherwise, data log, record, and analysis will be affected." | 1: enable; 2: disable
EMS Allow Rack Step-in | Control | 6.bms_rack | Holding Register |  |  |  |  | 0x0201 |  | 513 | uint16 |  |  | close_contactor | [11 empty] | /components/bms_rack |  | Yes | Close Contactor (must enable first) | 1: allow step-in; 0: no step-in allowed
EMS Allow Rack Quit-out | Control | 6.bms_rack | Holding Register |  |  |  |  | 0x0202 |  | 514 | uint16 |  |  | open_contactor | [11 empty] | /components/bms_rack |  | Yes | Open Contactor | 1: allow step-out; 0: no step-out allowed
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A13: Tony Olivo: Do not add rows below this line, the script will break
Note on A14: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B14: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D14: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E14: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F14: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G14: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H14: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J14: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on K14: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on L14: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on M14: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on N14: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on O14: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Y14: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on Z14: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AA14: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AB14: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AC14: Tony Olivo: Yes/No whether to include in the client/server config
Note on AD14: Tony Olivo: For humans
Note on AE14: Tony Olivo: For humans
Note on AF14: Tony Olivo: Ranges are for humans only

## Original
Connection Name | Risen BMS 340
Device Name | Risen BMS 340
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device ID String | risen_bms_340
ip_address | 192.168.112.10
port | 502
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical) | [23 empty] | OPTIONAL for web_ui configs only |  | required for modbus server configs only
Name | Type | Ref | Register Type | Unit | Words | Bus Scale | FIMS Scale | hexAddress | Scale | Address | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
System Run Information | [14 empty] | ems_running_info | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
System Status | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0101 |  | 257 | uint16 |  |  | sys_status | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
BMS Alarm | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0102 |  | 266 | uint16 |  |  | bms_alarms | [11 empty] | /components/ems_running_info |  | Yes
Heartbeat | Status | 2.sys_run_info | Input Register |  | 2 |  |  | 0x0116 |  | 278 | uint16 |  |  | heartbeat | [11 empty] | /components/ems_running_info |  | Yes | [0, 2^32 - 1]
EMS Communication State | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0118 |  | 280 | uint16 |  |  | ems_comms_state | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal
BMS Communication State | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0119 |  | 281 | uint16 |  |  | bms_comms_state | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal By bits bit0: BMS2
AC Communication State 1 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011B |  | 283 | uint16 |  |  | ac_comms_state_1 | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal By bits bit0: HVAC1, bit1: HVAC3
AC Communication State 2 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011C |  | 284 | uint16 |  |  | ac_comms_state_2 | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal
AC Communication State 3 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011D |  | 285 | uint16 |  |  | ac_comms_state_3 | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal
FSS Communication State | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x011F |  | 287 | uint16 |  |  | fss_comms_state | [11 empty] | /components/ems_running_info |  | Yes |  | 1: Normal, 0: Abnormal By bits bit0: FSS comms state
Year | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012A |  | 298 | uint16 |  |  | year | [11 empty] | /components/ems_running_info |  | Yes | [0-99]
Month | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012B |  | 299 | uint16 |  |  | month | [11 empty] | /components/ems_running_info |  | Yes | [1-12]
Day | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012C |  | 300 | uint16 |  |  | day | [11 empty] | /components/ems_running_info |  | Yes | [1-31]
Hour | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012D |  | 301 | uint16 |  |  | hour | [11 empty] | /components/ems_running_info |  | Yes | [0-23]
Minute | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012E |  | 302 | uint16 |  |  | minute | [11 empty] | /components/ems_running_info |  | Yes | [0-59]
Second | Status | 2.sys_run_info | Holding Register |  |  |  |  | 0x012F |  | 303 | uint16 |  |  | second | [11 empty] | /components/ems_running_info |  | Yes | [0-59]
Environment Alarms 1 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0140 |  | 320 | uint16 |  |  | env_alarms_1 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 1 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 1 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 1 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 1 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 1 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 1 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 2 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 2 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 2 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 2 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 2 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 2 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 2 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0141 |  | 321 | uint16 |  |  | env_alarms_2 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 3 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 3 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 3 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 3 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 3 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 3 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 4 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 4 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 4 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 4 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 4 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 4 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 3 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0142 |  | 322 | uint16 |  |  | env_alarms_3 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 5 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 5 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 5 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 5 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 5 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 5 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 6 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 6 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 6 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 6 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 6 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 6 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 4 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0143 |  | 323 | uint16 |  |  | env_alarms_4 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 7 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 7 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 7 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 7 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 7 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 7 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 8 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 8 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 8 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 8 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 8 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 8 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 5 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0144 |  | 324 | uint16 |  |  | env_alarms_5 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 9 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 9 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 9 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 9 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 9 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 9 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 10 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 10 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 10 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 10 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 10 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 10 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 6 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0145 |  | 325 | uint16 |  |  | env_alarms_6 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 11 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 11 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 11 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 11 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 11 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 11 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 12 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 12 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 12 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 12 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 12 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 12 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 7 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0146 |  | 326 | uint16 |  |  | env_alarms_7 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 13 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 13 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 13 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 13 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 13 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 13 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 14 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 14 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 14 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 14 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 14 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 14 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 8 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0147 |  | 327 | uint16 |  |  | env_alarms_8 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 15 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 15 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 15 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 15 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 15 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 15 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 16 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 16 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 16 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 16 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 16 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 16 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Environment Alarms 9 | Status | 2.sys_run_info | Input Register |  |  |  |  | 0x0148 |  | 328 | uint16 |  |  | env_alarms_9 | [11 empty] | /components/ems_running_info |  | Yes |  | Bit0: cabinet 17 temperature alarm (0: disappear, 1: appear) Bit1: cabinet 17 temperature sensor fault (0: disappear, 1: appear) Bit2: cabinet 17 smoke alarm (0: disappear, 1: appear) Bit3: cabinet 17 labyrinth pollution fault (0: disappear, 1: appear) Bit4: cabinet 17 smoke sensor failure (0: disappear, 1: appear) Bit5: cabinet 17 fire gas release (0: disappear, 1: appear) Bit6: reserved Bit7: reserved Bit8: cabinet 18 temperature alarm (0: disappear, 1: appear) Bit9: cabinet 18 temperature sensor fault (0: disappear, 1: appear) Bit10: cabinet 18 smoke alarm (0: disappear, 1: appear) Bit11: cabinet 18 labyrinth pollution fault (0: disappear, 1: appear) Bit12: cabinet 18 smoke sensor failure (0: disappear, 1: appear) Bit13: cabinet 18 fire gas release (0: disappear, 1: appear) Bit14: reserved Bit15: reserved
Battery Cabinet Air Conditioning Relay | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0180 |  | 384 | uint16 |  |  | batt_cabinet_air_conditioning_relay | [11 empty] | /components/ems_running_info |  | Yes |  | 1: relay close, 0: relay open
BCP Cabinet Air Conditioning Relay | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0181 |  | 385 | uint16 |  |  | bcp_cabinet_air_conditioning_relay | [11 empty] | /components/ems_running_info |  | Yes |  | 1: relay close, 0: relay open
Shunt Trip Control of DC Load Switch | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0187 |  | 391 | uint16 |  |  | dc_load_switch_shunt_trip_ctrl | [11 empty] | /components/ems_running_info |  | Yes |  | 1: relay close, 0: relay open
Maintenance Start | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0200 |  | 512 | uint16 |  |  | maint_start | [11 empty] | /components/ems_running_info |  | Yes |  | 0: not maintenance, 1: maintenance
SOC Protect Enable | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0201 |  | 513 | uint16 |  |  | soc_protect_enable | [11 empty] | /components/ems_running_info |  | Yes |  | 0: disable, 1: enable
SOC Protect Delay | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0202 |  | 514 | uint16 |  |  | soc_protect_delay | [11 empty] | /components/ems_running_info |  | Yes | S, 0-200
SOCH2 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0203 |  | 515 | uint16 |  |  | soc_h2_alarm | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCH2 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0204 |  | 516 | uint16 |  |  | soc_h2_recovery | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCH1 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0205 |  | 517 | uint16 |  |  | soc_h1_alarm | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCH1 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0206 |  | 518 | uint16 |  |  | soc_h1_recovery | [11 empty] | /components/ems_running_info |  | Yes | [500, 1000] 0.1%
SOCL1 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0207 |  | 519 | uint16 |  |  | soc_l1_recovery | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
SOCL1 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0208 |  | 520 | uint16 |  |  | soc_l1_alarm | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
SOCL2 Recovery | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x0209 |  | 521 | uint16 |  |  | soc_l2_recovery | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
SOCL2 Alarm | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x020A |  | 522 | uint16 |  |  | soc_l2_alarm | [11 empty] | /components/ems_running_info |  | Yes | [1, 499] 0.1%
EMS Timeout of Loss of Communication | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x020B |  | 523 | uint16 |  |  | ems_comms_loss_timeout_enable | [11 empty] | /components/ems_running_info |  | Yes |  | 0: disable, 1: enable
EMS Loss of Communication Timeout | Control | 2.sys_run_info | Holding Register |  |  |  |  | 0x020C |  | 524 | uint16 |  |  | ems_comms_loss_timeout | [11 empty] | /components/ems_running_info |  | Yes | second, if 0 default 10 [1, 120]
HVAC (Air-Conditioning) Information | [14 empty] | hvac_info | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Unit Running Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0300 |  | 768 | uint16 |  |  | hvac_1_unit_running_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Internal Fan Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0301 |  | 769 | uint16 |  |  | hvac_1_internal_fan_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
External Fan Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0302 |  | 770 | uint16 |  |  | hvac_1_external_fan_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Compressor Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0303 |  | 771 | uint16 |  |  | hvac_1_compressor_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Inside Return Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x0304 |  | 772 | int16 |  |  | hvac_1_inside_return_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Reserved 1 | Status | 3.AC_info | Input Register |  |  |  |  | 0z0305 |  | 773 | uint16 |  |  | hvac_1_reserved_1 | [11 empty] | /components/hvac_info |  | No
Outside Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x0306 |  | 774 | int16 |  |  | hvac_1_outside_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Condenser Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x0307 |  | 775 | int16 |  |  | hvac_1_condenser_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Reserved 2 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 776 | uint16 |  |  | hvac_1_reserved_2 | [11 empty] | /components/hvac_info |  | No
Reserved 3 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 777 | uint16 |  |  | hvac_1_reserved_3 | [11 empty] | /components/hvac_info |  | No
Reserved 4 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 778 | uint16 |  |  | hvac_1_reserved_4 | [11 empty] | /components/hvac_info |  | No
AC Input Voltage | Status | 3.AC_info | Input Register |  |  |  |  | 0x030B |  | 779 | int16 |  |  | hvac_1_ac_input_voltage | [11 empty] | /components/hvac_info |  | Yes | 1V
Reserved 5 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 780 | uint16 |  |  | hvac_1_reserved_5 | [11 empty] | /components/hvac_info |  | No
Reserved 6 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 781 | uint16 |  |  | hvac_1_reserved_6 | [11 empty] | /components/hvac_info |  | No
Emergency Air Fan State | Status | 3.AC_info | Input Register |  |  |  |  | 0x030E |  | 782 | uint16 |  |  | hvac_1_emergency_air_fan_state | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
Heat Exchanger Coil (Tubing) Temp | Status | 3.AC_info | Input Register |  |  |  |  | 0x030F |  | 783 | int16 |  |  | hvac_1_heat_exchanger_coil_temp | [11 empty] | /components/hvac_info |  | Yes | 0.1°C
Reserved 7 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 784 | uint16 |  |  | hvac_1_reserved_7 | [11 empty] | /components/hvac_info |  | No
Reserved 8 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 785 | uint16 |  |  | hvac_1_reserved_8 | [11 empty] | /components/hvac_info |  | No
Reserved 9 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0305 |  | 786 | uint16 |  |  | hvac_1_reserved_9 | [11 empty] | /components/hvac_info |  | No
Inside Return Humidity | Status | 3.AC_info | Input Register |  |  |  |  | 0x0313 |  | 787 | uint16 |  |  | hvac_1_inside_return_humidity | [11 empty] | /components/hvac_info |  | Yes | 1%
Electrical Heating Running Status | Status | 3.AC_info | Input Register |  |  |  |  | 0x0314 |  | 788 | uint16 |  |  | hvac_1_electrical_heating_running_status | [11 empty] | /components/hvac_info |  | Yes |  | 0: Stop, 1: Running, The rest is "Null"
HVAC Alarms 1 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0315 |  | 789 | uint16 |  |  | hvac_1_alarms_1 | [11 empty] | /components/hvac_info |  | Yes |  | bit0 High Temperature Waning bit1 Low Temperature Warning bit2 High Humidity Warning bit3 Low Humidity Warning bit4 Heat Exchanger Coil (Tubing) Frost Warning bit5 Exhaust Temperature High Warning bit6 Heat Exchanger Coil (Tubing) Temperature sensing failure Warning bit7 Exterior Temperature sensing failure Warning bit8 Condensation Temperature sensing failure warning bit9 Interior Temperature sensing failure warning bit10 Exhaust Temperature sensing failure warning bit11 Humidity sensing failure warning bit12 Interior fan failure warning bit13 Exterior fan failure warning bit14 Compressor failure warning bit15 Electric hearing failure warning
HVAC Alarms 2 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0316 |  | 790 | uint16 |  |  | hvac_1_alarms_2 | [11 empty] | /components/hvac_info |  | Yes |  | bit0 Emergency air fan failure warning bit1 High air pressure warning bit2 Low air pressure warning bit3 Flood warning bit4 Smoke warning bit5 Door open warning bit6 High air pressure lockdown warning bit7 Low air Pressure lockdown warning bit8 Exhaust lockdown warning bit9 AC high voltage warning bit10 AC low voltage warning bit11 AC drop out warning bit12 Phase loss warning bit13 Freq. abnormal warning bit14 Phase reversal warning bit15 DC high voltage warning
HVAC Alarms 3 | Status | 3.AC_info | Input Register |  |  |  |  | 0x0317 |  | 791 | uint16 |  |  | hvac_1_alarms_3 | [11 empty] | /components/hvac_info |  | Yes |  | bit0 DC low voltage warning
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 800 | repeat |  | 768 | hvac_2 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 832 | repeat |  | 768 | hvac_3 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 864 | repeat |  | 768 | hvac_4 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 896 | repeat |  | 768 | hvac_5 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 928 | repeat |  | 768 | hvac_6 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 960 | repeat |  | 768 | hvac_7 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 992 | repeat |  | 768 | hvac_8 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1024 | repeat |  | 768 | hvac_9 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1056 | repeat |  | 768 | hvac_10 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1088 | repeat |  | 768 | hvac_11 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1120 | repeat |  | 768 | hvac_12 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1152 | repeat |  | 768 | hvac_13 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1184 | repeat |  | 768 | hvac_14 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1216 | repeat |  | 768 | hvac_15 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1248 | repeat |  | 768 | hvac_16 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1280 | repeat |  | 768 | hvac_17 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1312 | repeat |  | 768 | hvac_18 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1344 | repeat |  | 768 | hvac_19 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1376 | repeat |  | 768 | hvac_20 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1408 | repeat |  | 768 | hvac_21 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1440 | repeat |  | 768 | hvac_22 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1472 | repeat |  | 768 | hvac_23 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1504 | repeat |  | 768 | hvac_24 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1536 | repeat |  | 768 | hvac_25 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1568 | repeat |  | 768 | hvac_26 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1600 | repeat |  | 768 | hvac_27 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1632 | repeat |  | 768 | hvac_28 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1664 | repeat |  | 768 | hvac_29 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1696 | repeat |  | 768 | hvac_30 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1728 | repeat |  | 768 | hvac_31 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1760 | repeat |  | 768 | hvac_32 | [11 empty] | /components/hvac_info |  | Yes
hvac_1 | Status | 3.AC_info | Input Register |  | 23 |  |  |  |  | 1792 | repeat |  | 768 | hvac_33 | [11 empty] | /components/hvac_info |  | Yes
HVAC (Air-Conditioning) Parameters | [14 empty] | hvac_params | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Remote AC On | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0801 |  | 2049 | uint16 |  |  | hvac_1_remote_ac_on | [11 empty] | /components/hvac_params |  | Yes |  | 0:off, 1:on, The reset is NULL
Cooling Temp Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0802 |  | 2050 | uint16 |  |  | hvac_1_cooling_temp_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Cooling Set-point Upper Limit | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0803 |  | 2051 | uint16 |  |  | hvac_1_cooling_setpoint_upper_limit | [11 empty] | /components/hvac_params |  | Yes | 1°C
HT Warning Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0804 |  | 2052 | uint16 |  |  | hvac_1_ht_warning_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
LT Warning Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0805 |  | 2053 | uint16 |  |  | hvac_1_lt_warning_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Interior Air Fan Stop Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x0806 |  | 2054 | uint16 |  |  | hvac_1_interior_air_fan_stop_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Heating Temp Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x080B |  | 2059 | uint16 |  |  | hvac_1_heating_temp_setting | [11 empty] | /components/hvac_params |  | Yes | 1°C
Heating Setpoint Lower Limit | Control | 4.ACParam | Holding Register |  |  |  |  | 0x080C |  | 2060 | uint16 |  |  | hvac_1_heating_setpoint_lower_limit | [11 empty] | /components/hvac_params |  | Yes | 1°C
De-humidify Setting | Control | 4.ACParam | Holding Register |  |  |  |  | 0x080D |  | 2061 | uint16 |  |  | hvac_1_dehumidify_setting | [11 empty] | /components/hvac_params |  | Yes | 1%
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2081 | repeat |  | 2049 | hvac_2 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2091 | repeat |  | 2059 | hvac_2 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2113 | repeat |  | 2049 | hvac_3 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2123 | repeat |  | 2059 | hvac_3 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2145 | repeat |  | 2049 | hvac_4 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2155 | repeat |  | 2059 | hvac_4 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2177 | repeat |  | 2049 | hvac_5 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2187 | repeat |  | 2059 | hvac_5 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2209 | repeat |  | 2049 | hvac_6 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2219 | repeat |  | 2059 | hvac_6 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2241 | repeat |  | 2049 | hvac_7 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2251 | repeat |  | 2059 | hvac_7 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2273 | repeat |  | 2049 | hvac_8 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2283 | repeat |  | 2059 | hvac_8 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2305 | repeat |  | 2049 | hvac_9 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2315 | repeat |  | 2059 | hvac_9 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2337 | repeat |  | 2049 | hvac_10 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2347 | repeat |  | 2059 | hvac_10 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2369 | repeat |  | 2049 | hvac_11 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2379 | repeat |  | 2059 | hvac_11 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2401 | repeat |  | 2049 | hvac_12 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2411 | repeat |  | 2059 | hvac_12 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2433 | repeat |  | 2049 | hvac_13 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2443 | repeat |  | 2059 | hvac_13 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2465 | repeat |  | 2049 | hvac_14 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2475 | repeat |  | 2059 | hvac_14 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2497 | repeat |  | 2049 | hvac_15 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2507 | repeat |  | 2059 | hvac_15 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2529 | repeat |  | 2049 | hvac_16 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2539 | repeat |  | 2059 | hvac_16 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2561 | repeat |  | 2049 | hvac_17 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2571 | repeat |  | 2059 | hvac_17 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2593 | repeat |  | 2049 | hvac_18 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2603 | repeat |  | 2059 | hvac_18 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2625 | repeat |  | 2049 | hvac_19 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2635 | repeat |  | 2059 | hvac_19 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2657 | repeat |  | 2049 | hvac_20 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2667 | repeat |  | 2059 | hvac_20 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2689 | repeat |  | 2049 | hvac_21 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2699 | repeat |  | 2059 | hvac_21 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2721 | repeat |  | 2049 | hvac_22 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2731 | repeat |  | 2059 | hvac_22 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2753 | repeat |  | 2049 | hvac_23 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2763 | repeat |  | 2059 | hvac_23 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2785 | repeat |  | 2049 | hvac_24 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2795 | repeat |  | 2059 | hvac_24 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2817 | repeat |  | 2049 | hvac_25 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2827 | repeat |  | 2059 | hvac_25 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2849 | repeat |  | 2049 | hvac_26 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2859 | repeat |  | 2059 | hvac_26 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2881 | repeat |  | 2049 | hvac_27 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2891 | repeat |  | 2059 | hvac_27 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2913 | repeat |  | 2049 | hvac_28 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2923 | repeat |  | 2059 | hvac_28 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2945 | repeat |  | 2049 | hvac_29 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2955 | repeat |  | 2059 | hvac_29 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 2977 | repeat |  | 2049 | hvac_30 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 2987 | repeat |  | 2059 | hvac_30 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 3009 | repeat |  | 2049 | hvac_31 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 3019 | repeat |  | 2059 | hvac_31 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 3041 | repeat |  | 2049 | hvac_32 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 3051 | repeat |  | 2059 | hvac_32 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 5 |  |  |  |  | 3073 | repeat |  | 2049 | hvac_33 | [11 empty] | /components/hvac_params |  | Yes
hvac_1 | Control | 4.ACParam | Holding Register |  | 2 |  |  |  |  | 3083 | repeat |  | 2059 | hvac_33 | [11 empty] | /components/hvac_params |  | Yes
BMS Information | [14 empty] | bms_info | TRUE | life_signal | life | 200 | 200 | 1000 | 20 | 98
Status of Connection Process | Status | 5.BMS_info | Input Register |  |  |  |  | 0x1200 |  | 4608 | uint16 |  |  | connection_status | [11 empty] | /components/bms_info | connection_status | Yes |  | 0x1: Start Connection 0x2: Connection Successful 0x3: Process End
Rack Enable Status | Status | 5.BMS_info | Holding Register |  |  |  |  | 0x1201 |  | 4609 | uint16 |  |  | rack_enable_status | [11 empty] | /components/bms_info | rack_enable_status | Yes
Rack Request Step in | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1202 |  | 4610 | uint16 |  |  | rack_request_step_in | [11 empty] | /components/bms_info | rack_request_step_in | Yes
Rack Request Step out | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1203 |  | 4611 | uint16 |  |  | rack_request_quit_out | [11 empty] | /components/bms_info | rack_request_quit_out | Yes
Allow Quit out Step in Status | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1204 |  | 4612 | uint16 |  |  | rack_request_status | [11 empty] | /components/bms_info | rack_request_status | Yes
System Operation State | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1205 |  | 4613 | uint16 |  |  | system_operation_state | [11 empty] | /components/bms_info | system_operation_state | Yes |  | 0: Normal (the system can be discharged and can be charged);-The self-test is completed and the BMS transition status is normal 1: No charge (the system can be discharged and cannot be charged); 2: No discharge (the system can be charged and cannot be discharged); 3: Standby (system cannot be charged and discharged);-PCS needs standby processing 4.PCS shall stop working, BMS also will trip protection by open contactor, after crtical alarm.
System Charge State | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1206 |  | 4614 | uint16 |  |  | system_charge_state | [11 empty] | /components/bms_info | system_charge_state | Yes |  | 0x0: Idle; 0x1: Discharging; 0x2: Charging
BAU Alarm State | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1207 |  | 4615 | uint16 |  |  | bau_alarm_state | [11 empty] | /components/bms_info | bau_alarm_state | Yes |  | 0: 正常, 1: 报警; note the chinese we may need to remember (0: Normal, 1: Alarm; ) Bit0:BMS internal communication failure Bit1: Reserved Bit2: Reserved Bit3: Reserved Bit4: Racks vol diff over large warning; Bit5: Racks current diff over large warning; Bit6: Emergency stop Bit7~Bit15: Reserved
Rack Warning | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1208 |  | 4616 | uint16 |  |  | rack_warning | [11 empty] | /components/bms_info | rack_warning | Yes |  | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh warn bit1: RackVolLow warn bit2 CellVolHigh Warn bit3: CellVolLow Warn Bit4：DsgOverCurr Warn Bit5：ChgOverCurr Warn bit6: DsgTempHigh Warn bit7: DsgTempLow Warn Bit8: ChgTempHigh Warn Bit9: ChgTempLow Warn Bit10: InsulationLow warn Bit11: TerminalTempHigh Warn Bit12: HVBTempHigh warn Bit13: CellVolDiffHigh warn Bit14: CellTempDiffHigh warn
Rack Alarm | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1209 |  | 4617 | uint16 |  |  | rack_alarm | [11 empty] | /components/bms_info | rack_alarm | Yes |  | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh Alarm bit1: RackVolLow Alarm bit2: CellVolHigh Alarm bit3: CellVolLow Alarm Bit4：DsgOverCurr Alarm Bit5：ChgOverCurr Alarm bit6: DsgTempHigh Alarm bit7: DsgTempLow Alarm Bit8: ChgTempHigh Alarm Bit9: ChgTempLow Alarm Bit10: InsulationLow Alarm Bit11: TerminalTempHigh Warn Bit12: HVBTempHigh Alarm Bit13:CellVolDiffHigh Alarm Bit14:CellTempDiffHigh Alarm
Rack Critical Alarm | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120A |  | 4618 | uint16 |  |  | rack_critical_alarm | [11 empty] | /components/bms_info | rack_critical_alarm | Yes |  | 0x0: Normal, 0x1: Warning; bit0: RackVolHigh CriticalAlarm bit1: RackVolLowCritical Alarm bit2: CellVolHigh Critical Alarm bit3: CellVolLow Critical Alarm Bit4：DsgOverCurr Critical Alarm Bit5：ChgOverCurr Critical Alarm bit6: DsgTempHigh Critical Alarm bit7: DsgTempLow Critical Alarm Bit8: ChgTempHigh Critical Alarm Bit9: ChgTempLow Critical Alarm Bit10: InsulationLow CriticalAlarm Bit11: TerminalTempHigh Critical Alarm Bit12: HVBTempHigh Critical Alarm Bit13: CellVolDiffHigh Critical Alarm Bit14: CellTempDiffHigh Critical Alarm
System Total Voltage | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120B | 10 | 4619 | uint16 |  |  | system_total_voltage | [11 empty] | /components/bms_info | system_total_voltage | Yes |  | 0.1 volt
System Total Current | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120C | 10 | 4620 | int16 |  |  | system_total_current | [11 empty] | /components/bms_info | system_total_current | Yes |  | 101 if all racks disabled
System SOC | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120D | 10 | 4621 | uint16 |  |  | system_soc | [11 empty] | /components/bms_info | system_soc | Yes
System SOH | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120E | 10 | 4622 | uint16 |  |  | system_soh | [11 empty] | /components/bms_info | system_soh | Yes
System Insulation | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x120F |  | 4623 | uint16 |  |  | system_insulation | [11 empty] | /components/bms_info | system_insulation | Yes
System Enable Charge Energy | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1210 |  | 4624 | uint16 |  |  | system_enable_charge_energy | [11 empty] | /components/bms_info | system_enable_charge_energy | Yes
System Enable Discharge Energy | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1211 |  | 4625 | uint16 |  |  | system_enable_discharge_energy | [11 empty] | /components/bms_info | system_enable_discharge_energy | Yes
System Enable Max Charge Current | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1212 |  | 4626 | uint16 |  |  | system_max_charge_current | [11 empty] | /components/bms_info | system_max_charge_current | Yes
System Enable Max Discharge Current | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1213 |  | 4627 | int16 |  |  | system_max_discharge_current | [11 empty] | /components/bms_info | system_max_discharge_current | Yes
Rack Current Difference | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1214 | 10 | 4628 | int16 |  |  | rack_cell_current_difference | [11 empty] | /components/bms_info | rack_cell_current_difference | Yes |  | the current diff between enabled racks' Max and Min current
Rack Voltage Difference | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1215 | 10 | 4629 | uint16 |  |  | rack_cell_voltage_difference | [11 empty] | /components/bms_info | rack_cell_voltage_difference | Yes |  | the rack voltage diff between enabled racks' Max and Min voltage
System Max Vol Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1216 |  | 4630 | uint16 |  |  | system_max_volt_cell_rack_id | [11 empty] | /components/bms_info | system_max_volt_cell_rack_id | Yes
System Max Vol Cell Slave ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1217 |  | 4631 | uint16 |  |  | system_max_volt_cell_module_id | [11 empty] | /components/bms_info | system_max_volt_cell_module_id | Yes
System Max Vol Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1218 |  | 4632 | uint16 |  |  | system_max_volt_cell_id | [11 empty] | /components/bms_info | system_max_volt_cell_id | Yes
System Max Cell Voltage | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1219 | 1000 | 4633 | uint16 |  |  | system_max_cell_voltage | [11 empty] | /components/bms_info | system_max_cell_voltage | Yes |  | mV
System Min Vol Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121A |  | 4634 | uint16 |  |  | system_min_volt_cell_rack_id | [11 empty] | /components/bms_info | system_min_volt_cell_rack_id | Yes
System Min Vol Cell Slave ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121B |  | 4635 | uint16 |  |  | system_min_volt_cell_module_id | [11 empty] | /components/bms_info | system_min_volt_cell_module_id | Yes
System Min Vol Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121C |  | 4636 | uint16 |  |  | system_min_volt_cell_id | [11 empty] | /components/bms_info | system_min_volt_cell_id | Yes
System Min Cell Voltage | Control | 5.BMS_info | Holding Register | % |  | 100 |  | 0x121D | 1000 | 4637 | uint16 |  |  | system_min_cell_voltage | [11 empty] | /components/bms_info | system_min_cell_voltage | Yes |  | mV
System Average voltage | Control | 5.BMS_info | Holding Register | % |  | 100 |  | 0x121E | 1000 | 4638 | uint16 |  |  | system_avg_voltage | [11 empty] | /components/bms_info | system_avg_voltage | Yes |  | mV
System Max Temp Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x121F |  | 4639 | uint16 |  |  | system_max_temp_cell_rack_id | [11 empty] | /components/bms_info | system_max_temp_cell_rack_id | Yes
System Max Temp Cell Slave ID | Control | 5.BMS_info | Holding Register |  |  | 100 |  | 0x1220 |  | 4640 | uint16 |  |  | system_max_temp_cell_module_id | [11 empty] | /components/bms_info | system_max_temp_cell_module_id | Yes
System Max Temp Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1221 |  | 4641 | uint16 |  |  | system_max_temp_cell_id | [11 empty] | /components/bms_info | system_max_temp_cell_id | Yes
System Max Cell Temperature | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1222 | 10 | 4642 | int16 |  |  | system_max_cell_temperature | [11 empty] | /components/bms_info | system_max_cell_temperature | Yes |  | deg
System Min Temp Cell Rack ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1223 |  | 4643 | uint16 |  |  | system_min_temp_cell_rack_id | [11 empty] | /components/bms_info | system_min_temp_cell_rack_id | Yes
System Min Temp Cell Slave ID | Control | 5.BMS_info | Holding Register | V |  |  |  | 0x1224 |  | 4644 | uint16 |  |  | system_min_temp_cell_module_id | [11 empty] | /components/bms_info | system_min_temp_cell_module_id | Yes
System Min Temp Cell ID | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1225 |  | 4645 | uint16 |  |  | system_min_temp_cell_id | [11 empty] | /components/bms_info | system_min_temp_cell_id | Yes
System Min Cell Temperature | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1226 | 10 | 4646 | int16 |  |  | system_min_cell_temperature | [11 empty] | /components/bms_info | system_min_cell_temperature | Yes |  | deg
System Average Temperature | Control | 5.BMS_info | Holding Register | % |  | 10 |  | 0x1227 | 10 | 4647 | int16 |  |  | system_avg_temperature | [11 empty] | /components/bms_info | system_avg_temperature | Yes
BAU BCU Communication Fault Alarm 1 | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1228 |  | 4648 | uint16 |  |  | bau_bcu_comm_fault_alarm_1 | [11 empty] | /components/bms_info | bau_bcu_comm_fault_alarm_1 | Yes |  | bit0:BCU1 … bit15: bcu16
BAU BCU Communication Fault Alarm 2 | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x1229 |  | 4649 | uint16 |  |  | bau_bcu_comm_fault_alarm_2 | [11 empty] | /components/bms_info | bau_bcu_comm_fault_alarm_2 | Yes |  | bit0:BCU17 … bit15: bcu32
BAU output dry contact status | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x122A |  | 4650 | uint16 |  |  | bau_output_dry_contact_status | [7 empty] | 0：closed,1:opend Bit0: Dry contact1 state; Bit1: Dry contact2 statet; |  |  |  | /components/bms_info | bau_output_dry_contact_status | Yes
Rack enable / disable status 2 Rack Enable Status2 | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x122B |  | 4651 | uint16 |  |  | rack_enable_disable_status_1 | [11 empty] | /components/bms_info | rack_enable_disable_status_1 | Yes
Rack Request Step-in 2 | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x122C |  | 4652 | uint16 |  |  | rack_request_step_in_1 | [11 empty] | /components/bms_info | rack_request_step_in_1 | Yes
RACK request quit-in 2 Rack Request Quit-out 2 | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x122D |  | 4653 | uint16 |  |  | rack_request_quit_in_1 | [11 empty] | /components/bms_info | rack_request_quit_in_1 | Yes
RACK xxxx step-in quit-in status2 Status of Allow Quit-out /Step-in 2 | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x122E |  | 4654 | uint16 |  |  | rack_request_status_quit_in_1 | [11 empty] | /components/bms_info | rack_request_status_quit_in_1 | Yes
Accum Charge Energy MSB | Control | 5.BMS_info | Holding Register | % |  |  |  | 0x122F |  | 4655 | uint16 |  |  | accumulation_charge_energy_msb | [11 empty] | /components/bms_info | accumulation_charge_energy_msb | Yes
Accum Charge Energy LSB | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1230 |  | 4656 | uint16 |  |  | accumulation_charge_energy_lsb | [11 empty] | /components/bms_info | accumulation_charge_energy_lsb | Yes
Accum Discharge Energy MSB | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1231 |  | 4657 | uint16 |  |  | accumulation_discharge_energy_msb | [11 empty] | /components/bms_info | accumulation_discharge_energy_msb | Yes
Accum Discharge Energy LSB | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1232 |  | 4658 | uint16 |  |  | accumulation_discharge_energy_lsb | [11 empty] | /components/bms_info | accumulation_discharge_energy_lsb | Yes
Number of Racks in Service | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1233 |  | 4659 | uint16 |  |  | number_of_racks_inservice | [11 empty] | /components/bms_info | number_of_racks_inservice | Yes
Number ot Total Racks | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1234 |  | 4660 | uint16 |  |  | number_of_racks_total | [11 empty] | /components/bms_info | number_of_racks_total | Yes
Min Number of Parallel Racks | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1235 |  | 4661 | uint16 |  |  | min_number_of_parallel_racks | [11 empty] | /components/bms_info | min_number_of_parallel_racks | Yes
Max discharge power | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1236 |  | 4662 | uint16 |  |  | max_discharge_power | [11 empty] | /components/bms_info | max_discharge_power | Yes
Max charge power | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1237 |  | 4663 | uint16 |  |  | max_charge_power | [11 empty] | /components/bms_info | max_charge_power | Yes
BMS heart beat | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1238 |  | 4664 | uint16 |  |  | bms_heartbeat | [11 empty] | /components/bms_info | bms_heartbeat | Yes | 15 acc every second
Start Connection | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1300 |  | 4864 | uint16 |  |  | start_connection | [11 empty] | /components/bms_info | start_connection | Yes | 0.1 to 15 s , 0 to 150
Insulation sampling function switch | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1301 |  | 4865 | uint16 |  |  | Insulation_sampling_function_switch | [11 empty] | /components/bms_info | Insulation_sampling_function_switch | Yes
reset PCS control fail alarm | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1302 |  | 4866 | uint16 |  |  | reset_pcs_control fail_alarm | [11 empty] | /components/bms_info | reset_pcs_control fail_alarm | Yes
Minimum number of parallel racks | Control | 5.BMS_info | Holding Register |  |  |  |  | 0x1303 |  | 4867 | uint16 |  |  | minimum_number_of_parallel_racks | [11 empty] | /components/bms_info | minimum_number_of_parallel_racks | Yes
rack_run_state | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0000 |  | 0 | bit_field |  |  | rack_run_state | [11 empty] | /components/rack_run_state |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
normal | Status | 6.bms_rack | filler |  |  |  |  | 0x0000 |  | 0 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
no_charge | Status | 6.bms_rack | filler |  |  |  |  | 0x0000 |  | 0 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
no_discharge | Status | 6.bms_rack | filler |  |  |  |  | 0x0000 |  | 0 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
standby | Status | 6.bms_rack | filler |  |  |  |  | 0x0000 |  | 0 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
stop | Status | 6.bms_rack | filler |  |  |  |  | 0x0000 |  | 0 | bit | 4 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_precharge_phase | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0001 |  | 1 | bit_field |  |  | rack_precharge_phase | [11 empty] | /components/rack_precharge_phase |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
disconnected | Status | 6.bms_rack | filler |  |  |  |  | 0x0001 |  | 1 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
start_connection | Status | 6.bms_rack | filler |  |  |  |  | 0x0001 |  | 1 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
connecting | Status | 6.bms_rack | filler |  |  |  |  | 0x0001 |  | 1 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
connected | Status | 6.bms_rack | filler |  |  |  |  | 0x0001 |  | 1 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
connection_fail | Status | 6.bms_rack | filler |  |  |  |  | 0x0001 |  | 1 | bit | 4 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_connection_state | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0002 |  | 2 | bit_field |  |  | rack_connection_state | [11 empty] | /components/rack_connection_state |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
positive_contactor_state | Status | 6.bms_rack | filler |  |  |  |  | 0x0002 |  | 2 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
pre_contactor_state | Status | 6.bms_rack | filler |  |  |  |  | 0x0002 |  | 2 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
negative_contactor_state | Status | 6.bms_rack | filler |  |  |  |  | 0x0002 |  | 2 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
disconnector_state | Status | 6.bms_rack | filler |  |  |  |  | 0x0002 |  | 2 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_alarm_info | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0003 |  | 3 | bit_field |  |  | rack_alarm_info | [11 empty] | /components/rack_alarm_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
bmu_hardware_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
bcu_hardware_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
fuse_protector_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
contactor_adhesion_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
bmu_communication_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 4 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
bau_communication_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 5 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
current_sensor_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 6 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
imd_fault | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 7 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
disconnector_open_when_rack_enabled | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 8 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
reserved (9-15) | Status | 6.bms_rack | filler |  |  |  |  | 0x0003 |  | 3 | bit | 15 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_warning | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0004 |  | 4 | bit_field |  |  | rack_alarm_info | [11 empty] | /components/rack_warning |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_low_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_low_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_over_curr_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 4 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_under_curr_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 5 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_temp_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 6 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_temp_low_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 7 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_temp_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 8 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_temp_low_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 9 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
insulation_low_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 10 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
terminal_temp_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 11 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
hvb_temp_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 12 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_diff_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 13 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_temp_diff_high_warn | Status | 6.bms_rack | filler |  |  |  |  | 0x0004 |  | 4 | bit | 14 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_alarm | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0005 |  | 5 | bit_field |  |  | rack_alarm | [11 empty] | /components/rack_alarm |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_low_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_low_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_over_curr_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 4 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_under_curr_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 5 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_temp_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 6 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_temp_low_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 7 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_temp_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 8 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_temp_low_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 9 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
insulation_low_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 10 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
terminal_temp_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 11 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
hvb_temp_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 12 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_diff_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 13 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_temp_diff_high_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0005 |  | 5 | bit | 14 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_critical_alarm | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0006 |  | 6 | bit_field |  |  | rack_critical_alarm | [11 empty] | /components/rack_critical_alarm |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_low_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 2 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_low_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 3 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_over_curr_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 4 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_under_curr_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 5 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_temp_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 6 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
dsg_temp_low_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 7 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_temp_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 8 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
chg_temp_low_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 9 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
insulation_low_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 10 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
terminal_temp_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 11 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
hvb_temp_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 12 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_vol_diff_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 13 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
cell_temp_diff_high_critical_alarm | Status | 6.bms_rack | filler |  |  |  |  | 0x0006 |  | 6 | bit | 14 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
reason_of_rack_step_in_failure | Status | 6.bms_rack | Input Register |  |  |  |  | 0x0007 |  | 7 | bit_field |  |  | reason_of_rack_step_in_failure | [11 empty] | /components/reason_of_rack_step_in_failure |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol_diff_large | Status | 6.bms_rack | filler |  |  |  |  | 0x0007 |  | 7 | bit | 0 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
sms_confirmation_overtime | Status | 6.bms_rack | filler |  |  |  |  | 0x0007 |  | 7 | bit | 1 |  | filler | [11 empty] | /components/bms_running_info |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
precharge_total_vol | Status | 6.bms_rack | Input Register | 0.1V | 1 |  |  | 0x0009 |  | 9 | uint16 |  |  | precharge_total_vol | [11 empty] | /components/precharge_total_vol |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_vol | Status | 6.bms_rack | Input Register | 0.1V | 1 |  |  | 0x000A |  | 10 | uint16 |  |  | rack_vol | [11 empty] | /components/rack_vol |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_current | Status | 6.bms_rack | Input Register | 0.1A | 1 |  |  | 0x000B |  | 11 | int16 |  |  | rack_current | [11 empty] | /components/rack_current |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_charge_discharge_state | Status | 6.bms_rack | Input Register |  | 1 |  |  | 0x000C |  | 12 | uint16 |  |  | rack_charge_discharge_state | [11 empty] | /components/rack_charge_discharge_state |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_soc | Status | 6.bms_rack | Input Register | % | 1 |  |  | 0x000D |  | 13 | uint16 |  |  | rack_soc | [11 empty] | /components/rack_soc |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_soh | Status | 6.bms_rack | Input Register | % | 1 |  |  | 0x000E |  | 14 | uint16 |  |  | rack_soh | [11 empty] | /components/rack_soh |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_insulation_value | Status | 6.bms_rack | Input Register | KΩ | 1 |  |  | 0x000F |  | 15 | uint16 |  |  | rack_insulation_value | [11 empty] | /components/rack_insulation_value |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_positive_insulation_value | Status | 6.bms_rack | Input Register | KΩ | 1 |  |  | 0x0010 |  | 16 | uint16 |  |  | rack_positive_insulation_value | [11 empty] | /components/rack_positive_insulation_value |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_negative_insulation_value | Status | 6.bms_rack | Input Register | KΩ | 1 |  |  | 0x0011 |  | 17 | uint16 |  |  | rack_negative_insulation_value | [11 empty] | /components/rack_negative_insulation_value |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_max_charge_current | Status | 6.bms_rack | Input Register | 0.1A | 1 |  |  | 0x0012 |  | 18 | uint16 |  |  | rack_max_charge_current | [11 empty] | /components/rack_max_charge_current |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_max_discharge_current | Status | 6.bms_rack | Input Register | 0.1A | 1 |  |  | 0x0013 |  | 19 | uint16 |  |  | rack_max_discharge_current | [11 empty] | /components/rack_max_discharge_current |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_max_cell_vol_id | Status | 6.bms_rack | Input Register |  | 1 |  |  | 0x0014 |  | 20 | uint16 |  |  | rack_max_cell_vol_id | [11 empty] | /components/rack_max_cell_vol_id |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_max_cell_vol | Status | 6.bms_rack | Input Register | mv | 1 |  |  | 0x0015 |  | 21 | uint16 |  |  | rack_max_cell_vol | [11 empty] | /components/rack_max_cell_vol |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_min_cell_vol_id | Status | 6.bms_rack | Input Register |  | 1 |  |  | 0x0016 |  | 22 | uint16 |  |  | rack_min_cell_vol_id | [11 empty] | /components/rack_min_cell_vol_id |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_min_cell_vol | Status | 6.bms_rack | Input Register | mv | 1 |  |  | 0x0017 |  | 23 | uint16 |  |  | rack_min_cell_vol | [11 empty] | /components/rack_min_cell_vol |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_max_cell_temp_id | Status | 6.bms_rack | Input Register |  | 1 |  |  | 0x0018 |  | 24 | uint16 |  |  | rack_max_cell_temp_id | [11 empty] | /components/rack_max_cell_temp_id |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_max_cell_temp | Status | 6.bms_rack | Input Register | 0.1℃ | 1 |  |  | 0x0019 |  | 25 | int16 |  |  | rack_max_cell_temp | [11 empty] | /components/rack_max_cell_temp |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_min_cell_temp_id | Status | 6.bms_rack | Input Register |  | 1 |  |  | 0x001A |  | 26 | uint16 |  |  | rack_min_cell_temp_id | [11 empty] | /components/rack_min_cell_temp_id |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_min_cell_temp | Status | 6.bms_rack | Input Register | 0.1℃ | 1 |  |  | 0x001B |  | 27 | int16 |  |  | rack_min_cell_temp | [11 empty] | /components/rack_min_cell_temp |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_average_vol | Status | 6.bms_rack | Input Register | mw | 1 |  |  | 0x001C |  | 28 | uint16 |  |  | rack_average_vol | [11 empty] | /components/rack_average_vol |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
rack_average_temp | Status | 6.bms_rack | Input Register | 0.1℃ | 1 |  |  | 0x001D |  | 29 | int16 |  |  | rack_average_temp | [11 empty] | /components/rack_average_temp |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
6.bms_rack
rack_enable_disable | Control | 6.bms_rack | Holding Register |  | 1 |  |  | 0x0200 |  | 512 | uint16 |  |  | rack_enable_disable | [11 empty] | /components/rack_enable_disable |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
close_contactor | Control | 6.bms_rack | Holding Register |  | 1 |  |  | 0x0201 |  | 513 | uint16 |  |  | close_contactor | [11 empty] | /components/close_contactor |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
open_contactor | Control | 6.bms_rack | Holding Register |  | 1 |  |  | 0x0202 |  | 514 | uint16 |  |  | open_contactor | [11 empty] | /components/open_contactor |  | Yes |  | Bit0: Fault signal of FSS (0: Normal, 1: Abnormal) Bit1: Alarm signal of FSS (0: Normal, 1: Abnormal) Bit2: Lightning Protector status (0: Abnormal, 1: Normal) Bit3: Transformer high temperature alarm (0: Normal, 1: Abnormal) Bit4: Emergency stop (0: Reversion, 1: Trigger) Bit5: DC load switch status (0: Open, 1: Close) Bit6: Access control status (0: Close, 1: Open) Bit7: DC fuse status (1: Normal, 0: Abnormal)
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A13: Tony Olivo: Do not add rows below this line, the script will break
Note on A14: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B14: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D14: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E14: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F14: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G14: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H14: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J14: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on K14: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on L14: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on M14: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on N14: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on O14: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Y14: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on Z14: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AA14: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AB14: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AC14: Tony Olivo: Yes/No whether to include in the client/server config
Note on AD14: Tony Olivo: For humans
Note on AE14: Tony Olivo: For humans
Note on AF14: Tony Olivo: Ranges are for humans only