## HybridOS Server
Device Name | FlexGen HybridOS
Device Protocol | DNP3
Device Protocol Version | 0.2 |  |  | Notes:
Device ID String | northfork_dnp3_server
Device IP Address (if TCP) | 0.0.0.0
Device Port (502 typical) | 20000
local_uri | /local_server
frequency | 5000
debug | 0
Name | Source Device | Type | Version | Register Type | Address | Unit | Words | Scale | Variation | Data Type | Range Start | Range End | Engineering Range Start | Engineering Range End | Description | Control Narrative for Register | Reg ID | URI | ID | Include | Repeat | Bit | Column1
Site - Active Power Total Gross | HybridOS | Status | 0.2 | analog | 0 | kW |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Power produced as measured by BESS Inverter |  | ess_total_active_power | /assets/ess/summary | ess_total_active_power | Yes
Site - Reactive Power Total Gross | HybridOS | Status | 0.2 | analog | 1 | kVAR |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Reactive Power produced as measued by BESS Inverter |  | ess_total_reactive_power | /assets/ess/summary | ess_total_reactive_power | Yes
Site - Apparent Power Total Gross | HybridOS | Status | 0.2 | analog | 2 | kVA |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Apparent Power as measured by the BESS Inverter |  | ess_total_apparent_power | /assets/ess/summary | ess_total_apparent_power | Yes
Site - Active Power Total Net | SEL-735 | Status | 0.2 | analog | 3 | kW |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Aggregated Active Power exported after Aux loads |  | active_power | /components/sel_735 | active_power | Yes
Site - Reactive Power Total Net | SEL-735 | Status | 0.2 | analog | 4 | kVAR |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Aggregated Reactive Power exported after Aux loads |  | reactive_power | /components/sel_735 | reactive_power | Yes
Site - Apparent Power Total Net | SEL-735 | Status | 0.2 | analog | 5 | kVA |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Aggregated Apparent Power exported after Aux Loads |  | apparent_power | /components/sel_735 | apparent_power | Yes
Site - Frequency | SEL-735 | Status | 0.2 | analog | 6 | Hz |  |  | Group30Var5 | uint32 |  |  |  |  | Bus frequency |  | frequency | /components/sel_735 | frequency | Yes
Site - Voltage L1-L2 | SEL-651R | Status | 0.2 | analog | 7 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L1 |  | voltage_l1_l2 | /components/sel_735 | voltage_l1_l2 | Yes
Site - Voltage L2-L3 | SEL-651R | Status | 0.2 | analog | 8 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L2 |  | voltage_l2_l3 | /components/sel_735 | voltage_l2_l3 | Yes
Site - Voltage L3-L1 | SEL-651R | Status | 0.2 | analog | 9 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L3 |  | voltage_l3_l1 | /components/sel_735 | voltage_l3_l1 | Yes
Battery - State of Charge % | HybridOS | Status | 0.2 | analog | 10 | % |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | State of charge expressed as % of MWh capacity based on current health |  | ess_average_soc | /assets/ess/summary | ess_average_soc | Yes
Battery - Chargable energy kWh | HybridOS | Status | 0.2 | analog | 11 | kWh |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | State of charge expressed as kWh of charge below 100 |  | ess_chargeable_energy | /metrics/ess | ess_chargeable_energy | Yes
Battery - Dischargeable energy kWh | HybridOS | Status | 0.2 | analog | 12 | kWh |  |  | Group30Var5 | uint32 |  |  |  |  | State of charge expressed as kWh of discharge above 0 |  | ess_dischargeable_energy | /metrics/ess | ess_dischargeable_energy | Yes
Battery - Chargeable power | HybridOS | Status | 0.2 | analog | 13 | kW |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | kW available to Charge |  | ess_chargeable_power | /assets/ess/summary | ess_chargeable_power | Yes
Battery - Dischargeable power | HybridOS | Status | 0.2 | analog | 14 | kW |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | kW available to discharge |  | ess_dischargeable_power | /assets/ess/summary | ess_dischargeable_power | Yes
Battery - Number ESS Available | HybridOS | Status | 0.2 | analog | 15 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | BESS Units that are currently able to be connected to grid |  | num_ess_available | /assets/ess/summary | num_ess_available | Yes
Battery - Number ESS Online | HybridOS | Status | 0.2 | analog | 16 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | BESS Units that are currently connected to grid |  | num_ess_running | /assets/ess/summary | num_ess_running | Yes
Heartbeat Counter | HybridOS | Status | 0.2 | analog | 17 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Incrementing counter to indicate functional communications from Server |  | heartbeat_counter | /site/operation | heartbeat_counter | Yes
Site - kWh Delivered |  |  |  | analog | 18 |  |  |  | Group30Var5 | [7 empty] | kwh_delivered | /components/sel_735 | kwh_delivered | Yes
Site - kWh Received |  |  |  | analog | 19 |  |  |  | Group30Var5 | [7 empty] | kwh_received | /components/sel_735 | kwh_received | Yes
Fleet Manager Metrics Timestamp Response |  |  |  | analog | 20 |  |  |  | Group30Var5 | [7 empty] | FM_timestamp | /metrics/timestamp | FM_timestamp | Yes
Transformer Low Side Voltage |  |  |  | analog | 21 |  |  |  | Group30Var5 | [7 empty] | transformer_low_side_voltage | /metrics/transformer_low_side_voltage | transformer_low_side_voltage | Yes
Generation Gross Active Power |  |  |  | analog | 22 |  |  |  | Group30Var5 | [7 empty] | gen_gross_active_power | /metrics/gen_gross_active_power | gen_gross_active_power | Yes
Generation Gross Reactive Power |  |  |  | analog | 23 |  |  |  | Group30Var5 | [7 empty] | gen_gross_reactive_power | /metrics/gen_gross_reactive_power | gen_gross_reactive_power | Yes
Auxiliary Load Active Power |  |  |  | analog | 24 |  |  |  | Group30Var5 | [7 empty] | aux_load_active_power | /metrics/aux_load_active_power | aux_load_active_power | Yes
Auxiliary Load Reactive Power |  |  |  | analog | 25 |  |  |  | Group30Var5 | [7 empty] | aux_load_reactive_power | /metrics/aux_load_reactive_power | aux_load_reactive_power | Yes
GSU Transformer Flow Active Power |  |  |  | analog | 26 |  |  |  | Group30Var5 | [7 empty] | gsu_transformer_flow_active_power | /metrics/gsu_transformer_flow_active_power | gsu_transformer_flow_active_power | Yes
GSU Transformer Flow Reactive Power |  |  |  | analog | 27 |  |  |  | Group30Var5 | [7 empty] | gsu_transformer_flow_reactive_power | /metrics/gsu_transformer_flow_reactive_power | gsu_transformer_flow_reactive_power | Yes
Estimated PCS Auxiliary Power |  |  |  | analog | 28 |  |  |  | Group30Var5 | [7 empty] | pcs_aux_load_active_power | /metrics/aux_power | pcs_aux_load_active_power | Yes
Measured BMS Auxiliary Power |  |  |  | analog | 29 |  |  |  | Group30Var5 | [7 empty] | battery_load_active_power | /metrics/battery_load_active_power | battery_load_active_power | Yes
Frequency Response Enable Word | HybridOS | Status | 0.2 | analog | 30 |  |  |  | Group30Var5 | [7 empty] | fr_enable_mask | /metrics/active_power | fr_enable_mask | Yes
Baseload Power Command | HybridOS | Status | 0.2 | analog | 31 |  |  |  | Group30Var5 | [7 empty] | fr_baseload_cmd_kw | /metrics/active_power | fr_baseload_cmd_kw | Yes
FFR Inactive Power Command | HybridOS | Status | 0.2 | analog | 32 |  |  |  | Group30Var5 | [7 empty] | uf_ffr_inactive_cmd_kw | /metrics/active_power | uf_ffr_inactive_cmd_kw | Yes
FRRS UF Inactive Power Command | HybridOS | Status | 0.2 | analog | 33 |  |  |  | Group30Var5 | [7 empty] | uf_frrs_inactive_cmd_kw | /metrics/active_power | uf_frrs_inactive_cmd_kw | Yes
FRRS OF Inactive Power Command | HybridOS | Status | 0.2 | analog | 34 |  |  |  | Group30Var5 | [7 empty] | of_frrs_inactive_cmd_kw | /metrics/active_power | of_frrs_inactive_cmd_kw | Yes
FRRS Up Active Power Command | HybridOS | Status | 0.2 | analog | 35 |  |  |  | Group30Var5 | [7 empty] | uf_frrs_active_cmd_kw | /metrics/active_power | uf_frrs_active_cmd_kw | Yes
FRRS Down Active Power Command | HybridOS | Status | 0.2 | analog | 36 |  |  |  | Group30Var5 | [7 empty] | of_frrs_active_cmd_kw | /metrics/active_power | of_frrs_active_cmd_kw | Yes
FFR Active Power Command | HybridOS | Status | 0.2 | analog | 37 |  |  |  | Group30Var5 | [7 empty] | uf_ffr_active_cmd_kw | /metrics/active_power | uf_ffr_active_cmd_kw | Yes
Auto-PFR Up Active Power Command | HybridOS | Status | 0.2 | analog | 38 |  |  |  | Group30Var5 | [7 empty] | uf_pfr_active_cmd_kw | /metrics/active_power | uf_pfr_active_cmd_kw | Yes
Auto-PFR Down Active Power Command | HybridOS | Status | 0.2 | analog | 39 |  |  |  | Group30Var5 | [7 empty] | of_pfr_active_cmd_kw | /metrics/active_power | of_pfr_active_cmd_kw | Yes
Site Active Power Charge Limit | HybridOS | Status | 0.2 | analog | 40 |  |  |  | Group30Var5 | [7 empty] | total_site_kW_charge_limit | /features/active_power | total_site_kW_charge_limit | Yes
Site Active Power Discharge Limit | HybridOS | Status | 0.2 | analog | 41 |  |  |  | Group30Var5 | [7 empty] | total_site_kW_discharge_limit | /features/active_power | total_site_kW_discharge_limit | Yes
BESS Container #1 System Mode | HybridOS | Status | 0.2 | analog | 42 |  |  |  | Group30Var5 | uint32 | 0 | 4294967295 | 0 |  | BESS Container #1 System mode of operation |  | status | /assets/ess/ess_01 | status | Yes
BESS Container #1 System SOC | HybridOS | Status | 0.2 | analog | 43 | % |  |  | Group30Var5 | uint32 | 0 | 65535 | 0 |  | BESS Container #1 State of Charge |  | soc | /assets/ess/ess_01 | soc | Yes
BESS Container #1 Number of Active Racks | HybridOS | Status | 0.2 | analog | 44 | # |  |  | Group30Var5 | uint32 | 0 | 65535 | 0 |  | BESS Container #1 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_01 | bms_racks_in_service | Yes
BESS Container #2 System Mode | HybridOS | Status | 0.2 | analog | 45 |  |  |  | Group30Var5 | uint32 | 0 | -1227049253.5714 | 0 |  | BESS Container #2 System mode of operation |  | status | /assets/ess/ess_02 | status | Yes
BESS Container #2 System SOC | HybridOS | Status | 0.2 | analog | 46 | % |  |  | Group30Var5 | uint32 | 0 | -4908393619.2857 | 0 |  | BESS Container #2 State of Charge |  | soc | /assets/ess/ess_02 | soc | Yes
BESS Container #2 Number of Active Racks | HybridOS | Status | 0.2 | analog | 47 | # |  |  | Group30Var5 | uint32 | 0 | -6135508407.8572 | 0 |  | BESS Container #2 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_02 | bms_racks_in_service | Yes
BESS Container #3 System Mode | HybridOS | Status | 0.2 | analog | 48 |  |  |  | Group30Var5 | uint32 | 0 | -8589737985 | 0 |  | BESS Container #3 System mode of operation |  | status | /assets/ess/ess_03 | status | Yes
BESS Container #3 System SOC | HybridOS | Status | 0.2 | analog | 49 | % |  |  | Group30Var5 | uint32 | 0 | -12271082350.7143 | 0 |  | BESS Container #3 State of Charge |  | soc | /assets/ess/ess_03 | soc | Yes
BESS Container #3 Number of Active Racks | HybridOS | Status | 0.2 | analog | 50 | # |  |  | Group30Var5 | uint32 | 0 | -13498197139.2858 | 0 |  | BESS Container #3 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_03 | bms_racks_in_service | Yes
BESS Container #4 System Mode | HybridOS | Status | 0.2 | analog | 51 |  |  |  | Group30Var5 | uint32 | 0 | -14725311927.8572 | 0 |  | BESS Container #4 System mode of operation |  | status | /assets/ess/ess_04 | status | Yes
BESS Container #4 System SOC | HybridOS | Status | 0.2 | analog | 52 | % |  |  | Group30Var5 | uint32 | 0 | -18406656293.5716 | 0 |  | BESS Container #4 State of Charge |  | soc | /assets/ess/ess_04 | soc | Yes
BESS Container #4 Number of Active Racks | HybridOS | Status | 0.2 | analog | 53 | # |  |  | Group30Var5 | uint32 | 0 | -19633771082.143 | 0 |  | BESS Container #4 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_04 | bms_racks_in_service | Yes
BESS Container #5 System Mode | HybridOS | Status | 0.2 | analog | 54 |  |  |  | Group30Var5 | [5 empty] | BESS Container #5 System mode of operation |  | status | /assets/ess/ess_05 | status | Yes
BESS Container #5 System SOC | HybridOS | Status | 0.2 | analog | 55 | % |  |  | Group30Var5 | [5 empty] | BESS Container #5 State of Charge |  | soc | /assets/ess/ess_05 | soc | Yes
BESS Container #5 Number of Active Racks | HybridOS | Status | 0.2 | analog | 56 | # |  |  | Group30Var5 | [5 empty] | BESS Container #5 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_05 | bms_racks_in_service | Yes
BESS Container #6 System Mode | HybridOS | Status | 0.2 | analog | 57 |  |  |  | Group30Var5 | [5 empty] | BESS Container #6 System mode of operation |  | status | /assets/ess/ess_06 | status | Yes
BESS Container #6 System SOC | HybridOS | Status | 0.2 | analog | 58 | % |  |  | Group30Var5 | [5 empty] | BESS Container #6 State of Charge |  | soc | /assets/ess/ess_06 | soc | Yes
BESS Container #6 Number of Active Racks | HybridOS | Status | 0.2 | analog | 59 | # |  |  | Group30Var5 | [5 empty] | BESS Container #6 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_06 | bms_racks_in_service | Yes
BESS Container #7 System Mode | HybridOS | Status | 0.2 | analog | 60 |  |  |  | Group30Var5 | [5 empty] | BESS Container #7 System mode of operation |  | status | /assets/ess/ess_07 | status | Yes
BESS Container #7 System SOC | HybridOS | Status | 0.2 | analog | 61 | % |  |  | Group30Var5 | [5 empty] | BESS Container #7 State of Charge |  | soc | /assets/ess/ess_07 | soc | Yes
BESS Container #7 Number of Active Racks | HybridOS | Status | 0.2 | analog | 62 | # |  |  | Group30Var5 | [5 empty] | BESS Container #7 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_07 | bms_racks_in_service | Yes
BESS Container #8 System Mode | HybridOS | Status | 0.2 | analog | 63 |  |  |  | Group30Var5 | [5 empty] | BESS Container #8 System mode of operation |  | status | /assets/ess/ess_08 | status | Yes
BESS Container #8 System SOC | HybridOS | Status | 0.2 | analog | 64 | % |  |  | Group30Var5 | [5 empty] | BESS Container #8 State of Charge |  | soc | /assets/ess/ess_08 | soc | Yes
BESS Container #8 Number of Active Racks | HybridOS | Status | 0.2 | analog | 65 | # |  |  | Group30Var5 | [5 empty] | BESS Container #8 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_08 | bms_racks_in_service | Yes
BESS Container #9 System Mode | HybridOS | Status | 0.2 | analog | 66 |  |  |  | Group30Var5 | [5 empty] | BESS Container #9 System mode of operation |  | status | /assets/ess/ess_09 | status | Yes
BESS Container #9 System SOC | HybridOS | Status | 0.2 | analog | 67 | % |  |  | Group30Var5 | [5 empty] | BESS Container #9 State of Charge |  | soc | /assets/ess/ess_09 | soc | Yes
BESS Container #9 Number of Active Racks | HybridOS | Status | 0.2 | analog | 68 | # |  |  | Group30Var5 | [5 empty] | BESS Container #9 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_09 | bms_racks_in_service | Yes
BESS Container #10 System Mode | HybridOS | Status | 0.2 | analog | 69 |  |  |  | Group30Var5 | [5 empty] | BESS Container #10 System mode of operation |  | status | /assets/ess/ess_10 | status | Yes
BESS Container #10 System SOC | HybridOS | Status | 0.2 | analog | 70 | % |  |  | Group30Var5 | [5 empty] | BESS Container #10 State of Charge |  | soc | /assets/ess/ess_10 | soc | Yes
BESS Container #10 Number of Active Racks | HybridOS | Status | 0.2 | analog | 71 | # |  |  | Group30Var5 | [5 empty] | BESS Container #10 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_10 | bms_racks_in_service | Yes
BESS Container #11 System Mode | HybridOS | Status | 0.2 | analog | 72 |  |  |  | Group30Var5 | [5 empty] | BESS Container #11 System mode of operation |  | status | /assets/ess/ess_11 | status | Yes
BESS Container #11 System SOC | HybridOS | Status | 0.2 | analog | 73 | % |  |  | Group30Var5 | [5 empty] | BESS Container #11 State of Charge |  | soc | /assets/ess/ess_11 | soc | Yes
BESS Container #11 Number of Active Racks | HybridOS | Status | 0.2 | analog | 74 | # |  |  | Group30Var5 | [5 empty] | BESS Container #11 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_11 | bms_racks_in_service | Yes
BESS Container #12 System Mode | HybridOS | Status | 0.2 | analog | 75 |  |  |  | Group30Var5 | [5 empty] | BESS Container #12 System mode of operation |  | status | /assets/ess/ess_12 | status | Yes
BESS Container #12 System SOC | HybridOS | Status | 0.2 | analog | 76 | % |  |  | Group30Var5 | [5 empty] | BESS Container #12 State of Charge |  | soc | /assets/ess/ess_12 | soc | Yes
BESS Container #12 Number of Active Racks | HybridOS | Status | 0.2 | analog | 77 | # |  |  | Group30Var5 | [5 empty] | BESS Container #12 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_12 | bms_racks_in_service | Yes
BESS Container #13 System Mode | HybridOS | Status | 0.2 | analog | 78 |  |  |  | Group30Var5 | [5 empty] | BESS Container #13 System mode of operation |  | status | /assets/ess/ess_13 | status | Yes
BESS Container #13 System SOC | HybridOS | Status | 0.2 | analog | 79 | % |  |  | Group30Var5 | [5 empty] | BESS Container #13 State of Charge |  | soc | /assets/ess/ess_13 | soc | Yes
BESS Container #13 Number of Active Racks | HybridOS | Status | 0.2 | analog | 80 | # |  |  | Group30Var5 | [5 empty] | BESS Container #13 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_13 | bms_racks_in_service | Yes
BESS Container #14 System Mode | HybridOS | Status | 0.2 | analog | 81 |  |  |  | Group30Var5 | [5 empty] | BESS Container #14 System mode of operation |  | status | /assets/ess/ess_14 | status | Yes
BESS Container #14 System SOC | HybridOS | Status | 0.2 | analog | 82 | % |  |  | Group30Var5 | [5 empty] | BESS Container #14 State of Charge |  | soc | /assets/ess/ess_14 | soc | Yes
BESS Container #14 Number of Active Racks | HybridOS | Status | 0.2 | analog | 83 | # |  |  | Group30Var5 | [5 empty] | BESS Container #14 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_14 | bms_racks_in_service | Yes
BESS Container #15 System Mode | HybridOS | Status | 0.2 | analog | 84 |  |  |  | Group30Var5 | [5 empty] | BESS Container #15 System mode of operation |  | status | /assets/ess/ess_15 | status | Yes
BESS Container #15 System SOC | HybridOS | Status | 0.2 | analog | 85 | % |  |  | Group30Var5 | [5 empty] | BESS Container #15 State of Charge |  | soc | /assets/ess/ess_15 | soc | Yes
BESS Container #15 Number of Active Racks | HybridOS | Status | 0.2 | analog | 86 | # |  |  | Group30Var5 | [5 empty] | BESS Container #15 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_15 | bms_racks_in_service | Yes
BESS Container #16 System Mode | HybridOS | Status | 0.2 | analog | 87 |  |  |  | Group30Var5 | [5 empty] | BESS Container #16 System mode of operation |  | status | /assets/ess/ess_16 | status | Yes
BESS Container #16 System SOC | HybridOS | Status | 0.2 | analog | 88 | % |  |  | Group30Var5 | [5 empty] | BESS Container #16 State of Charge |  | soc | /assets/ess/ess_16 | soc | Yes
BESS Container #16 Number of Active Racks | HybridOS | Status | 0.2 | analog | 89 | # |  |  | Group30Var5 | [5 empty] | BESS Container #16 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_16 | bms_racks_in_service | Yes
BESS Container #17 System Mode | HybridOS | Status | 0.2 | analog | 90 |  |  |  | Group30Var5 | [5 empty] | BESS Container #17 System mode of operation |  | status | /assets/ess/ess_17 | status | Yes
BESS Container #17 System SOC | HybridOS | Status | 0.2 | analog | 91 | % |  |  | Group30Var5 | [5 empty] | BESS Container #17 State of Charge |  | soc | /assets/ess/ess_17 | soc | Yes
BESS Container #17 Number of Active Racks | HybridOS | Status | 0.2 | analog | 92 | # |  |  | Group30Var5 | [5 empty] | BESS Container #17 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_17 | bms_racks_in_service | Yes
BESS Container #18 System Mode | HybridOS | Status | 0.2 | analog | 93 |  |  |  | Group30Var5 | [5 empty] | BESS Container #18 System mode of operation |  | status | /assets/ess/ess_18 | status | Yes
BESS Container #18 System SOC | HybridOS | Status | 0.2 | analog | 94 | % |  |  | Group30Var5 | [5 empty] | BESS Container #18 State of Charge |  | soc | /assets/ess/ess_18 | soc | Yes
BESS Container #18 Number of Active Racks | HybridOS | Status | 0.2 | analog | 95 | # |  |  | Group30Var5 | [5 empty] | BESS Container #18 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_18 | bms_racks_in_service | Yes
BESS Container #19 System Mode | HybridOS | Status | 0.2 | analog | 96 |  |  |  | Group30Var5 | [5 empty] | BESS Container #19 System mode of operation |  | status | /assets/ess/ess_19 | status | Yes
BESS Container #19 System SOC | HybridOS | Status | 0.2 | analog | 97 | % |  |  | Group30Var5 | [5 empty] | BESS Container #19 State of Charge |  | soc | /assets/ess/ess_19 | soc | Yes
BESS Container #19 Number of Active Racks | HybridOS | Status | 0.2 | analog | 98 | # |  |  | Group30Var5 | [5 empty] | BESS Container #19 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_19 | bms_racks_in_service | Yes
BESS Container #20 System Mode | HybridOS | Status | 0.2 | analog | 99 |  |  |  | Group30Var5 | [5 empty] | BESS Container #20 System mode of operation |  | status | /assets/ess/ess_20 | status | Yes
BESS Container #20 System SOC | HybridOS | Status | 0.2 | analog | 100 | % |  |  | Group30Var5 | [5 empty] | BESS Container #20 State of Charge |  | soc | /assets/ess/ess_20 | soc | Yes
BESS Container #20 Number of Active Racks | HybridOS | Status | 0.2 | analog | 101 | # |  |  | Group30Var5 | [5 empty] | BESS Container #20 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_20 | bms_racks_in_service | Yes
BESS Container #21 System Mode | HybridOS | Status | 0.2 | analog | 102 |  |  |  | Group30Var5 | [5 empty] | BESS Container #21 System mode of operation |  | status | /assets/ess/ess_21 | status | Yes
BESS Container #21 System SOC | HybridOS | Status | 0.2 | analog | 103 | % |  |  | Group30Var5 | [5 empty] | BESS Container #21 State of Charge |  | soc | /assets/ess/ess_21 | soc | Yes
BESS Container #21 Number of Active Racks | HybridOS | Status | 0.2 | analog | 104 | # |  |  | Group30Var5 | [5 empty] | BESS Container #21 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_21 | bms_racks_in_service | Yes
BESS Container #22 System Mode | HybridOS | Status | 0.2 | analog | 105 |  |  |  | Group30Var5 | [5 empty] | BESS Container #22 System mode of operation |  | status | /assets/ess/ess_22 | status | Yes
BESS Container #22 System SOC | HybridOS | Status | 0.2 | analog | 106 | % |  |  | Group30Var5 | [5 empty] | BESS Container #22 State of Charge |  | soc | /assets/ess/ess_22 | soc | Yes
BESS Container #22 Number of Active Racks | HybridOS | Status | 0.2 | analog | 107 | # |  |  | Group30Var5 | [5 empty] | BESS Container #22 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_22 | bms_racks_in_service | Yes
BESS Container #23 System Mode | HybridOS | Status | 0.2 | analog | 108 |  |  |  | Group30Var5 | [5 empty] | BESS Container #23 System mode of operation |  | status | /assets/ess/ess_23 | status | Yes
BESS Container #23 System SOC | HybridOS | Status | 0.2 | analog | 109 | % |  |  | Group30Var5 | [5 empty] | BESS Container #23 State of Charge |  | soc | /assets/ess/ess_23 | soc | Yes
BESS Container #23 Number of Active Racks | HybridOS | Status | 0.2 | analog | 110 | # |  |  | Group30Var5 | [5 empty] | BESS Container #23 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_23 | bms_racks_in_service | Yes
BESS Container #24 System Mode | HybridOS | Status | 0.2 | analog | 111 |  |  |  | Group30Var5 | [5 empty] | BESS Container #24 System mode of operation |  | status | /assets/ess/ess_24 | status | Yes
BESS Container #24 System SOC | HybridOS | Status | 0.2 | analog | 112 | % |  |  | Group30Var5 | [5 empty] | BESS Container #24 State of Charge |  | soc | /assets/ess/ess_24 | soc | Yes
BESS Container #24 Number of Active Racks | HybridOS | Status | 0.2 | analog | 113 | # |  |  | Group30Var5 | [5 empty] | BESS Container #24 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_24 | bms_racks_in_service | Yes
BESS Container #25 System Mode | HybridOS | Status | 0.2 | analog | 114 |  |  |  | Group30Var5 | [5 empty] | BESS Container #25 System mode of operation |  | status | /assets/ess/ess_25 | status | Yes
BESS Container #25 System SOC | HybridOS | Status | 0.2 | analog | 115 | % |  |  | Group30Var5 | [5 empty] | BESS Container #25 State of Charge |  | soc | /assets/ess/ess_25 | soc | Yes
BESS Container #25 Number of Active Racks | HybridOS | Status | 0.2 | analog | 116 | # |  |  | Group30Var5 | [5 empty] | BESS Container #25 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_25 | bms_racks_in_service | Yes
BESS Container #26 System Mode | HybridOS | Status | 0.2 | analog | 117 |  |  |  | Group30Var5 | [5 empty] | BESS Container #26 System mode of operation |  | status | /assets/ess/ess_26 | status | Yes
BESS Container #26 System SOC | HybridOS | Status | 0.2 | analog | 118 | % |  |  | Group30Var5 | [5 empty] | BESS Container #26 State of Charge |  | soc | /assets/ess/ess_26 | soc | Yes
BESS Container #26 Number of Active Racks | HybridOS | Status | 0.2 | analog | 119 | # |  |  | Group30Var5 | [5 empty] | BESS Container #26 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_26 | bms_racks_in_service | Yes
BESS Container #27 System Mode | HybridOS | Status | 0.2 | analog | 120 |  |  |  | Group30Var5 | [5 empty] | BESS Container #27 System mode of operation |  | status | /assets/ess/ess_27 | status | Yes
BESS Container #27 System SOC | HybridOS | Status | 0.2 | analog | 121 | % |  |  | Group30Var5 | [5 empty] | BESS Container #27 State of Charge |  | soc | /assets/ess/ess_27 | soc | Yes
BESS Container #27 Number of Active Racks | HybridOS | Status | 0.2 | analog | 122 | # |  |  | Group30Var5 | [5 empty] | BESS Container #27 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_27 | bms_racks_in_service | Yes
BESS Container #28 System Mode | HybridOS | Status | 0.2 | analog | 123 |  |  |  | Group30Var5 | [5 empty] | BESS Container #28 System mode of operation |  | status | /assets/ess/ess_28 | status | Yes
BESS Container #28 System SOC | HybridOS | Status | 0.2 | analog | 124 | % |  |  | Group30Var5 | [5 empty] | BESS Container #28 State of Charge |  | soc | /assets/ess/ess_28 | soc | Yes
BESS Container #28 Number of Active Racks | HybridOS | Status | 0.2 | analog | 125 | # |  |  | Group30Var5 | [5 empty] | BESS Container #28 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_28 | bms_racks_in_service | Yes
BESS Container #29 System Mode | HybridOS | Status | 0.2 | analog | 126 |  |  |  | Group30Var5 | [5 empty] | BESS Container #29 System mode of operation |  | status | /assets/ess/ess_29 | status | Yes
BESS Container #29 System SOC | HybridOS | Status | 0.2 | analog | 127 | % |  |  | Group30Var5 | [5 empty] | BESS Container #29 State of Charge |  | soc | /assets/ess/ess_29 | soc | Yes
BESS Container #29 Number of Active Racks | HybridOS | Status | 0.2 | analog | 128 | # |  |  | Group30Var5 | [5 empty] | BESS Container #29 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_29 | bms_racks_in_service | Yes
BESS Container #30 System Mode | HybridOS | Status | 0.2 | analog | 129 |  |  |  | Group30Var5 | [5 empty] | BESS Container #30 System mode of operation |  | status | /assets/ess/ess_30 | status | Yes
BESS Container #30 System SOC | HybridOS | Status | 0.2 | analog | 130 | % |  |  | Group30Var5 | [5 empty] | BESS Container #30 State of Charge |  | soc | /assets/ess/ess_30 | soc | Yes
BESS Container #30 Number of Active Racks | HybridOS | Status | 0.2 | analog | 131 | # |  |  | Group30Var5 | [5 empty] | BESS Container #30 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_30 | bms_racks_in_service | Yes
BESS Container #31 System Mode | HybridOS | Status | 0.2 | analog | 132 |  |  |  | Group30Var5 | [5 empty] | BESS Container #31 System mode of operation |  | status | /assets/ess/ess_31 | status | Yes
BESS Container #31 System SOC | HybridOS | Status | 0.2 | analog | 133 | % |  |  | Group30Var5 | [5 empty] | BESS Container #31 State of Charge |  | soc | /assets/ess/ess_31 | soc | Yes
BESS Container #31 Number of Active Racks | HybridOS | Status | 0.2 | analog | 134 | # |  |  | Group30Var5 | [5 empty] | BESS Container #31 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_31 | bms_racks_in_service | Yes
BESS Container #32 System Mode | HybridOS | Status | 0.2 | analog | 135 |  |  |  | Group30Var5 | [5 empty] | BESS Container #32 System mode of operation |  | status | /assets/ess/ess_32 | status | Yes
BESS Container #32 System SOC | HybridOS | Status | 0.2 | analog | 136 | % |  |  | Group30Var5 | [5 empty] | BESS Container #32 State of Charge |  | soc | /assets/ess/ess_32 | soc | Yes
BESS Container #32 Number of Active Racks | HybridOS | Status | 0.2 | analog | 137 | # |  |  | Group30Var5 | [5 empty] | BESS Container #32 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_32 | bms_racks_in_service | Yes
BESS Container #33 System Mode | HybridOS | Status | 0.2 | analog | 138 |  |  |  | Group30Var5 | [5 empty] | BESS Container #33 System mode of operation |  | status | /assets/ess/ess_33 | status | Yes
BESS Container #33 System SOC | HybridOS | Status | 0.2 | analog | 139 | % |  |  | Group30Var5 | [5 empty] | BESS Container #33 State of Charge |  | soc | /assets/ess/ess_33 | soc | Yes
BESS Container #33 Number of Active Racks | HybridOS | Status | 0.2 | analog | 140 |  |  |  | Group30Var5 | [5 empty] | BESS Container #33 Number of Active Racks |  | bms_racks_in_service | /assets/ess/ess_33 | bms_racks_in_service | Yes
Watchdog Pet | HybridOS | Command | 0.2 | AnOPF32 | 0 |  |  |  |  | uint32 |  |  |  |  | Client will write this register with unique integer periodically |  | watchdog_pet | /features/site_operation | watchdog_pet | Yes
Frequency Response Enable Word | HybridOS | Command | 0.2 | AnOPF32 | 1 | [11 empty] | fr_enable_mask_dnp3 | /features/active_power | fr_enable_mask_dnp3 | Yes
Baseload Power Command | HybridOS | Command | 0.2 | AnOPF32 | 2 | kW | [10 empty] | fr_baseload_cmd_kw_dnp3 | /features/active_power | fr_baseload_cmd_kw_dnp3 | Yes
FFR Inactive Power Command | HybridOS | Command | 0.2 | AnOPF32 | 3 | kW | [10 empty] | uf_ffr_inactive_cmd_kw_dnp3 | /features/active_power | uf_ffr_inactive_cmd_kw_dnp3 | Yes
UF FRRS Inactive Power Command | HybridOS | Command | 0.2 | AnOPF32 | 4 | kW | [10 empty] | uf_frrs_inactive_cmd_kw_dnp3 | /features/active_power | uf_frrs_inactive_cmd_kw_dnp3 | Yes
FRRS Inactive Power Command | HybridOS | Command | 0.2 | AnOPF32 | 5 | kW | [10 empty] | of_frrs_inactive_cmd_kw_dnp3 | /features/active_power | of_frrs_inactive_cmd_kw_dnp3 | Yes
UF FRRS Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 6 | kW | [10 empty] | uf_frrs_active_cmd_kw_dnp3 | /features/active_power | uf_frrs_active_cmd_kw_dnp3 | Yes
OF FRRS Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 7 | kW | [10 empty] | of_frrs_active_cmd_kw_dnp3 | /features/active_power | of_frrs_active_cmd_kw_dnp3 | Yes
FFR Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 8 | kW | [10 empty] | uf_ffr_active_cmd_kw_dnp3 | /features/active_power | uf_ffr_active_cmd_kw_dnp3 | Yes
UF PFR Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 9 | kW | [10 empty] | uf_pfr_active_cmd_kw_dnp3 | /features/active_power | uf_pfr_active_cmd_kw_dnp3 | Yes
OF PFR Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 10 | kW | [10 empty] | of_pfr_active_cmd_kw_dnp3 | /features/active_power | of_pfr_active_cmd_kw_dnp3 | Yes
Fleet Manager Metrics Timestamp | HybridOS | Command | 0.2 | AnOPF32 | 11 | [11 empty] | FM_timestamp | /metrics/timestamp | FM_timestamp | Yes
Active Voltage Regulation Command | HybridOS | Command | 0.2 | AnOPF32 | 12 | V | [10 empty] | active_voltage_cmd_local | /features/reactive_power | active_voltage_cmd_local | Yes
Reactive Power Setpoint | HybridOS | Command | 0.2 | AnOPF32 | 13 | kVAR | [10 empty] | reactive_setpoint_kVAR_cmd_local | /features/reactive_power | reactive_setpoint_kVAR_cmd_local | Yes
Reactive Power Mode Select Command | HybridOS | Command | 0.2 | AnOPF32 | 14 | [11 empty] | runmode1_kVAR_mode_cmd | /features/reactive_power | runmode1_kVAR_mode_cmd
Main Breaker Closed | SEL-651 | Status | 0.2 | binary | 0 |  |  |  |  | uint32 | 0 | 65535 | 5 |  | Main Breaker Closed | Bit 5 = MAIN BREAKER OPEN STATUS ¦ 1 = breaker closed, 0 = breaker open | breaker_status | /components/sel_411l_pri | breaker_status | Yes
Running Status | HybridOS | Status | 0.2 | binary | 1 |  |  |  |  | bool | 0 | 65535 |  |  | BESS Plant running status, feeder closed, at least one ESS or PV on | 0 = Not running, 1 = Running | running_status_flag | /site/operation | running_status_flag | Yes
Alarm Status | HybridOS | Status | 0.2 | binary | 2 |  |  |  |  | bool | 0 | 65535 |  |  | If any alarm is present, performance may be degraded and site requires attention | 0 = No alarms present, 1 = Alarms present | alarm_status_flag | /site/operation | alarm_status_flag | Yes
Fault Status | HybridOS | Status | 0.2 | binary | 3 |  |  |  |  | bool | 0 | 65535 |  |  | If any fault is present that prevents BESS plant from running on grid. | 0 = No faults present, 1 = Faults present | fault_status_flag | /site/operation | fault_status_flag | Yes
FFR UF Response Status | HybridOS | Status | 0.2 | binary | 4 | [11 empty] | uf_ffr_active_response_status | /features/active_power | uf_ffr_active_response_status | Yes
FFR UF Cooldown Status | HybridOS | Status | 0.2 | binary | 5 | [11 empty] | uf_ffr_in_cooldown | /features/active_power | uf_ffr_in_cooldown | Yes
PFR UF Response Status | HybridOS | Status | 0.2 | binary | 6 | [11 empty] | uf_pfr_active_response_status | /features/active_power | uf_pfr_active_response_status | Yes
PFR UF Cooldown Status | HybridOS | Status | 0.2 | binary | 7 | [11 empty] | uf_pfr_in_cooldown | /features/active_power | uf_pfr_in_cooldown | Yes
PFR OF Response Status | HybridOS | Status | 0.2 | binary | 8 | [11 empty] | of_pfr_active_response_status | /features/active_power | of_pfr_active_response_status | Yes
PFR OF Cooldown Status | HybridOS | Status | 0.2 | binary | 9 | [11 empty] | of_pfr_in_cooldown | /features/active_power | of_pfr_in_cooldown | Yes
FRRS UF Response Status | HybridOS | Status | 0.2 | binary | 10 | [11 empty] | uf_frrs_active_response_status | /features/active_power | uf_frrs_active_response_status | Yes
FRRS UF Cooldown Status | HybridOS | Status | 0.2 | binary | 11 | [11 empty] | uf_frrs_in_cooldown | /features/active_power | uf_frrs_in_cooldown | Yes
FRRS OF Response Status | HybridOS | Status | 0.2 | binary | 12 | [11 empty] | of_frrs_active_response_status | /features/active_power | of_frrs_active_response_status | Yes
FRRS OF Cooldown Status | HybridOS | Status | 0.2 | binary | 13 | [11 empty] | of_frrs_in_cooldown | /features/active_power | of_frrs_in_cooldown | Yes
Virtual MV Breaker Status (SEL-351s) | HybridOS | Status | 0.2 | binary | 14 | [11 empty] | virtual_switch_status | /metrics/breaker_status | virtual_switch_status | Yes
Generation AVR Status | HybridOS | Status | 0.2 | binary | 15 | [11 empty] | avr_status | /metrics/avr_status | avr_status | Yes
Generation Reactive Setpoint Status | HybridOS | Status | 0.2 | binary | 16 | [11 empty] | reactive_setpoint_status | /metrics/reactive_setpoint_status | reactive_setpoint_status | Yes
BESS Container #1 Fault Flag | HybridOS | Status | 0.2 | binary | 17 |  |  |  |  | bool |  |  |  |  | BESS Container #1 Fault Flag |  | faults | /assets/ess/ess_01 | faults | Yes |  |  |  | 1 | /assets/ess/ess_0
BESS Container #1 Alarm Flag | HybridOS | Status | 0.2 | binary | 18 |  |  |  |  | bool | 0 | 4294967295 | 0 | 100 | BESS Container #1 Alarm Flag |  | alarms | /assets/ess/ess_01 | alarms | Yes |  |  |  | 1
BESS Container #2 Fault Flag | HybridOS | Status | 0.2 | binary | 19 |  |  |  |  | bool |  | -2454164042.1428 |  | 102.2857 | BESS Container #2 Fault Flag |  | faults | /assets/ess/ess_02 | faults | Yes |  |  |  | 2
BESS Container #2 Alarm Flag | HybridOS | Status | 0.2 | binary | 20 |  |  |  |  | bool | 0 | -3681278830.7143 | 0 | 113.0286 | BESS Container #2 Alarm Flag |  | alarms | /assets/ess/ess_02 | alarms | Yes |  |  |  | 2
BESS Container #3 Fault Flag | HybridOS | Status | 0.2 | binary | 21 |  |  |  |  | bool |  | -9816852773.5715 |  | 166.7429 | BESS Container #3 Fault Flag |  | faults | /assets/ess/ess_03 | faults | Yes |  |  |  | 3
BESS Container #3 Alarm Flag | HybridOS | Status | 0.2 | binary | 22 |  |  |  |  | bool | 0 | -11043967562.1429 | 0 | 177.4857 | BESS Container #3 Alarm Flag |  | alarms | /assets/ess/ess_03 | alarms | Yes |  |  |  | 3
BESS Container #4 Fault Flag | HybridOS | Status | 0.2 | binary | 23 |  |  |  |  | bool |  | -15952426716.4287 |  | 220.4571 | BESS Container #4 Fault Flag |  | faults | /assets/ess/ess_04 | faults | Yes |  |  |  | 4
BESS Container #4 Alarm Flag | HybridOS | Status | 0.2 | binary | 24 |  |  |  |  | bool | 0 | -17179541505.0001 | 0 | 231.2 | BESS Container #4 Alarm Flag |  | alarms | /assets/ess/ess_04 | alarms | Yes |  |  |  | 4 | BESS Container # | Alarm Flag | Fault Flag
BESS Container #5 Fault Flag | HybridOS | Status | 0.2 | binary | 25 | [9 empty] | BESS Container #5 Fault Flag |  | faults | /assets/ess/ess_05 | faults | Yes |  |  |  | 5 |  |  | Alarm Flag
BESS Container #5 Alarm Flag | HybridOS | Status | 0.2 | binary | 26 | [9 empty] | BESS Container #5 Alarm Flag |  | alarms | /assets/ess/ess_05 | alarms | Yes |  |  |  | 5 |  |  | Fault Flag
BESS Container #6 Fault Flag | HybridOS | Status | 0.2 | binary | 27 | [9 empty] | BESS Container #6 Fault Flag |  | faults | /assets/ess/ess_06 | faults | Yes |  |  |  | 6 |  |  | Alarm Flag
BESS Container #6 Alarm Flag | HybridOS | Status | 0.2 | binary | 28 | [9 empty] | BESS Container #6 Alarm Flag |  | alarms | /assets/ess/ess_06 | alarms | Yes |  |  |  | 6 |  |  | Fault Flag
BESS Container #7 Fault Flag | HybridOS | Status | 0.2 | binary | 29 | [9 empty] | BESS Container #7 Fault Flag |  | faults | /assets/ess/ess_07 | faults | Yes |  |  |  | 7 |  |  | Alarm Flag
BESS Container #7 Alarm Flag | HybridOS | Status | 0.2 | binary | 30 | [9 empty] | BESS Container #7 Alarm Flag |  | alarms | /assets/ess/ess_07 | alarms | Yes |  |  |  | 7 |  |  | Fault Flag
BESS Container #8 Fault Flag | HybridOS | Status | 0.2 | binary | 31 | [9 empty] | BESS Container #8 Fault Flag |  | faults | /assets/ess/ess_08 | faults | Yes |  |  |  | 8 |  |  | Alarm Flag
BESS Container #8 Alarm Flag | HybridOS | Status | 0.2 | binary | 32 | [9 empty] | BESS Container #8 Alarm Flag |  | alarms | /assets/ess/ess_08 | alarms | Yes |  |  |  | 8 |  |  | Fault Flag
BESS Container #9 Fault Flag | HybridOS | Status | 0.2 | binary | 33 | [9 empty] | BESS Container #9 Fault Flag |  | faults | /assets/ess/ess_09 | faults | Yes |  |  |  | 9 |  |  | Alarm Flag
BESS Container #9 Alarm Flag | HybridOS | Status | 0.2 | binary | 34 | [9 empty] | BESS Container #9 Alarm Flag |  | alarms | /assets/ess/ess_09 | alarms | Yes |  |  |  | 9 |  |  | Fault Flag
BESS Container #10 Fault Flag | HybridOS | Status | 0.2 | binary | 35 | [9 empty] | BESS Container #10 Fault Flag |  | faults | /assets/ess/ess_10 | faults | Yes |  |  |  | 10 | /assets/ess/ess_ |  | Alarm Flag
BESS Container #10 Alarm Flag | HybridOS | Status | 0.2 | binary | 36 | [9 empty] | BESS Container #10 Alarm Flag |  | alarms | /assets/ess/ess_10 | alarms | Yes |  |  |  | 10 |  |  | Fault Flag
BESS Container #11 Fault Flag | HybridOS | Status | 0.2 | binary | 37 | [9 empty] | BESS Container #11 Fault Flag |  | faults | /assets/ess/ess_11 | faults | Yes |  |  |  | 11 |  |  | Alarm Flag
BESS Container #11 Alarm Flag | HybridOS | Status | 0.2 | binary | 38 | [9 empty] | BESS Container #11 Alarm Flag |  | alarms | /assets/ess/ess_11 | alarms | Yes |  |  |  | 11 |  |  | Fault Flag
BESS Container #12 Fault Flag | HybridOS | Status | 0.2 | binary | 39 | [9 empty] | BESS Container #12 Fault Flag |  | faults | /assets/ess/ess_12 | faults | Yes |  |  |  | 12 |  |  | Alarm Flag
BESS Container #12 Alarm Flag | HybridOS | Status | 0.2 | binary | 40 | [9 empty] | BESS Container #12 Alarm Flag |  | alarms | /assets/ess/ess_12 | alarms | Yes |  |  |  | 12 |  |  | Fault Flag
BESS Container #13 Fault Flag | HybridOS | Status | 0.2 | binary | 41 | [9 empty] | BESS Container #13 Fault Flag |  | faults | /assets/ess/ess_13 | faults | Yes |  |  |  | 13 |  |  | Alarm Flag
BESS Container #13 Alarm Flag | HybridOS | Status | 0.2 | binary | 42 | [9 empty] | BESS Container #13 Alarm Flag |  | alarms | /assets/ess/ess_13 | alarms | Yes |  |  |  | 13 |  |  | Fault Flag
BESS Container #14 Fault Flag | HybridOS | Status | 0.2 | binary | 43 | [9 empty] | BESS Container #14 Fault Flag |  | faults | /assets/ess/ess_14 | faults | Yes |  |  |  | 14 |  |  | Alarm Flag
BESS Container #14 Alarm Flag | HybridOS | Status | 0.2 | binary | 44 | [9 empty] | BESS Container #14 Alarm Flag |  | alarms | /assets/ess/ess_14 | alarms | Yes |  |  |  | 14 |  |  | Fault Flag
BESS Container #15 Fault Flag | HybridOS | Status | 0.2 | binary | 45 | [9 empty] | BESS Container #15 Fault Flag |  | faults | /assets/ess/ess_15 | faults | Yes |  |  |  | 15 |  |  | Alarm Flag
BESS Container #15 Alarm Flag | HybridOS | Status | 0.2 | binary | 46 | [9 empty] | BESS Container #15 Alarm Flag |  | alarms | /assets/ess/ess_15 | alarms | Yes |  |  |  | 15 |  |  | Fault Flag
BESS Container #16 Fault Flag | HybridOS | Status | 0.2 | binary | 47 | [9 empty] | BESS Container #16 Fault Flag |  | faults | /assets/ess/ess_16 | faults | Yes |  |  |  | 16 |  |  | Alarm Flag
BESS Container #16 Alarm Flag | HybridOS | Status | 0.2 | binary | 48 | [9 empty] | BESS Container #16 Alarm Flag |  | alarms | /assets/ess/ess_16 | alarms | Yes |  |  |  | 16 |  |  | Fault Flag
BESS Container #17 Fault Flag | HybridOS | Status | 0.2 | binary | 49 | [9 empty] | BESS Container #17 Fault Flag |  | faults | /assets/ess/ess_17 | faults | Yes |  |  |  | 17 |  |  | Alarm Flag
BESS Container #17 Alarm Flag | HybridOS | Status | 0.2 | binary | 50 | [9 empty] | BESS Container #17 Alarm Flag |  | alarms | /assets/ess/ess_17 | alarms | Yes |  |  |  | 17 |  |  | Fault Flag
BESS Container #18 Fault Flag | HybridOS | Status | 0.2 | binary | 51 | [9 empty] | BESS Container #18 Fault Flag |  | faults | /assets/ess/ess_18 | faults | Yes |  |  |  | 18 |  |  | Alarm Flag
BESS Container #18 Alarm Flag | HybridOS | Status | 0.2 | binary | 52 | [9 empty] | BESS Container #18 Alarm Flag |  | alarms | /assets/ess/ess_18 | alarms | Yes |  |  |  | 18 |  |  | Fault Flag
BESS Container #19 Fault Flag | HybridOS | Status | 0.2 | binary | 53 | [9 empty] | BESS Container #19 Fault Flag |  | faults | /assets/ess/ess_19 | faults | Yes |  |  |  | 19 |  |  | Alarm Flag
BESS Container #19 Alarm Flag | HybridOS | Status | 0.2 | binary | 54 | [9 empty] | BESS Container #19 Alarm Flag |  | alarms | /assets/ess/ess_19 | alarms | Yes |  |  |  | 19 |  |  | Fault Flag
BESS Container #20 Fault Flag | HybridOS | Status | 0.2 | binary | 55 | [9 empty] | BESS Container #20 Fault Flag |  | faults | /assets/ess/ess_20 | faults | Yes |  |  |  | 20 |  |  | Alarm Flag
BESS Container #20 Alarm Flag | HybridOS | Status | 0.2 | binary | 56 | [9 empty] | BESS Container #20 Alarm Flag |  | alarms | /assets/ess/ess_20 | alarms | Yes |  |  |  | 20 |  |  | Fault Flag
BESS Container #21 Fault Flag | HybridOS | Status | 0.2 | binary | 57 | [9 empty] | BESS Container #21 Fault Flag |  | faults | /assets/ess/ess_21 | faults | Yes |  |  |  | 21 |  |  | Alarm Flag
BESS Container #21 Alarm Flag | HybridOS | Status | 0.2 | binary | 58 | [9 empty] | BESS Container #21 Alarm Flag |  | alarms | /assets/ess/ess_21 | alarms | Yes |  |  |  | 21 |  |  | Fault Flag
BESS Container #22 Fault Flag | HybridOS | Status | 0.2 | binary | 59 | [9 empty] | BESS Container #22 Fault Flag |  | faults | /assets/ess/ess_22 | faults | Yes |  |  |  | 22 |  |  | Alarm Flag
BESS Container #22 Alarm Flag | HybridOS | Status | 0.2 | binary | 60 | [9 empty] | BESS Container #22 Alarm Flag |  | alarms | /assets/ess/ess_22 | alarms | Yes |  |  |  | 22 |  |  | Fault Flag
BESS Container #23 Fault Flag | HybridOS | Status | 0.2 | binary | 61 | [9 empty] | BESS Container #23 Fault Flag |  | faults | /assets/ess/ess_23 | faults | Yes |  |  |  | 23 |  |  | Alarm Flag
BESS Container #23 Alarm Flag | HybridOS | Status | 0.2 | binary | 62 | [9 empty] | BESS Container #23 Alarm Flag |  | alarms | /assets/ess/ess_23 | alarms | Yes |  |  |  | 23 |  |  | Fault Flag
BESS Container #24 Fault Flag | HybridOS | Status | 0.2 | binary | 63 | [9 empty] | BESS Container #24 Fault Flag |  | faults | /assets/ess/ess_24 | faults | Yes |  |  |  | 24 |  |  | Alarm Flag
BESS Container #24 Alarm Flag | HybridOS | Status | 0.2 | binary | 64 | [9 empty] | BESS Container #24 Alarm Flag |  | alarms | /assets/ess/ess_24 | alarms | Yes |  |  |  | 24 |  |  | Fault Flag
BESS Container #25 Fault Flag | HybridOS | Status | 0.2 | binary | 65 | [9 empty] | BESS Container #25 Fault Flag |  | faults | /assets/ess/ess_25 | faults | Yes |  |  |  | 25 |  |  | Alarm Flag
BESS Container #25 Alarm Flag | HybridOS | Status | 0.2 | binary | 66 | [9 empty] | BESS Container #25 Alarm Flag |  | alarms | /assets/ess/ess_25 | alarms | Yes |  |  |  | 25 |  |  | Fault Flag
BESS Container #26 Fault Flag | HybridOS | Status | 0.2 | binary | 67 | [9 empty] | BESS Container #26 Fault Flag |  | faults | /assets/ess/ess_26 | faults | Yes |  |  |  | 26 |  |  | Alarm Flag
BESS Container #26 Alarm Flag | HybridOS | Status | 0.2 | binary | 68 | [9 empty] | BESS Container #26 Alarm Flag |  | alarms | /assets/ess/ess_26 | alarms | Yes |  |  |  | 26 |  |  | Fault Flag
BESS Container #27 Fault Flag | HybridOS | Status | 0.2 | binary | 69 | [9 empty] | BESS Container #27 Fault Flag |  | faults | /assets/ess/ess_27 | faults | Yes |  |  |  | 27 |  |  | Alarm Flag
BESS Container #27 Alarm Flag | HybridOS | Status | 0.2 | binary | 70 | [9 empty] | BESS Container #27 Alarm Flag |  | alarms | /assets/ess/ess_27 | alarms | Yes |  |  |  | 27 |  |  | Fault Flag
BESS Container #28 Fault Flag | HybridOS | Status | 0.2 | binary | 71 | [9 empty] | BESS Container #28 Fault Flag |  | faults | /assets/ess/ess_28 | faults | Yes |  |  |  | 28 |  |  | Alarm Flag
BESS Container #28 Alarm Flag | HybridOS | Status | 0.2 | binary | 72 | [9 empty] | BESS Container #28 Alarm Flag |  | alarms | /assets/ess/ess_28 | alarms | Yes |  |  |  | 28 |  |  | Fault Flag
BESS Container #29 Fault Flag | HybridOS | Status | 0.2 | binary | 73 | [9 empty] | BESS Container #29 Fault Flag |  | faults | /assets/ess/ess_29 | faults | Yes |  |  |  | 29 |  |  | Alarm Flag
BESS Container #29 Alarm Flag | HybridOS | Status | 0.2 | binary | 74 | [9 empty] | BESS Container #29 Alarm Flag |  | alarms | /assets/ess/ess_29 | alarms | Yes |  |  |  | 29 |  |  | Fault Flag
BESS Container #30 Fault Flag | HybridOS | Status | 0.2 | binary | 75 | [9 empty] | BESS Container #30 Fault Flag |  | faults | /assets/ess/ess_30 | faults | Yes |  |  |  | 30 |  |  | Alarm Flag
BESS Container #30 Alarm Flag | HybridOS | Status | 0.2 | binary | 76 | [9 empty] | BESS Container #30 Alarm Flag |  | alarms | /assets/ess/ess_30 | alarms | Yes |  |  |  | 30 |  |  | Fault Flag
BESS Container #31 Fault Flag | HybridOS | Status | 0.2 | binary | 77 | [9 empty] | BESS Container #31 Fault Flag |  | faults | /assets/ess/ess_31 | faults | Yes |  |  |  | 31 |  |  | Alarm Flag
BESS Container #31 Alarm Flag | HybridOS | Status | 0.2 | binary | 78 | [9 empty] | BESS Container #31 Alarm Flag |  | alarms | /assets/ess/ess_31 | alarms | Yes |  |  |  | 31 |  |  | Fault Flag
BESS Container #32 Fault Flag | HybridOS | Status | 0.2 | binary | 79 | [9 empty] | BESS Container #32 Fault Flag |  | faults | /assets/ess/ess_32 | faults | Yes |  |  |  | 32 |  |  | Alarm Flag
BESS Container #32 Alarm Flag | HybridOS | Status | 0.2 | binary | 80 | [9 empty] | BESS Container #32 Alarm Flag |  | alarms | /assets/ess/ess_32 | alarms | Yes |  |  |  | 32 |  |  | Fault Flag
BESS Container #33 Fault Flag | HybridOS | Status | 0.2 | binary | 81 | [9 empty] | BESS Container #33 Fault Flag |  | faults | /assets/ess/ess_33 | faults | Yes |  |  |  | 33 |  |  | Alarm Flag
BESS Container #33 Alarm Flag | HybridOS | Status | 0.2 | binary | 82 | [9 empty] | BESS Container #33 Alarm Flag |  | alarms | /assets/ess/ess_33 | alarms | Yes |  |  |  | 33 |  |  | Fault Flag
Start Site Command | HybridOS | Command | 0.2 | CROB | 0 |  |  |  |  | uint32 |  |  |  |  | start site when true |  | enable_flag_dnp3 | /site/operation | enable_flag_dnp3 | Yes
Disable Site Command | HybridOS | Command | 0.2 | CROB | 1 |  |  |  |  | uint32 |  |  |  |  | disable site when true (blocks start site command) |  | disable_flag | /site/operation | disable_flag | Yes
Clear Faults Command | HybridOS | Command | 0.2 | CROB | 2 |  |  |  |  | uint32 |  |  |  |  | clear faults when true |  | clear_faults_flag_dnp3 | /site/operation | clear_faults_flag_dnp3 | Yes

## HybridOS Client
Device Name | FlexGen HybridOS
Device Protocol | DNP3
Device Protocol Version | 0.2 |  |  | Notes:
Device ID String | northfork
Device IP Address (if TCP) | 10.10.1.31
Device Port (502 typical) | 20000
base_uri | /sites
local_uri | /local_server
frequency | 1000
debug | 0
respTime | 2000
maxElapsed | 100
Name | Source Device | Type | Version | Register Type | Address | Unit | Words | Scale | Variation | Data Type | Range Start | Range End | Engineering Range Start | Engineering Range End | Description | Control Narrative for Register | Reg ID | URI | ID | Include | Repeat | Bit
Site - Active Power Total Gross | HybridOS | Status | 0.2 | analog | 0 | kW |  | 1000 | Group30Var5 | uint32 | -32768 | 32767 |  |  | Power produced as measured by BESS Inverter |  | ess_total_active_power |  | ess_total_active_power | Yes
Site - Reactive Power Total Gross | HybridOS | Status | 0.2 | analog | 1 | kVAR |  | 1000 | Group30Var5 | uint32 | -32768 | 32767 |  |  | Reactive Power produced as measued by BESS Inverter |  | ess_total_reactive_power |  | ess_total_reactive_power | Yes
Site - Apparent Power Total Gross | HybridOS | Status | 0.2 | analog | 2 | kVA |  | 1000 | Group30Var5 | uint32 | 0 | 65535 |  |  | Apparent Power as measured by the BESS Inverter |  | ess_total_apparent_power |  | ess_total_apparent_power | Yes
Site - Active Power Total Net | SEL-735 | Status | 0.2 | analog | 3 | kW |  | 1000 | Group30Var5 | uint32 | -32768 | 32767 |  |  | Aggregated Active Power exported after Aux loads |  | active_power |  | active_power | Yes
Site - Reactive Power Total Net | SEL-735 | Status | 0.2 | analog | 4 | kVAR |  | 1000 | Group30Var5 | uint32 | -32768 | 32767 |  |  | Aggregated Reactive Power exported after Aux loads |  | reactive_power |  | reactive_power | Yes
Site - Apparent Power Total Net | SEL-735 | Status | 0.2 | analog | 5 | kVA |  | 1000 | Group30Var5 | uint32 | 0 | 65535 |  |  | Aggregated Apparent Power exported after Aux Loads |  | apparent_power |  | apparent_power | Yes
Site - Frequency | SEL-735 | Status | 0.2 | analog | 6 | Hz |  |  | Group30Var5 | uint32 |  |  |  |  | Bus frequency |  | frequency |  | frequency | Yes
Site - Voltage L1-L2 | SEL-651R | Status | 0.2 | analog | 7 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L1 |  | grid_voltage_l1_l2 |  | grid_voltage_l1_l2 | Yes
Site - Voltage L2-L3 | SEL-651R | Status | 0.2 | analog | 8 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L2 |  | grid_voltage_l2_l3 |  | grid_voltage_l2_l3 | Yes
Site - Voltage L3-L1 | SEL-651R | Status | 0.2 | analog | 9 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L3 |  | grid_voltage_l3_l1 |  | grid_voltage_l3_l1 | Yes
Battery - State of Charge % | HybridOS | Status | 0.2 | analog | 10 | % |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | State of charge expressed as % of MWh capacity based on current health |  | ess_average_soc |  | ess_average_soc | Yes
Battery - Chargable energy kWh | HybridOS | Status | 0.2 | analog | 11 | kWh |  | 1000 | Group30Var5 | uint32 | 0 | 65535 |  |  | State of charge expressed as kWh of charge below 100 |  | ess_chargeable_energy |  | ess_chargeable_energy | Yes
Battery - Dischargeable energy kWh | HybridOS | Status | 0.2 | analog | 12 | kWh |  | 1000 | Group30Var5 | uint32 |  |  |  |  | State of charge expressed as kWh of discharge above 0 |  | ess_dischargeable_energy |  | ess_dischargeable_energy | Yes
Battery - Chargeable power | HybridOS | Status | 0.2 | analog | 13 | kW |  | 1000 | Group30Var5 | uint32 | 0 | 65535 |  |  | kW available to Charge |  | ess_chargeable_power |  | ess_chargeable_power | Yes
Battery - Dischargeable power | HybridOS | Status | 0.2 | analog | 14 | kW |  | 1000 | Group30Var5 | uint32 | 0 | 65535 |  |  | kW available to discharge |  | ess_dischargeable_power |  | ess_dischargeable_power | Yes
Battery - Number ESS Available | HybridOS | Status | 0.2 | analog | 15 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | BESS Units that are currently able to be connected to grid |  | num_ess_available |  | num_ess_available | Yes
Battery - Number ESS Online | HybridOS | Status | 0.2 | analog | 16 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | BESS Units that are currently connected to grid |  | running_ess_num |  | running_ess_num | Yes
Heartbeat Counter | HybridOS | Status | 0.2 | analog | 17 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Incrementing counter to indicate functional communications from Server |  | heartbeat_counter |  | heartbeat_counter | Yes
Site - kWh Delivered | HybridOS | Status | 0.2 | analog | 18 |  |  | 1000 | Group30Var5 | [7 empty] | mwh_delivered |  | mwh_delivered | Yes
Site - kWh Received | HybridOS | Status | 0.2 | analog | 19 |  |  | 1000 | Group30Var5 | [7 empty] | mwh_received |  | mwh_received | Yes
Fleet Manager Metrics Timestamp Response | HybridOS | Status | 0.2 | analog | 20 |  |  |  | Group30Var5 | [7 empty] | FM_timestamp |  | FM_timestamp | Yes
Transformer Low Side Voltage | HybridOS | Status | 0.2 | analog | 21 |  |  |  | Group30Var5 | [7 empty] | transformer_low_side_voltage |  | transformer_low_side_voltage | Yes
Generation Gross Active Power | HybridOS | Status | 0.2 | analog | 22 |  |  | 1000 | Group30Var5 | [7 empty] | gen_gross_active_power |  | gen_gross_active_power | Yes
Generation Gross Reactive Power | HybridOS | Status | 0.2 | analog | 23 |  |  | 1000 | Group30Var5 | [7 empty] | gen_gross_reactive_power |  | gen_gross_reactive_power | Yes
Auxiliary Load Active Power | HybridOS | Status | 0.2 | analog | 24 |  |  |  | Group30Var5 | [7 empty] | aux_load_active_power |  | aux_load_active_power | Yes
Auxiliary Load Reactive Power | HybridOS | Status | 0.2 | analog | 25 |  |  |  | Group30Var5 | [7 empty] | aux_load_reactive_power |  | aux_load_reactive_power | Yes
GSU Transformer Flow Active Power | HybridOS | Status | 0.2 | analog | 26 |  |  |  | Group30Var5 | [7 empty] | gsu_transformer_flow_active_power |  | gsu_transformer_flow_active_power | Yes
GSU Transformer Flow Reactive Power | HybridOS | Status | 0.2 | analog | 27 |  |  |  | Group30Var5 | [7 empty] | gsu_transformer_flow_reactive_power |  | gsu_transformer_flow_reactive_power | Yes
Estimated PCS Auxiliary Power | HybridOS | Status | 0.2 | analog | 28 |  |  |  | Group30Var5 | [7 empty] | pcs_aux_load_active_power |  | pcs_aux_load_active_power | Yes
Measured BMS Auxiliary Power | HybridOS | Status | 0.2 | analog | 29 |  |  |  | Group30Var5 | [7 empty] | battery_load_active_power |  | battery_load_active_power | Yes
Frequency Response Enable Word | HybridOS | Status | 0.2 | analog | 30 |  |  |  | Group30Var5 | [7 empty] | fr_response_enable_mask_in |  | fr_response_enable_mask_in | Yes
Baseload Power Command | HybridOS | Status | 0.2 | analog | 31 |  |  | 1000 | Group30Var5 | [7 empty] | fr_baseload_cmd_mw_in |  | fr_baseload_cmd_mw_in | Yes
FFR Inactive Power Command | HybridOS | Status | 0.2 | analog | 32 |  |  | 1000 | Group30Var5 | [7 empty] | fr_ffr_inactive_cmd_mw_in |  | fr_ffr_inactive_cmd_mw_in | Yes
FRRS UF Inactive Power Command | HybridOS | Status | 0.2 | analog | 33 |  |  | 1000 | Group30Var5 | [7 empty] | fr_frrs_up_inactive_cmd_mw_in |  | fr_frrs_up_inactive_cmd_mw_in | Yes
FRRS OF Inactive Power Command | HybridOS | Status | 0.2 | analog | 34 |  |  | 1000 | Group30Var5 | [7 empty] | fr_frrs_down_inactive_cmd_mw_in |  | fr_frrs_down_inactive_cmd_mw_in | Yes
FRRS Up Active Power Command | HybridOS | Status | 0.2 | analog | 35 |  |  | 1000 | Group30Var5 | [7 empty] | fr_frrs_up_active_cmd_mw_in |  | fr_frrs_up_active_cmd_mw_in | Yes
FRRS Down Active Power Command | HybridOS | Status | 0.2 | analog | 36 |  |  | 1000 | Group30Var5 | [7 empty] | fr_frrs_down_active_cmd_mw_in |  | fr_frrs_down_active_cmd_mw_in | Yes
FFR Active Power Command | HybridOS | Status | 0.2 | analog | 37 |  |  | 1000 | Group30Var5 | [7 empty] | fr_ffr_active_cmd_mw_in |  | fr_ffr_active_cmd_mw_in | Yes
Auto-PFR Up Active Power Command | HybridOS | Status | 0.2 | analog | 38 |  |  | 1000 | Group30Var5 | [7 empty] | fr_pfr_up_active_cmd_mw_in |  | fr_pfr_up_active_cmd_mw_in | Yes
Auto-PFR Down Active Power Command | HybridOS | Status | 0.2 | analog | 39 |  |  | 1000 | Group30Var5 | [7 empty] | fr_pfr_down_active_cmd_mw_in |  | fr_pfr_down_active_cmd_mw_in | Yes
Site Active Power Charge Limit | HybridOS | Status | 0.2 | analog | 40 |  |  | -1000 | Group30Var5 | [7 empty] | site_chargeable_mw |  | site_chargeable_mw | Yes
Site Active Power Discharge Limit | HybridOS | Status | 0.2 | analog | 41 |  |  | 1000 | Group30Var5 | [7 empty] | site_dischargeable_mw |  | site_dischargeable_mw | Yes
BESS Container #1 System Mode | HybridOS | Status | 0.2 | analog | 42 |  |  |  | Group30Var5 | uint32 | 0 | 4294967295 | 0 |  | BESS Container #1 System mode of operation |  | ess_1_status |  | ess_1_status | Yes
BESS Container #1 System SOC | HybridOS | Status | 0.2 | analog | 43 | % |  |  | Group30Var5 | uint32 | 0 | 65535 | 0 |  | BESS Container #1 State of Charge |  | ess_1_soc |  | ess_1_soc | Yes
BESS Container #1 Number of Active Racks | HybridOS | Status | 0.2 | analog | 44 | # |  |  | Group30Var5 | uint32 | 0 | 65535 | 0 |  | BESS Container #1 Number of Active Racks |  | ess_1_racks |  | ess_1_racks | Yes
BESS Container #2 System Mode | HybridOS | Status | 0.2 | analog | 45 |  |  |  | Group30Var5 | uint32 | 0 | -1227049253.5714 | 0 |  | BESS Container #2 System mode of operation |  | ess_2_status |  | ess_2_status | Yes
BESS Container #2 System SOC | HybridOS | Status | 0.2 | analog | 46 | % |  |  | Group30Var5 | uint32 | 0 | -4908393619.2857 | 0 |  | BESS Container #2 State of Charge |  | ess_2_soc |  | ess_2_soc | Yes
BESS Container #2 Number of Active Racks | HybridOS | Status | 0.2 | analog | 47 | # |  |  | Group30Var5 | uint32 | 0 | -6135508407.8572 | 0 |  | BESS Container #2 Number of Active Racks |  | ess_2_racks |  | ess_2_racks | Yes
BESS Container #3 System Mode | HybridOS | Status | 0.2 | analog | 48 |  |  |  | Group30Var5 | uint32 | 0 | -8589737985 | 0 |  | BESS Container #3 System mode of operation |  | ess_3_status |  | ess_3_status | Yes
BESS Container #3 System SOC | HybridOS | Status | 0.2 | analog | 49 | % |  |  | Group30Var5 | uint32 | 0 | -12271082350.7143 | 0 |  | BESS Container #3 State of Charge |  | ess_3_soc |  | ess_3_soc | Yes
BESS Container #3 Number of Active Racks | HybridOS | Status | 0.2 | analog | 50 | # |  |  | Group30Var5 | uint32 | 0 | -13498197139.2858 | 0 |  | BESS Container #3 Number of Active Racks |  | ess_3_racks |  | ess_3_racks | Yes
BESS Container #4 System Mode | HybridOS | Status | 0.2 | analog | 51 |  |  |  | Group30Var5 | uint32 | 0 | -14725311927.8572 | 0 |  | BESS Container #4 System mode of operation |  | ess_4_status |  | ess_4_status | Yes
BESS Container #4 System SOC | HybridOS | Status | 0.2 | analog | 52 | % |  |  | Group30Var5 | uint32 | 0 | -18406656293.5716 | 0 |  | BESS Container #4 State of Charge |  | ess_4_soc |  | ess_4_soc | Yes
BESS Container #4 Number of Active Racks | HybridOS | Status | 0.2 | analog | 53 | # |  |  | Group30Var5 | uint32 | 0 | -19633771082.143 | 0 |  | BESS Container #4 Number of Active Racks |  | ess_4_racks |  | ess_4_racks | Yes
BESS Container #5 System Mode | HybridOS | Status | 0.2 | analog | 54 |  |  |  | Group30Var5 | [5 empty] | BESS Container #5 System mode of operation |  | ess_5_status |  | ess_5_status | Yes
BESS Container #5 System SOC | HybridOS | Status | 0.2 | analog | 55 | % |  |  | Group30Var5 | [5 empty] | BESS Container #5 State of Charge |  | ess_5_soc |  | ess_5_soc | Yes
BESS Container #5 Number of Active Racks | HybridOS | Status | 0.2 | analog | 56 | # |  |  | Group30Var5 | [5 empty] | BESS Container #5 Number of Active Racks |  | ess_5_racks |  | ess_5_racks | Yes
BESS Container #6 System Mode | HybridOS | Status | 0.2 | analog | 57 |  |  |  | Group30Var5 | [5 empty] | BESS Container #6 System mode of operation |  | ess_6_status |  | ess_6_status | Yes
BESS Container #6 System SOC | HybridOS | Status | 0.2 | analog | 58 | % |  |  | Group30Var5 | [5 empty] | BESS Container #6 State of Charge |  | ess_6_soc |  | ess_6_soc | Yes
BESS Container #6 Number of Active Racks | HybridOS | Status | 0.2 | analog | 59 | # |  |  | Group30Var5 | [5 empty] | BESS Container #6 Number of Active Racks |  | ess_6_racks |  | ess_6_racks | Yes
BESS Container #7 System Mode | HybridOS | Status | 0.2 | analog | 60 |  |  |  | Group30Var5 | [5 empty] | BESS Container #7 System mode of operation |  | ess_7_status |  | ess_7_status | Yes
BESS Container #7 System SOC | HybridOS | Status | 0.2 | analog | 61 | % |  |  | Group30Var5 | [5 empty] | BESS Container #7 State of Charge |  | ess_7_soc |  | ess_7_soc | Yes
BESS Container #7 Number of Active Racks | HybridOS | Status | 0.2 | analog | 62 | # |  |  | Group30Var5 | [5 empty] | BESS Container #7 Number of Active Racks |  | ess_7_racks |  | ess_7_racks | Yes
BESS Container #8 System Mode | HybridOS | Status | 0.2 | analog | 63 |  |  |  | Group30Var5 | [5 empty] | BESS Container #8 System mode of operation |  | ess_8_status |  | ess_8_status | Yes
BESS Container #8 System SOC | HybridOS | Status | 0.2 | analog | 64 | % |  |  | Group30Var5 | [5 empty] | BESS Container #8 State of Charge |  | ess_8_soc |  | ess_8_soc | Yes
BESS Container #8 Number of Active Racks | HybridOS | Status | 0.2 | analog | 65 | # |  |  | Group30Var5 | [5 empty] | BESS Container #8 Number of Active Racks |  | ess_8_racks |  | ess_8_racks | Yes
BESS Container #9 System Mode | HybridOS | Status | 0.2 | analog | 66 |  |  |  | Group30Var5 | [5 empty] | BESS Container #9 System mode of operation |  | ess_9_status |  | ess_9_status | Yes
BESS Container #9 System SOC | HybridOS | Status | 0.2 | analog | 67 | % |  |  | Group30Var5 | [5 empty] | BESS Container #9 State of Charge |  | ess_9_soc |  | ess_9_soc | Yes
BESS Container #9 Number of Active Racks | HybridOS | Status | 0.2 | analog | 68 | # |  |  | Group30Var5 | [5 empty] | BESS Container #9 Number of Active Racks |  | ess_9_racks |  | ess_9_racks | Yes
BESS Container #10 System Mode | HybridOS | Status | 0.2 | analog | 69 |  |  |  | Group30Var5 | [5 empty] | BESS Container #10 System mode of operation |  | ess_10_status |  | ess_10_status | Yes
BESS Container #10 System SOC | HybridOS | Status | 0.2 | analog | 70 | % |  |  | Group30Var5 | [5 empty] | BESS Container #10 State of Charge |  | ess_10_soc |  | ess_10_soc | Yes
BESS Container #10 Number of Active Racks | HybridOS | Status | 0.2 | analog | 71 | # |  |  | Group30Var5 | [5 empty] | BESS Container #10 Number of Active Racks |  | ess_10_racks |  | ess_10_racks | Yes
BESS Container #11 System Mode | HybridOS | Status | 0.2 | analog | 72 |  |  |  | Group30Var5 | [5 empty] | BESS Container #11 System mode of operation |  | ess_11_status |  | ess_11_status | Yes
BESS Container #11 System SOC | HybridOS | Status | 0.2 | analog | 73 | % |  |  | Group30Var5 | [5 empty] | BESS Container #11 State of Charge |  | ess_11_soc |  | ess_11_soc | Yes
BESS Container #11 Number of Active Racks | HybridOS | Status | 0.2 | analog | 74 | # |  |  | Group30Var5 | [5 empty] | BESS Container #11 Number of Active Racks |  | ess_11_racks |  | ess_11_racks | Yes
BESS Container #12 System Mode | HybridOS | Status | 0.2 | analog | 75 |  |  |  | Group30Var5 | [5 empty] | BESS Container #12 System mode of operation |  | ess_12_status |  | ess_12_status | Yes
BESS Container #12 System SOC | HybridOS | Status | 0.2 | analog | 76 | % |  |  | Group30Var5 | [5 empty] | BESS Container #12 State of Charge |  | ess_12_soc |  | ess_12_soc | Yes
BESS Container #12 Number of Active Racks | HybridOS | Status | 0.2 | analog | 77 | # |  |  | Group30Var5 | [5 empty] | BESS Container #12 Number of Active Racks |  | ess_12_racks |  | ess_12_racks | Yes
BESS Container #13 System Mode | HybridOS | Status | 0.2 | analog | 78 |  |  |  | Group30Var5 | [5 empty] | BESS Container #13 System mode of operation |  | ess_13_status |  | ess_13_status | Yes
BESS Container #13 System SOC | HybridOS | Status | 0.2 | analog | 79 | % |  |  | Group30Var5 | [5 empty] | BESS Container #13 State of Charge |  | ess_13_soc |  | ess_13_soc | Yes
BESS Container #13 Number of Active Racks | HybridOS | Status | 0.2 | analog | 80 | # |  |  | Group30Var5 | [5 empty] | BESS Container #13 Number of Active Racks |  | ess_13_racks |  | ess_13_racks | Yes
BESS Container #14 System Mode | HybridOS | Status | 0.2 | analog | 81 |  |  |  | Group30Var5 | [5 empty] | BESS Container #14 System mode of operation |  | ess_14_status |  | ess_14_status | Yes
BESS Container #14 System SOC | HybridOS | Status | 0.2 | analog | 82 | % |  |  | Group30Var5 | [5 empty] | BESS Container #14 State of Charge |  | ess_14_soc |  | ess_14_soc | Yes
BESS Container #14 Number of Active Racks | HybridOS | Status | 0.2 | analog | 83 | # |  |  | Group30Var5 | [5 empty] | BESS Container #14 Number of Active Racks |  | ess_14_racks |  | ess_14_racks | Yes
BESS Container #15 System Mode | HybridOS | Status | 0.2 | analog | 84 |  |  |  | Group30Var5 | [5 empty] | BESS Container #15 System mode of operation |  | ess_15_status |  | ess_15_status | Yes
BESS Container #15 System SOC | HybridOS | Status | 0.2 | analog | 85 | % |  |  | Group30Var5 | [5 empty] | BESS Container #15 State of Charge |  | ess_15_soc |  | ess_15_soc | Yes
BESS Container #15 Number of Active Racks | HybridOS | Status | 0.2 | analog | 86 | # |  |  | Group30Var5 | [5 empty] | BESS Container #15 Number of Active Racks |  | ess_15_racks |  | ess_15_racks | Yes
BESS Container #16 System Mode | HybridOS | Status | 0.2 | analog | 87 |  |  |  | Group30Var5 | [5 empty] | BESS Container #16 System mode of operation |  | ess_16_status |  | ess_16_status | Yes
BESS Container #16 System SOC | HybridOS | Status | 0.2 | analog | 88 | % |  |  | Group30Var5 | [5 empty] | BESS Container #16 State of Charge |  | ess_16_soc |  | ess_16_soc | Yes
BESS Container #16 Number of Active Racks | HybridOS | Status | 0.2 | analog | 89 | # |  |  | Group30Var5 | [5 empty] | BESS Container #16 Number of Active Racks |  | ess_16_racks |  | ess_16_racks | Yes
BESS Container #17 System Mode | HybridOS | Status | 0.2 | analog | 90 |  |  |  | Group30Var5 | [5 empty] | BESS Container #17 System mode of operation |  | ess_17_status |  | ess_17_status | Yes
BESS Container #17 System SOC | HybridOS | Status | 0.2 | analog | 91 | % |  |  | Group30Var5 | [5 empty] | BESS Container #17 State of Charge |  | ess_17_soc |  | ess_17_soc | Yes
BESS Container #17 Number of Active Racks | HybridOS | Status | 0.2 | analog | 92 | # |  |  | Group30Var5 | [5 empty] | BESS Container #17 Number of Active Racks |  | ess_17_racks |  | ess_17_racks | Yes
BESS Container #18 System Mode | HybridOS | Status | 0.2 | analog | 93 |  |  |  | Group30Var5 | [5 empty] | BESS Container #18 System mode of operation |  | ess_18_status |  | ess_18_status | Yes
BESS Container #18 System SOC | HybridOS | Status | 0.2 | analog | 94 | % |  |  | Group30Var5 | [5 empty] | BESS Container #18 State of Charge |  | ess_18_soc |  | ess_18_soc | Yes
BESS Container #18 Number of Active Racks | HybridOS | Status | 0.2 | analog | 95 | # |  |  | Group30Var5 | [5 empty] | BESS Container #18 Number of Active Racks |  | ess_18_racks |  | ess_18_racks | Yes
BESS Container #19 System Mode | HybridOS | Status | 0.2 | analog | 96 |  |  |  | Group30Var5 | [5 empty] | BESS Container #19 System mode of operation |  | ess_19_status |  | ess_19_status | Yes
BESS Container #19 System SOC | HybridOS | Status | 0.2 | analog | 97 | % |  |  | Group30Var5 | [5 empty] | BESS Container #19 State of Charge |  | ess_19_soc |  | ess_19_soc | Yes
BESS Container #19 Number of Active Racks | HybridOS | Status | 0.2 | analog | 98 | # |  |  | Group30Var5 | [5 empty] | BESS Container #19 Number of Active Racks |  | ess_19_racks |  | ess_19_racks | Yes
BESS Container #20 System Mode | HybridOS | Status | 0.2 | analog | 99 |  |  |  | Group30Var5 | [5 empty] | BESS Container #20 System mode of operation |  | ess_20_status |  | ess_20_status | Yes
BESS Container #20 System SOC | HybridOS | Status | 0.2 | analog | 100 | % |  |  | Group30Var5 | [5 empty] | BESS Container #20 State of Charge |  | ess_20_soc |  | ess_20_soc | Yes
BESS Container #20 Number of Active Racks | HybridOS | Status | 0.2 | analog | 101 | # |  |  | Group30Var5 | [5 empty] | BESS Container #20 Number of Active Racks |  | ess_20_racks |  | ess_20_racks | Yes
BESS Container #21 System Mode | HybridOS | Status | 0.2 | analog | 102 |  |  |  | Group30Var5 | [5 empty] | BESS Container #21 System mode of operation |  | ess_21_status |  | ess_21_status | Yes
BESS Container #21 System SOC | HybridOS | Status | 0.2 | analog | 103 | % |  |  | Group30Var5 | [5 empty] | BESS Container #21 State of Charge |  | ess_21_soc |  | ess_21_soc | Yes
BESS Container #21 Number of Active Racks | HybridOS | Status | 0.2 | analog | 104 | # |  |  | Group30Var5 | [5 empty] | BESS Container #21 Number of Active Racks |  | ess_21_racks |  | ess_21_racks | Yes
BESS Container #22 System Mode | HybridOS | Status | 0.2 | analog | 105 |  |  |  | Group30Var5 | [5 empty] | BESS Container #22 System mode of operation |  | ess_22_status |  | ess_22_status | Yes
BESS Container #22 System SOC | HybridOS | Status | 0.2 | analog | 106 | % |  |  | Group30Var5 | [5 empty] | BESS Container #22 State of Charge |  | ess_22_soc |  | ess_22_soc | Yes
BESS Container #22 Number of Active Racks | HybridOS | Status | 0.2 | analog | 107 | # |  |  | Group30Var5 | [5 empty] | BESS Container #22 Number of Active Racks |  | ess_22_racks |  | ess_22_racks | Yes
BESS Container #23 System Mode | HybridOS | Status | 0.2 | analog | 108 |  |  |  | Group30Var5 | [5 empty] | BESS Container #23 System mode of operation |  | ess_23_status |  | ess_23_status | Yes
BESS Container #23 System SOC | HybridOS | Status | 0.2 | analog | 109 | % |  |  | Group30Var5 | [5 empty] | BESS Container #23 State of Charge |  | ess_23_soc |  | ess_23_soc | Yes
BESS Container #23 Number of Active Racks | HybridOS | Status | 0.2 | analog | 110 | # |  |  | Group30Var5 | [5 empty] | BESS Container #23 Number of Active Racks |  | ess_23_racks |  | ess_23_racks | Yes
BESS Container #24 System Mode | HybridOS | Status | 0.2 | analog | 111 |  |  |  | Group30Var5 | [5 empty] | BESS Container #24 System mode of operation |  | ess_24_status |  | ess_24_status | Yes
BESS Container #24 System SOC | HybridOS | Status | 0.2 | analog | 112 | % |  |  | Group30Var5 | [5 empty] | BESS Container #24 State of Charge |  | ess_24_soc |  | ess_24_soc | Yes
BESS Container #24 Number of Active Racks | HybridOS | Status | 0.2 | analog | 113 | # |  |  | Group30Var5 | [5 empty] | BESS Container #24 Number of Active Racks |  | ess_24_racks |  | ess_24_racks | Yes
BESS Container #25 System Mode | HybridOS | Status | 0.2 | analog | 114 |  |  |  | Group30Var5 | [5 empty] | BESS Container #25 System mode of operation |  | ess_25_status |  | ess_25_status | Yes
BESS Container #25 System SOC | HybridOS | Status | 0.2 | analog | 115 | % |  |  | Group30Var5 | [5 empty] | BESS Container #25 State of Charge |  | ess_25_soc |  | ess_25_soc | Yes
BESS Container #25 Number of Active Racks | HybridOS | Status | 0.2 | analog | 116 | # |  |  | Group30Var5 | [5 empty] | BESS Container #25 Number of Active Racks |  | ess_25_racks |  | ess_25_racks | Yes
BESS Container #26 System Mode | HybridOS | Status | 0.2 | analog | 117 |  |  |  | Group30Var5 | [5 empty] | BESS Container #26 System mode of operation |  | ess_26_status |  | ess_26_status | Yes
BESS Container #26 System SOC | HybridOS | Status | 0.2 | analog | 118 | % |  |  | Group30Var5 | [5 empty] | BESS Container #26 State of Charge |  | ess_26_soc |  | ess_26_soc | Yes
BESS Container #26 Number of Active Racks | HybridOS | Status | 0.2 | analog | 119 | # |  |  | Group30Var5 | [5 empty] | BESS Container #26 Number of Active Racks |  | ess_26_racks |  | ess_26_racks | Yes
BESS Container #27 System Mode | HybridOS | Status | 0.2 | analog | 120 |  |  |  | Group30Var5 | [5 empty] | BESS Container #27 System mode of operation |  | ess_27_status |  | ess_27_status | Yes
BESS Container #27 System SOC | HybridOS | Status | 0.2 | analog | 121 | % |  |  | Group30Var5 | [5 empty] | BESS Container #27 State of Charge |  | ess_27_soc |  | ess_27_soc | Yes
BESS Container #27 Number of Active Racks | HybridOS | Status | 0.2 | analog | 122 | # |  |  | Group30Var5 | [5 empty] | BESS Container #27 Number of Active Racks |  | ess_27_racks |  | ess_27_racks | Yes
BESS Container #28 System Mode | HybridOS | Status | 0.2 | analog | 123 |  |  |  | Group30Var5 | [5 empty] | BESS Container #28 System mode of operation |  | ess_28_status |  | ess_28_status | Yes
BESS Container #28 System SOC | HybridOS | Status | 0.2 | analog | 124 | % |  |  | Group30Var5 | [5 empty] | BESS Container #28 State of Charge |  | ess_28_soc |  | ess_28_soc | Yes
BESS Container #28 Number of Active Racks | HybridOS | Status | 0.2 | analog | 125 | # |  |  | Group30Var5 | [5 empty] | BESS Container #28 Number of Active Racks |  | ess_28_racks |  | ess_28_racks | Yes
BESS Container #29 System Mode | HybridOS | Status | 0.2 | analog | 126 |  |  |  | Group30Var5 | [5 empty] | BESS Container #29 System mode of operation |  | ess_29_status |  | ess_29_status | Yes
BESS Container #29 System SOC | HybridOS | Status | 0.2 | analog | 127 | % |  |  | Group30Var5 | [5 empty] | BESS Container #29 State of Charge |  | ess_29_soc |  | ess_29_soc | Yes
BESS Container #29 Number of Active Racks | HybridOS | Status | 0.2 | analog | 128 | # |  |  | Group30Var5 | [5 empty] | BESS Container #29 Number of Active Racks |  | ess_29_racks |  | ess_29_racks | Yes
BESS Container #30 System Mode | HybridOS | Status | 0.2 | analog | 129 |  |  |  | Group30Var5 | [5 empty] | BESS Container #30 System mode of operation |  | ess_30_status |  | ess_30_status | Yes
BESS Container #30 System SOC | HybridOS | Status | 0.2 | analog | 130 | % |  |  | Group30Var5 | [5 empty] | BESS Container #30 State of Charge |  | ess_30_soc |  | ess_30_soc | Yes
BESS Container #30 Number of Active Racks | HybridOS | Status | 0.2 | analog | 131 | # |  |  | Group30Var5 | [5 empty] | BESS Container #30 Number of Active Racks |  | ess_30_racks |  | ess_30_racks | Yes
BESS Container #31 System Mode | HybridOS | Status | 0.2 | analog | 132 |  |  |  | Group30Var5 | [5 empty] | BESS Container #31 System mode of operation |  | ess_31_status |  | ess_31_status | Yes
BESS Container #31 System SOC | HybridOS | Status | 0.2 | analog | 133 | % |  |  | Group30Var5 | [5 empty] | BESS Container #31 State of Charge |  | ess_31_soc |  | ess_31_soc | Yes
BESS Container #31 Number of Active Racks | HybridOS | Status | 0.2 | analog | 134 | # |  |  | Group30Var5 | [5 empty] | BESS Container #31 Number of Active Racks |  | ess_31_racks |  | ess_31_racks | Yes
BESS Container #32 System Mode | HybridOS | Status | 0.2 | analog | 135 |  |  |  | Group30Var5 | [5 empty] | BESS Container #32 System mode of operation |  | ess_32_status |  | ess_32_status | Yes
BESS Container #32 System SOC | HybridOS | Status | 0.2 | analog | 136 | % |  |  | Group30Var5 | [5 empty] | BESS Container #32 State of Charge |  | ess_32_soc |  | ess_32_soc | Yes
BESS Container #32 Number of Active Racks | HybridOS | Status | 0.2 | analog | 137 | # |  |  | Group30Var5 | [5 empty] | BESS Container #32 Number of Active Racks |  | ess_32_racks |  | ess_32_racks | Yes
BESS Container #33 System Mode | HybridOS | Status | 0.2 | analog | 138 |  |  |  | Group30Var5 | [5 empty] | BESS Container #33 System mode of operation |  | ess_33_status |  | ess_33_status | Yes
BESS Container #33 System SOC | HybridOS | Status | 0.2 | analog | 139 | % |  |  | Group30Var5 | [5 empty] | BESS Container #33 State of Charge |  | ess_33_soc |  | ess_33_soc | Yes
BESS Container #33 Number of Active Racks | HybridOS | Status | 0.2 | analog | 140 |  |  |  | Group30Var5 | [5 empty] | BESS Container #33 Number of Active Racks |  | ess_33_racks |  | ess_33_racks | Yes
Watchdog Pet | HybridOS | Command | 0.2 | AnOPF32 | 0 |  |  |  |  | uint32 |  |  |  |  | Client will write this register with unique integer periodically |  | watchdog_pet |  | watchdog_pet | Yes
Frequency Response Enable Word | HybridOS | Command | 0.2 | AnOPF32 | 1 | [11 empty] | fr_response_enable_mask |  | fr_response_enable_mask | Yes
Baseload Power Command | HybridOS | Command | 0.2 | AnOPF32 | 2 | mw |  | 1000 | [8 empty] | fr_baseload_cmd_mw |  | fr_baseload_cmd_mw | Yes
FFR Inactive Power Command | HybridOS | Command | 0.2 | AnOPF32 | 3 | mw |  | 1000 | [8 empty] | fr_ffr_inactive_cmd_mw |  | fr_ffr_inactive_cmd_mw | Yes
UF FRRS Inactive Power Command | HybridOS | Command | 0.2 | AnOPF32 | 4 | mw |  | 1000 | [8 empty] | fr_frrs_up_inactive_cmd_mw |  | fr_frrs_up_inactive_cmd_mw | Yes
FRRS Inactive Power Command | HybridOS | Command | 0.2 | AnOPF32 | 5 | mw |  | 1000 | [8 empty] | fr_frrs_down_inactive_cmd_mw |  | fr_frrs_down_inactive_cmd_mw | Yes
UF FRRS Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 6 | mw |  | 1000 | [8 empty] | fr_frrs_up_active_cmd_mw |  | fr_frrs_up_active_cmd_mw | Yes
OF FRRS Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 7 | mw |  | 1000 | [8 empty] | fr_frrs_down_active_cmd_mw |  | fr_frrs_down_active_cmd_mw | Yes
FFR Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 8 | mw |  | 1000 | [8 empty] | fr_ffr_active_cmd_mw |  | fr_ffr_active_cmd_mw | Yes
UF PFR Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 9 | mw |  | 1000 | [8 empty] | fr_pfr_up_active_cmd_mw |  | fr_pfr_up_active_cmd_mw | Yes
OF PFR Active Power Command | HybridOS | Command | 0.2 | AnOPF32 | 10 | mw |  | 1000 | [8 empty] | fr_pfr_down_active_cmd_mw |  | fr_pfr_down_active_cmd_mw | Yes
Fleet Manager Metrics Timestamp | HybridOS | Command | 0.2 | AnOPF32 | 11 | [11 empty] | fm_timestamp |  | fm_timestamp | Yes
Active Voltage Regulation Command | HybridOS | Command | 0.2 | AnOPF32 | 12 | V | [10 empty] | active_voltage_cmd_local |  | active_voltage_cmd_local | Yes
Reactive Power Setpoint | HybridOS | Command | 0.2 | AnOPF32 | 13 | kVAR | [10 empty] | reactive_setpoint_kVAR_cmd_local |  | reactive_setpoint_kVAR_cmd_local | Yes
Reactive Power Mode Select Command | HybridOS | Command | 0.2 | AnOPF32 | 14 | [11 empty] | features_kVAR_mode_cmd |  | features_kVAR_mode_cmd
Main Breaker Closed | SEL-651 | Status | 0.2 | binary | 0 |  |  |  |  | uint32 | 0 | 65535 | 5 |  | Main Breaker Closed | Bit 5 = MAIN BREAKER OPEN STATUS ¦ 1 = breaker closed, 0 = breaker open | breaker_status |  | breaker_status | Yes
Running Status | HybridOS | Status | 0.2 | binary | 1 |  |  |  |  | bool | 0 | 65535 |  |  | BESS Plant running status, feeder closed, at least one ESS or PV on | 0 = Not running, 1 = Running | running_status_flag |  | running_status_flag | Yes
Alarm Status | HybridOS | Status | 0.2 | binary | 2 |  |  |  |  | bool | 0 | 65535 |  |  | If any alarm is present, performance may be degraded and site requires attention | 0 = No alarms present, 1 = Alarms present | alarm_status_flag |  | alarm_status_flag | Yes
Fault Status | HybridOS | Status | 0.2 | binary | 3 |  |  |  |  | bool | 0 | 65535 |  |  | If any fault is present that prevents BESS plant from running on grid. | 0 = No faults present, 1 = Faults present | fault_status_flag |  | fault_status_flag | Yes
FFR UF Response Status | HybridOS | Status | 0.2 | binary | 4 | [11 empty] | fr_ffr_status_flag |  | fr_ffr_status_flag | Yes
FFR UF Cooldown Status | HybridOS | Status | 0.2 | binary | 5 | [11 empty] | fr_ffr_cooldown_status |  | fr_ffr_cooldown_status | Yes
PFR UF Response Status | HybridOS | Status | 0.2 | binary | 6 | [11 empty] | fr_pfr_up_status_flag |  | fr_pfr_up_status_flag | Yes
PFR UF Cooldown Status | HybridOS | Status | 0.2 | binary | 7 | [11 empty] | fr_pfr_up_cooldown_status |  | fr_pfr_up_cooldown_status | Yes
PFR OF Response Status" | HybridOS | Status | 0.2 | binary | 8 | [11 empty] | fr_pfr_down_status_flag |  | fr_pfr_down_status_flag | Yes
PFR OF Cooldown Status | HybridOS | Status | 0.2 | binary | 9 | [11 empty] | fr_pfr_down_cooldown_status |  | fr_pfr_down_cooldown_status | Yes
FRRS UF Response Status | HybridOS | Status | 0.2 | binary | 10 | [11 empty] | fr_frrs_up_status_flag |  | fr_frrs_up_status_flag | Yes
FRRS UF Cooldown Status | HybridOS | Status | 0.2 | binary | 11 | [11 empty] | fr_frrs_up_cooldown_status |  | fr_frrs_up_cooldown_status | Yes
FRRS OF Response Status | HybridOS | Status | 0.2 | binary | 12 | [11 empty] | fr_frrs_down_status_flag |  | fr_frrs_down_status_flag | Yes
FRRS OF Cooldown Status | HybridOS | Status | 0.2 | binary | 13 | [11 empty] | fr_frrs_down_cooldown_status |  | fr_frrs_down_cooldown_status | Yes
Virtual MV Breaker Status (SEL-351s) | HybridOS | Status | 0.2 | binary | 14 | [11 empty] | virtual_switch_status |  | virtual_switch_status | Yes
Generation AVR Status | HybridOS | Status | 0.2 | binary | 15 | [11 empty] | avr_status |  | avr_status | Yes
Generation Reactive Setpoint Status | HybridOS | Status | 0.2 | binary | 16 | [11 empty] | reactive_setpoint_status |  | reactive_setpoint_status | Yes
BESS Container #1 Fault Flag | HybridOS | Status | 0.2 | binary | 17 |  |  |  |  | bool |  |  |  |  | BESS Container #1 Fault Flag |  | ess_1_faults |  | ess_1_faults | Yes
BESS Container #1 Alarm Flag | HybridOS | Status | 0.2 | binary | 18 |  |  |  |  | bool | 0 | 4294967295 | 0 | 100 | BESS Container #1 Alarm Flag |  | ess_1_alarms |  | ess_1_alarms | Yes
BESS Container #2 Fault Flag | HybridOS | Status | 0.2 | binary | 19 |  |  |  |  | bool |  | -2454164042.1428 |  | 102.2857 | BESS Container #2 Fault Flag |  | ess_2_faults |  | ess_2_faults | Yes
BESS Container #2 Alarm Flag | HybridOS | Status | 0.2 | binary | 20 |  |  |  |  | bool | 0 | -3681278830.7143 | 0 | 113.0286 | BESS Container #2 Alarm Flag |  | ess_2_alarms |  | ess_2_alarms | Yes
BESS Container #3 Fault Flag | HybridOS | Status | 0.2 | binary | 21 |  |  |  |  | bool |  | -9816852773.5715 |  | 166.7429 | BESS Container #3 Fault Flag |  | ess_3_faults |  | ess_3_faults | Yes
BESS Container #3 Alarm Flag | HybridOS | Status | 0.2 | binary | 22 |  |  |  |  | bool | 0 | -11043967562.1429 | 0 | 177.4857 | BESS Container #3 Alarm Flag |  | ess_3_alarms |  | ess_3_alarms | Yes
BESS Container #4 Fault Flag | HybridOS | Status | 0.2 | binary | 23 |  |  |  |  | bool |  | -15952426716.4287 |  | 220.4571 | BESS Container #4 Fault Flag |  | ess_4_faults |  | ess_4_faults | Yes
BESS Container #4 Alarm Flag | HybridOS | Status | 0.2 | binary | 24 |  |  |  |  | bool | 0 | -17179541505.0001 | 0 | 231.2 | BESS Container #4 Alarm Flag |  | ess_4_alarms |  | ess_4_alarms | Yes
BESS Container #5 Fault Flag | HybridOS | Status | 0.2 | binary | 25 | [9 empty] | BESS Container #5 Fault Flag |  | ess_5_faults |  | ess_5_faults | Yes
BESS Container #5 Alarm Flag | HybridOS | Status | 0.2 | binary | 26 | [9 empty] | BESS Container #5 Alarm Flag |  | ess_5_alarms |  | ess_5_alarms | Yes
BESS Container #6 Fault Flag | HybridOS | Status | 0.2 | binary | 27 | [9 empty] | BESS Container #6 Fault Flag |  | ess_6_faults |  | ess_6_faults | Yes
BESS Container #6 Alarm Flag | HybridOS | Status | 0.2 | binary | 28 | [9 empty] | BESS Container #6 Alarm Flag |  | ess_6_alarms |  | ess_6_alarms | Yes
BESS Container #7 Fault Flag | HybridOS | Status | 0.2 | binary | 29 | [9 empty] | BESS Container #7 Fault Flag |  | ess_7_faults |  | ess_7_faults | Yes
BESS Container #7 Alarm Flag | HybridOS | Status | 0.2 | binary | 30 | [9 empty] | BESS Container #7 Alarm Flag |  | ess_7_alarms |  | ess_7_alarms | Yes
BESS Container #8 Fault Flag | HybridOS | Status | 0.2 | binary | 31 | [9 empty] | BESS Container #8 Fault Flag |  | ess_8_faults |  | ess_8_faults | Yes
BESS Container #8 Alarm Flag | HybridOS | Status | 0.2 | binary | 32 | [9 empty] | BESS Container #8 Alarm Flag |  | ess_8_alarms |  | ess_8_alarms | Yes
BESS Container #9 Fault Flag | HybridOS | Status | 0.2 | binary | 33 | [9 empty] | BESS Container #9 Fault Flag |  | ess_9_faults |  | ess_9_faults | Yes
BESS Container #9 Alarm Flag | HybridOS | Status | 0.2 | binary | 34 | [9 empty] | BESS Container #9 Alarm Flag |  | ess_9_alarms |  | ess_9_alarms | Yes
BESS Container #10 Fault Flag | HybridOS | Status | 0.2 | binary | 35 | [9 empty] | BESS Container #10 Fault Flag |  | ess_10_faults |  | ess_10_faults | Yes
BESS Container #10 Alarm Flag | HybridOS | Status | 0.2 | binary | 36 | [9 empty] | BESS Container #10 Alarm Flag |  | ess_10_alarms |  | ess_10_alarms | Yes
BESS Container #11 Fault Flag | HybridOS | Status | 0.2 | binary | 37 | [9 empty] | BESS Container #11 Fault Flag |  | ess_11_faults |  | ess_11_faults | Yes
BESS Container #11 Alarm Flag | HybridOS | Status | 0.2 | binary | 38 | [9 empty] | BESS Container #11 Alarm Flag |  | ess_11_alarms |  | ess_11_alarms | Yes
BESS Container #12 Fault Flag | HybridOS | Status | 0.2 | binary | 39 | [9 empty] | BESS Container #12 Fault Flag |  | ess_12_faults |  | ess_12_faults | Yes
BESS Container #12 Alarm Flag | HybridOS | Status | 0.2 | binary | 40 | [9 empty] | BESS Container #12 Alarm Flag |  | ess_12_alarms |  | ess_12_alarms | Yes
BESS Container #13 Fault Flag | HybridOS | Status | 0.2 | binary | 41 | [9 empty] | BESS Container #13 Fault Flag |  | ess_13_faults |  | ess_13_faults | Yes
BESS Container #13 Alarm Flag | HybridOS | Status | 0.2 | binary | 42 | [9 empty] | BESS Container #13 Alarm Flag |  | ess_13_alarms |  | ess_13_alarms | Yes
BESS Container #14 Fault Flag | HybridOS | Status | 0.2 | binary | 43 | [9 empty] | BESS Container #14 Fault Flag |  | ess_14_faults |  | ess_14_faults | Yes
BESS Container #14 Alarm Flag | HybridOS | Status | 0.2 | binary | 44 | [9 empty] | BESS Container #14 Alarm Flag |  | ess_14_alarms |  | ess_14_alarms | Yes
BESS Container #15 Fault Flag | HybridOS | Status | 0.2 | binary | 45 | [9 empty] | BESS Container #15 Fault Flag |  | ess_15_faults |  | ess_15_faults | Yes
BESS Container #15 Alarm Flag | HybridOS | Status | 0.2 | binary | 46 | [9 empty] | BESS Container #15 Alarm Flag |  | ess_15_alarms |  | ess_15_alarms | Yes
BESS Container #16 Fault Flag | HybridOS | Status | 0.2 | binary | 47 | [9 empty] | BESS Container #16 Fault Flag |  | ess_16_faults |  | ess_16_faults | Yes
BESS Container #16 Alarm Flag | HybridOS | Status | 0.2 | binary | 48 | [9 empty] | BESS Container #16 Alarm Flag |  | ess_16_alarms |  | ess_16_alarms | Yes
BESS Container #17 Fault Flag | HybridOS | Status | 0.2 | binary | 49 | [9 empty] | BESS Container #17 Fault Flag |  | ess_17_faults |  | ess_17_faults | Yes
BESS Container #17 Alarm Flag | HybridOS | Status | 0.2 | binary | 50 | [9 empty] | BESS Container #17 Alarm Flag |  | ess_17_alarms |  | ess_17_alarms | Yes
BESS Container #18 Fault Flag | HybridOS | Status | 0.2 | binary | 51 | [9 empty] | BESS Container #18 Fault Flag |  | ess_18_faults |  | ess_18_faults | Yes
BESS Container #18 Alarm Flag | HybridOS | Status | 0.2 | binary | 52 | [9 empty] | BESS Container #18 Alarm Flag |  | ess_18_alarms |  | ess_18_alarms | Yes
BESS Container #19 Fault Flag | HybridOS | Status | 0.2 | binary | 53 | [9 empty] | BESS Container #19 Fault Flag |  | ess_19_faults |  | ess_19_faults | Yes
BESS Container #19 Alarm Flag | HybridOS | Status | 0.2 | binary | 54 | [9 empty] | BESS Container #19 Alarm Flag |  | ess_19_alarms |  | ess_19_alarms | Yes
BESS Container #20 Fault Flag | HybridOS | Status | 0.2 | binary | 55 | [9 empty] | BESS Container #20 Fault Flag |  | ess_20_faults |  | ess_20_faults | Yes
BESS Container #20 Alarm Flag | HybridOS | Status | 0.2 | binary | 56 | [9 empty] | BESS Container #20 Alarm Flag |  | ess_20_alarms |  | ess_20_alarms | Yes
BESS Container #21 Fault Flag | HybridOS | Status | 0.2 | binary | 57 | [9 empty] | BESS Container #21 Fault Flag |  | ess_21_faults |  | ess_21_faults | Yes
BESS Container #21 Alarm Flag | HybridOS | Status | 0.2 | binary | 58 | [9 empty] | BESS Container #21 Alarm Flag |  | ess_21_alarms |  | ess_21_alarms | Yes
BESS Container #22 Fault Flag | HybridOS | Status | 0.2 | binary | 59 | [9 empty] | BESS Container #22 Fault Flag |  | ess_22_faults |  | ess_22_faults | Yes
BESS Container #22 Alarm Flag | HybridOS | Status | 0.2 | binary | 60 | [9 empty] | BESS Container #22 Alarm Flag |  | ess_22_alarms |  | ess_22_alarms | Yes
BESS Container #23 Fault Flag | HybridOS | Status | 0.2 | binary | 61 | [9 empty] | BESS Container #23 Fault Flag |  | ess_23_faults |  | ess_23_faults | Yes
BESS Container #23 Alarm Flag | HybridOS | Status | 0.2 | binary | 62 | [9 empty] | BESS Container #23 Alarm Flag |  | ess_23_alarms |  | ess_23_alarms | Yes
BESS Container #24 Fault Flag | HybridOS | Status | 0.2 | binary | 63 | [9 empty] | BESS Container #24 Fault Flag |  | ess_24_faults |  | ess_24_faults | Yes
BESS Container #24 Alarm Flag | HybridOS | Status | 0.2 | binary | 64 | [9 empty] | BESS Container #24 Alarm Flag |  | ess_24_alarms |  | ess_24_alarms | Yes
BESS Container #25 Fault Flag | HybridOS | Status | 0.2 | binary | 65 | [9 empty] | BESS Container #25 Fault Flag |  | ess_25_faults |  | ess_25_faults | Yes
BESS Container #25 Alarm Flag | HybridOS | Status | 0.2 | binary | 66 | [9 empty] | BESS Container #25 Alarm Flag |  | ess_25_alarms |  | ess_25_alarms | Yes
BESS Container #26 Fault Flag | HybridOS | Status | 0.2 | binary | 67 | [9 empty] | BESS Container #26 Fault Flag |  | ess_26_faults |  | ess_26_faults | Yes
BESS Container #26 Alarm Flag | HybridOS | Status | 0.2 | binary | 68 | [9 empty] | BESS Container #26 Alarm Flag |  | ess_26_alarms |  | ess_26_alarms | Yes
BESS Container #27 Fault Flag | HybridOS | Status | 0.2 | binary | 69 | [9 empty] | BESS Container #27 Fault Flag |  | ess_27_faults |  | ess_27_faults | Yes
BESS Container #27 Alarm Flag | HybridOS | Status | 0.2 | binary | 70 | [9 empty] | BESS Container #27 Alarm Flag |  | ess_27_alarms |  | ess_27_alarms | Yes
BESS Container #28 Fault Flag | HybridOS | Status | 0.2 | binary | 71 | [9 empty] | BESS Container #28 Fault Flag |  | ess_28_faults |  | ess_28_faults | Yes
BESS Container #28 Alarm Flag | HybridOS | Status | 0.2 | binary | 72 | [9 empty] | BESS Container #28 Alarm Flag |  | ess_28_alarms |  | ess_28_alarms | Yes
BESS Container #29 Fault Flag | HybridOS | Status | 0.2 | binary | 73 | [9 empty] | BESS Container #29 Fault Flag |  | ess_29_faults |  | ess_29_faults | Yes
BESS Container #29 Alarm Flag | HybridOS | Status | 0.2 | binary | 74 | [9 empty] | BESS Container #29 Alarm Flag |  | ess_29_alarms |  | ess_29_alarms | Yes
BESS Container #30 Fault Flag | HybridOS | Status | 0.2 | binary | 75 | [9 empty] | BESS Container #30 Fault Flag |  | ess_30_faults |  | ess_30_faults | Yes
BESS Container #30 Alarm Flag | HybridOS | Status | 0.2 | binary | 76 | [9 empty] | BESS Container #30 Alarm Flag |  | ess_30_alarms |  | ess_30_alarms | Yes
BESS Container #31 Fault Flag | HybridOS | Status | 0.2 | binary | 77 | [9 empty] | BESS Container #31 Fault Flag |  | ess_31_faults |  | ess_31_faults | Yes
BESS Container #31 Alarm Flag | HybridOS | Status | 0.2 | binary | 78 | [9 empty] | BESS Container #31 Alarm Flag |  | ess_31_alarms |  | ess_31_alarms | Yes
BESS Container #32 Fault Flag | HybridOS | Status | 0.2 | binary | 79 | [9 empty] | BESS Container #32 Fault Flag |  | ess_32_faults |  | ess_32_faults | Yes
BESS Container #32 Alarm Flag | HybridOS | Status | 0.2 | binary | 80 | [9 empty] | BESS Container #32 Alarm Flag |  | ess_32_alarms |  | ess_32_alarms | Yes
BESS Container #33 Fault Flag | HybridOS | Status | 0.2 | binary | 81 | [9 empty] | BESS Container #33 Fault Flag |  | ess_33_faults |  | ess_33_faults | Yes
BESS Container #33 Alarm Flag | HybridOS | Status | 0.2 | binary | 82 | [9 empty] | BESS Container #33 Alarm Flag |  | ess_33_alarms |  | ess_33_alarms | Yes
Start Site Command | HybridOS | Command | 0.2 | CROB | 0 |  |  |  |  | uint32 |  |  |  |  | start site when true |  | remote_enable_flag |  | remote_enable_flag | Yes
Disable Site Command | HybridOS | Command | 0.2 | CROB | 1 |  |  |  |  | uint32 |  |  |  |  | disable site when true (blocks start site command) |  | remote_disable_flag |  | remote_disable_flag | Yes
Clear Faults Command | HybridOS | Command | 0.2 | CROB | 2 |  |  |  |  | uint32 |  |  |  |  | clear faults when true |  | remote_clear_faults |  | remote_clear_faults | Yes