## modified_10282022
Connection Name | FlexGen ESS Controller #
ip_address | 172.3.27.203
port | 10005
Device Name | FlexGen ESS Controller # | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | FALSE |  | 200 | life | 100 | 98 | 20 | flexgen_ess_#_hs | Yes
Heartbeat Write | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Start/Stop/Standby Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Start/Stop/Standby Command |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
On-grid Charging/Discharging Mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | On-grid Charging/Discharging Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Active Power Setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  |  | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Reactive Power Setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  |  | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active Power Rising Slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active Power Droop Slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive Power Rising Slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive Power Droop Slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
Clear Faults Command | clear_faults | Control |  | Holding Register |  |  |  | 1011 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1011 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
BMS DC Contactor Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1012 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Low Speed | [11 empty] | TRUE | life_signal | 200 |  | 1000 | 98 | 10 | flexgen_ess_#_ls | Yes
Heartbeat Read | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_ls
Chargeable Energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_ls
Dischargeable Energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_ls
Chargeable Power | chargeable_power | Status | 1 | Input Register | kW |  |  | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_ls
Dischargeable Power | dischargeable_power | Status | 1 | Input Register | kW |  |  | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_ls
System State | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_ls
Stop |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Stop
Run |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Run
Fault |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Fault
Standby |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Comms Status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_ls |  | 0 = online 1 = offline
PCS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | PCS Communication Status
BMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BMS Communication Status
EMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | EMMU Communication Status
FSS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | EMS Communication Status
External Management System Alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | External Management System (EMS) Alarms |  | /site/ess_ls
E-stop Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Disconnect Switch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Door Latch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Surge Arrester |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Fire Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fuse Monitoring |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Trouble Relay |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | yes |  | 6 | /site/ess_ls
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2009 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
BMS Max Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
BMS Min Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Grid Voltage 1 | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2011 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_ls
Grid Voltage 2 | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2012 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_ls
Grid Voltage 3 | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2013 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_ls
Grid Current 1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2014 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_ls
Grid Current 2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2015 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_ls
Grid Current 3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2016 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_ls
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2017 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_ls
Active Power | active_power | Status | 1 | Input Register | kW |  |  | 2018 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_ls
Reactive Power | reactive_power | Status | 1 | Input Register | kVAr |  |  | 2019 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_ls
Apparent Power | apparent_power | Status |  | Input Register | kVA |  | 10 | 2020 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2021 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_ls
DC Voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2022 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_ls
DC Current | current_dc | Status | 1 | Input Register | A |  | 10 | 2023 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_ls
DC Active Power | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2024 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_ls
PCS Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2025 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2026 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Status |  | /site/ess_ls | Refer to PCS Instructions
Power up |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Initialization |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Off |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Precharge |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Wait |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
On |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Discharge |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fault |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
LVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
OVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Night |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Night DC off |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVPL |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Pre-on |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Self-diagnosis |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Filter contactors |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Premagnetization |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Bank balancing |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
CV standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Number of PCS Modules in Service | pcs_modules_in_service | Status |  | Input Register |  |  |  | 2028 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of PCS Modules Online |  | /site/ess_ls
Derating Active | derating_active | Status |  | Input Register |  |  |  | 2029 | individual_bits | 0 | 65535 | [8 empty] | Yes | Derating Active Status |  | /site/ess_ls
derating_active | derating_active | Status |  | Input Register |  |  |  | 2029 | bit | [10 empty] | Yes |  |  | /site/ess_ls
Grid Voltage 1 Low Voltage | voltage_l1_l2_lv | Status | 1 | Input Register | V |  |  | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage Low Voltage |  | /site/ess_ls
Grid Voltage 2 Low Voltage | voltage_l2_l3_lv | Status | 1 | Input Register | V |  |  | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage Low Voltage |  | /site/ess_ls
Grid Voltage 3 Low Voltage | voltage_l3_l1_lv | Status | 1 | Input Register | V |  |  | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage Low Voltage |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS Maximum Cell Voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS Minimum Cell Voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS Average Cell Voltage | bms_average_cell_voltage | Status |  | Input Register | V |  | 10000 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Cell Voltage |  | /site/ess_ls
BMS Maximum Cell Temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2203 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS Minimum Cell Temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2204 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS Average Cell Temperature | bms_average_cell_temperature | Status |  | Input Register | °C |  | 100 | 2205 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS Power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2209 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2211 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2212 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC Contactors Closed Status | dc_contactors_closed | Status |  | Input Register |  |  |  | 2213 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2213 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | 0 = contactors closed, 1 = contactors open
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2284 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2286 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2400 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2401 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2402 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2403 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2404 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2405 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2406 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2407 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2408 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2409 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2410 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2411 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2412 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Aerosol State | Aerosol State | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Battery Rack No. 1 fault state 1 | sbmu_1_faults1 | Status |  | Input Register |  | 2 |  | 2414 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Battery Rack No. 1 fault state 2 | sbmu_1_faults2 | Status |  | Input Register |  | 2 |  | 2416 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 2 |  | /site/ess_ls
Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Battery Chiller Fan Fault (TMS Level 2 Fault) | Battery Chiller Fan Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Battery Chiller Pump Fault (TMS Level 2 Fault) | Battery Chiller Pump Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 17 |  | 2418 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_3 | Status |  |  |  | 17 |  | 2436 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_4 | Status |  |  |  | 17 |  | 2454 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_5 | Status |  |  |  | 17 |  | 2472 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_6 | Status |  |  |  | 17 |  | 2490 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_7 | Status |  |  |  | 17 |  | 2508 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_8 | Status |  |  |  | 17 |  | 2526 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_9 | Status |  |  |  | 17 |  | 2544 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400

## modified_10112022
Connection Name | FlexGen_ESS_Controller
ip_address | 0.0.0.0
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | FALSE |  | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Heartbeat Write | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Start/Stop/Standby Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Start/Stop/Standby Command |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
On-grid Charging/Discharging Mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | On-grid Charging/Discharging Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Active Power Setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  |  | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Reactive Power Setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  |  | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active Power Rising Slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active Power Droop Slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive Power Rising Slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive Power Droop Slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
Clear Faults Command | clear_faults | Control |  | Holding Register |  |  |  | 1011 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1011 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
BMS DC Contactor Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1012 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Low Speed | [11 empty] | TRUE | life_signal | 200 |  | 1000 | 98 | 10 | ess_ls | Yes
Heartbeat Read | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_ls
Chargeable Energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_ls
Dischargeable Energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_ls
Chargeable Power | chargeable_power | Status | 1 | Input Register | kW |  |  | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_ls
Dischargeable Power | dischargeable_power | Status | 1 | Input Register | kW |  |  | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_ls
System State | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_ls
Stop |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Stop
Run |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Run
Fault |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Fault
Standby |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Comms Status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_ls |  | 0 = online 1 = offline
PCS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | PCS Communication Status
BMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BMS Communication Status
EMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | EMMU Communication Status
FSS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | EMS Communication Status
External Management System Alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | External Management System (EMS) Alarms |  | /site/ess_ls
E-stop Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Disconnect Switch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Door Latch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Surge Arrester |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Fire Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fuse Monitoring |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Trouble Relay |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | yes |  | 6 | /site/ess_ls
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2009 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
BMS Max Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
BMS Min Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Grid Voltage 1 | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2011 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_ls
Grid Voltage 2 | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2012 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_ls
Grid Voltage 3 | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2013 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_ls
Grid Current 1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2014 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_ls
Grid Current 2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2015 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_ls
Grid Current 3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2016 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_ls
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2017 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_ls
Active Power | active_power | Status | 1 | Input Register | kW |  |  | 2018 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_ls
Reactive Power | reactive_power | Status | 1 | Input Register | kVAr |  |  | 2019 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_ls
Apparent Power | apparent_power | Status |  | Input Register | kVA |  | 10 | 2020 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2021 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_ls
DC Voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2022 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_ls
DC Current | current_dc | Status | 1 | Input Register | A |  | 10 | 2023 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_ls
DC Active Power | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2024 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_ls
PCS Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2025 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2026 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Status |  | /site/ess_ls | Refer to PCS Instructions
Power up |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Initialization |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Off |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Precharge |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Wait |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
On |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Discharge |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fault |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
LVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
OVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Night |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Night DC off |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVPL |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Pre-on |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Self-diagnosis |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Filter contactors |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Premagnetization |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Bank balancing |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
CV standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Number of PCS Modules in Service | pcs_modules_in_service | Status |  | Input Register |  |  |  | 2028 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of PCS Modules Online |  | /site/ess_ls
Derating Active | derating_active | Status |  | Input Register |  |  |  | 2029 | individual_bits | 0 | 65535 | [8 empty] | Yes | Derating Active Status |  | /site/ess_ls
derating_active | derating_active | Status |  | Input Register |  |  |  | 2029 | bit | [10 empty] | Yes |  |  | /site/ess_ls
Grid Voltage 1 Low Voltage | voltage_l1_l2_lv | Status | 1 | Input Register | V |  |  | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage Low Voltage |  | /site/ess_ls
Grid Voltage 2 Low Voltage | voltage_l2_l3_lv | Status | 1 | Input Register | V |  |  | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage Low Voltage |  | /site/ess_ls
Grid Voltage 3 Low Voltage | voltage_l3_l1_lv | Status | 1 | Input Register | V |  |  | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage Low Voltage |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS Maximum Cell Voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS Minimum Cell Voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS Average Cell Voltage | bms_average_cell_voltage | Status |  | Input Register | V |  | 10000 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Cell Voltage |  | /site/ess_ls
BMS Maximum Cell Temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2203 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS Minimum Cell Temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2204 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS Average Cell Temperature | bms_average_cell_temperature | Status |  | Input Register | °C |  | 100 | 2205 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS Power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2209 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2211 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2212 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC Contactors Closed Status | dc_contactors_closed | Status |  | Input Register |  |  |  | 2213 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2213 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | 0 = contactors closed, 1 = contactors open
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2284 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2286 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2400 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2401 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2402 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2403 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2404 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2405 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2406 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2407 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2408 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2409 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2410 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2411 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2412 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Aerosol State | Aerosol State | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Battery Rack No. 1 fault state 1 | sbmu_1_faults1 | Status |  | Input Register |  | 2 |  | 2414 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Battery Rack No. 1 fault state 2 | sbmu_1_faults2 | Status |  | Input Register |  | 2 |  | 2416 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 2 |  | /site/ess_ls
Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Battery Chiller Fan Fault (TMS Level 2 Fault) | Battery Chiller Fan Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Battery Chiller Pump Fault (TMS Level 2 Fault) | Battery Chiller Pump Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 17 |  | 2418 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_3 | Status |  |  |  | 17 |  | 2436 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_4 | Status |  |  |  | 17 |  | 2454 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_5 | Status |  |  |  | 17 |  | 2472 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_6 | Status |  |  |  | 17 |  | 2490 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_7 | Status |  |  |  | 17 |  | 2508 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_8 | Status |  |  |  | 17 |  | 2526 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_9 | Status |  |  |  | 17 |  | 2544 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400

## modified_09072021
Connection Name | FlexGen_ESS_Controller
ip_address | 192.168.114.11
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Heartbeat Write | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Start/Stop/Standby Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Start/Stop/Standby Command |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
On-grid Charging/Discharging Mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | On-grid Charging/Discharging Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Active Power Setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  |  | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Reactive Power Setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  |  | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active Power Rising Slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active Power Droop Slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive Power Rising Slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive Power Droop Slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
Clear Faults Command | clear_faults | Control |  | Holding Register |  |  |  | 1011 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1011 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
BMS DC Contactor Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1012 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Low Speed | [11 empty] | TRUE | life_signal | 200 | life | 1000 | 98 | 10 | ess_ls | Yes
Heartbeat Read | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_ls
Chargeable Energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_ls
Dischargeable Energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_ls
Chargeable Power | chargeable_power | Status | 1 | Input Register | kW |  |  | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_ls
Dischargeable Power | dischargeable_power | Status | 1 | Input Register | kW |  |  | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_ls
System State | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_ls
Stop |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Stop
Run |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Run
Fault |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Fault
Standby |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Comms Status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_ls |  | 0 = online 1 = offline
PCS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | PCS Communication Status
BMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BMS Communication Status
EMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | EMMU Communication Status
FSS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | EMS Communication Status
External Management System Alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | External Management System (EMS) Alarms |  | /site/ess_ls
E-stop Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Disconnect Switch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Door Latch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Surge Arrester |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Fire Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fuse Monitoring |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2009 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
BMS Max Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
BMS Min Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Grid Voltage 1 | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2011 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_ls
Grid Voltage 2 | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2012 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_ls
Grid Voltage 3 | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2013 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_ls
Grid Current 1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2014 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_ls
Grid Current 2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2015 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_ls
Grid Current 3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2016 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_ls
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2017 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_ls
Active Power | active_power | Status | 1 | Input Register | kW |  |  | 2018 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_ls
Reactive Power | reactive_power | Status | 1 | Input Register | kVAr |  |  | 2019 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_ls
Apparent Power | apparent_power | Status |  | Input Register | kVA |  | 10 | 2020 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2021 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_ls
DC Voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2022 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_ls
DC Current | current_dc | Status | 1 | Input Register | A |  | 10 | 2023 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_ls
DC Active Power | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2024 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_ls
PCS Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2025 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2026 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Status |  | /site/ess_ls | Refer to PCS Instructions
Power up |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Initialization |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Off |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Precharge |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Wait |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
On |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Discharge |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fault |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
LVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
OVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Night |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Night DC off |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVPL |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Pre-on |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Self-diagnosis |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Filter contactors |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Premagnetization |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Bank balancing |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
CV standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Number of PCS Modules in Service | pcs_modules_in_service | Status |  | Input Register |  |  |  | 2028 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of PCS Modules Online |  | /site/ess_ls
Derating Active | derating_active | Status |  | Input Register |  |  |  | 2029 | individual_bits | 0 | 65535 | [8 empty] | Yes | Derating Active Status |  | /site/ess_ls
derating_active | derating_active | Status |  | Input Register |  |  |  | 2029 | bit | [10 empty] | Yes |  |  | /site/ess_ls
Grid Voltage 1 Low Voltage | voltage_l1_l2_lv | Status | 1 | Input Register | V |  |  | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage Low Voltage |  | /site/ess_ls
Grid Voltage 2 Low Voltage | voltage_l2_l3_lv | Status | 1 | Input Register | V |  |  | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage Low Voltage |  | /site/ess_ls
Grid Voltage 3 Low Voltage | voltage_l3_l1_lv | Status | 1 | Input Register | V |  |  | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage Low Voltage |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS Maximum Cell Voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS Minimum Cell Voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS Average Cell Voltage | bms_average_cell_voltage | Status |  | Input Register | V |  | 10000 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Cell Voltage |  | /site/ess_ls
BMS Maximum Cell Temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2203 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS Minimum Cell Temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2204 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS Average Cell Temperature | bms_average_cell_temperature | Status |  | Input Register | °C |  | 100 | 2205 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS Power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2209 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2211 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2212 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC Contactors Closed Status | dc_contactors_closed | Status |  | Input Register |  |  |  | 2213 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2213 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | 0 = contactors closed, 1 = contactors open
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2284 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2286 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2400 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2401 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2402 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2403 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2404 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2405 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2406 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2407 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2408 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2409 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2410 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2411 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2412 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Aerosol State | Aerosol State | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Battery Rack No. 1 fault state 1 | sbmu_1_faults1 | Status |  | Input Register |  | 2 |  | 2414 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Battery Rack No. 1 fault state 2 | sbmu_1_faults2 | Status |  | Input Register |  | 2 |  | 2416 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 2 |  | /site/ess_ls
Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Battery Chiller Fan Fault (TMS Level 2 Fault) | Battery Chiller Fan Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Battery Chiller Pump Fault (TMS Level 2 Fault) | Battery Chiller Pump Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 17 |  | 2418 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_3 | Status |  |  |  | 17 |  | 2436 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_4 | Status |  |  |  | 17 |  | 2454 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_5 | Status |  |  |  | 17 |  | 2472 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_6 | Status |  |  |  | 17 |  | 2490 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_7 | Status |  |  |  | 17 |  | 2508 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_8 | Status |  |  |  | 17 |  | 2526 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_9 | Status |  |  |  | 17 |  | 2544 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400

## modified_09012021
Connection Name | FlexGen_ESS_Controller
ip_address | 192.168.114.11
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Heartbeat Write | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Start/Stop/Standby Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Start/Stop/Standby Command |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
On-grid Charging/Discharging Mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | On-grid Charging/Discharging Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Active Power Setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  |  | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Reactive Power Setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  |  | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active Power Rising Slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active Power Droop Slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive Power Rising Slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive Power Droop Slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
Clear Faults Command | clear_faults | Control |  | Holding Register |  |  |  | 1011 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1011 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
BMS DC Contactor Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1012 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Low Speed | [11 empty] | TRUE | life_signal | 200 | life | 1000 | 98 | 10 | ess_ls | Yes
Heartbeat Read | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_ls
Chargeable Energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_ls
Dischargeable Energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_ls
Chargeable Power | chargeable_power | Status | 1 | Input Register | kW |  |  | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_ls
Dischargeable Power | dischargeable_power | Status | 1 | Input Register | kW |  |  | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_ls
System State | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_ls
Stop |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Stop
Run |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Run
Fault |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Fault
Standby |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Comms Status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_ls |  | 0 = online 1 = offline
PCS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | PCS Communication Status
BMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BMS Communication Status
EMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | EMMU Communication Status
FSS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | EMS Communication Status
External Management System Alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | External Management System (EMS) Alarms |  | /site/ess_ls
E-stop Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Disconnect Switch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Door Latch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Surge Arrester |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Fire Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fuse Monitoring |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2009 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
BMS Max Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
BMS Min Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Grid Voltage 1 | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2011 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_ls
Grid Voltage 2 | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2012 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_ls
Grid Voltage 3 | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2013 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_ls
Grid Current 1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2014 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_ls
Grid Current 2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2015 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_ls
Grid Current 3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2016 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_ls
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2017 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_ls
Active Power | active_power | Status | 1 | Input Register | kW |  |  | 2018 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_ls
Reactive Power | reactive_power | Status | 1 | Input Register | kVAr |  |  | 2019 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_ls
Apparent Power | apparent_power | Status |  | Input Register | kVA |  | 10 | 2020 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2021 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_ls
DC Voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2022 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_ls
DC Current | current_dc | Status | 1 | Input Register | A |  | 10 | 2023 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_ls
DC Active Power | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2024 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_ls
PCS Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2025 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2026 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Status |  | /site/ess_ls | Refer to PCS Instructions
Power up |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Initialization |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Off |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Precharge |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Wait |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
On |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Discharge |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fault |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
LVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
OVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Night |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Night DC off |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVPL |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Pre-on |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Self-diagnosis |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Filter contactors |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Premagnetization |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Bank balancing |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
CV standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Number of PCS Modules in Service | pcs_modules_in_service | Status |  | Input Register |  |  |  | 2028 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of PCS Modules Online |  | /site/ess_ls
Derating Active | derating_active | Status |  | Input Register |  |  |  | 2029 | individual_bits | 0 | 65535 | [8 empty] | Yes | Derating Active Status |  | /site/ess_ls
derating_active | derating_active | Status |  | Input Register |  |  |  | 2029 | bit | [10 empty] | Yes |  |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS Maximum Cell Voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS Minimum Cell Voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS Average Cell Voltage | bms_average_cell_voltage | Status |  | Input Register | V |  | 10000 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Cell Voltage |  | /site/ess_ls
BMS Maximum Cell Temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2203 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS Minimum Cell Temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2204 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS Average Cell Temperature | bms_average_cell_temperature | Status |  | Input Register | °C |  | 100 | 2205 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS Power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2209 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2211 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2212 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC Contactors Closed Status | dc_contactors_closed | Status |  | Input Register |  |  |  | 2213 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2213 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | 0 = contactors closed, 1 = contactors open
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2284 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2286 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2400 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2401 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2402 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2403 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2404 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2405 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2406 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2407 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2408 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2409 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2410 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2411 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2412 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Aerosol State | Aerosol State | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Inlet Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Environment Humidity Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Battery Chiller Outer Water Pressure Sensor Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Battery Chiller Water Pressure Difference Alarm (TMS Level 3 Alarm) | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Battery Rack No. 1 fault state 1 | sbmu_1_faults1 | Status |  | Input Register |  | 2 |  | 2414 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Battery Rack No. 1 fault state 2 | sbmu_1_faults2 | Status |  | Input Register |  | 2 |  | 2416 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 2 |  | /site/ess_ls
Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Battery Chiller CAN Communication Loss (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Battery Chiller HV Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Battery Chiller K2 Relay Fault (TMS Level 1 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC A Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Battery Chiller AC/DC B Inverter Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Battery Chiller Fan Fault (TMS Level 2 Fault) | Battery Chiller Fan Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Battery Chiller HV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Overvoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Battery Chiller HV Undervoltage Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Battery Chiller LV Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Battery Chiller LV Sensor Too High (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Battery Chiller LV Sensor Too Low (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Outlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Battery Chiller Inlet Temperature Sensor Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Battery Chiller Pump Fault (TMS Level 2 Fault) | Battery Chiller Pump Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Battery Chiller AC Communication Loss Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Battery Chiller AC Compression Control Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Battery Chiller PTC - Heater Overtemperature Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Battery Chiller HV Pressure Switch Fault (TMS Level 2 Fault) | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 17 |  | 2418 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_3 | Status |  |  |  | 17 |  | 2436 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_4 | Status |  |  |  | 17 |  | 2454 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_5 | Status |  |  |  | 17 |  | 2472 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_6 | Status |  |  |  | 17 |  | 2490 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_7 | Status |  |  |  | 17 |  | 2508 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_8 | Status |  |  |  | 17 |  | 2526 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_9 | Status |  |  |  | 17 |  | 2544 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400

## modified_08122021
Connection Name | FlexGen_ESS_Controller
ip_address | 192.168.114.11
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Heartbeat Write | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Start/Stop/Standby Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Start/Stop/Standby Command |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
On-grid Charging/Discharging Mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | On-grid Charging/Discharging Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Active Power Setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Reactive Power Setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active Power Rising Slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active Power Droop Slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive Power Rising Slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive Power Droop Slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
Clear Faults Command | clear_faults | Control |  | Holding Register |  |  |  | 1011 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1011 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
BMS DC Contactor Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1012 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Low Speed | [11 empty] | TRUE | life_signal | 200 | life | 1000 | 98 | 10 | ess_ls | Yes
Heartbeat Read | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_ls
Chargeable Energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_ls
Dischargeable Energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_ls
Chargeable Power | chargeable_power | Status | 1 | Input Register | kW |  |  | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_ls
Dischargeable Power | dischargeable_power | Status | 1 | Input Register | kW |  |  | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_ls
System State | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_ls
Stop |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Stop
Run |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Run
Fault |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Fault
Standby |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Comms Status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_ls |  | 0 = online 1 = offline
PCS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | PCS Communication Status
BMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BMS Communication Status
EMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | EMMU Communication Status
FSS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | EMS Communication Status
External Management System Alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | External Management System (EMS) Alarms |  | /site/ess_ls
E-stop Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Disconnect Switch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Door Latch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Surge Arrester |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Fire Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fuse Monitoring |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2009 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
BMS Max Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
BMS Min Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Grid Voltage 1 | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2011 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_ls
Grid Voltage 2 | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2012 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_ls
Grid Voltage 3 | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2013 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_ls
Grid Current 1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2014 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_ls
Grid Current 2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2015 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_ls
Grid Current 3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2016 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_ls
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2017 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_ls
Active Power | active_power | Status | 1 | Input Register | kW |  |  | 2018 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_ls
Reactive Power | reactive_power | Status | 1 | Input Register | kVAr |  |  | 2019 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_ls
Apparent Power | apparent_power | Status |  | Input Register | kVA |  | 10 | 2020 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2021 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_ls
DC Voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2022 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_ls
DC Current | current_dc | Status | 1 | Input Register | A |  | 10 | 2023 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_ls
DC Active Power | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2024 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_ls
PCS Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2025 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2026 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Status |  | /site/ess_ls | Refer to PCS Instructions
Power up |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Initialization |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Off |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Precharge |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Wait |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
On |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Discharge |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fault |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
LVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
OVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Night |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Night DC off |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVPL |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Pre-on |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Self-diagnosis |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Filter contactors |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Premagnetization |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Bank balancing |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
CV standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Number of PCS Modules in Service | pcs_modules_in_service | Status |  | Input Register |  |  |  | 2028 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of PCS Modules Online |  | /site/ess_ls
Derating Active | derating_active | Status |  | Input Register |  |  |  | 2029 | individual_bits | 0 | 65535 | [8 empty] | Yes | Derating Active Status |  | /site/ess_ls
derating_active | derating_active | Status |  | Input Register |  |  |  | 2029 | bit | [10 empty] | Yes |  |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS Maximum Cell Voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS Minimum Cell Voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS Average Cell Voltage | bms_average_cell_voltage | Status |  | Input Register | V |  | 10000 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Cell Voltage |  | /site/ess_ls
BMS Maximum Cell Temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2203 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS Minimum Cell Temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2204 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS Average Cell Temperature | bms_average_cell_temperature | Status |  | Input Register | °C |  | 100 | 2205 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS Power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2209 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2211 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2212 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC Contactors Closed Status | dc_contactors_closed | Status |  | Input Register |  |  |  | 2213 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2213 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | 0 = contactors closed, 1 = contactors open
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2284 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2286 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2400 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2401 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2402 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2403 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2404 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2405 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2406 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2407 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2408 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2409 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2410 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2411 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2412 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
TMS Fault Level 3 | TMS Warning Level 3 | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Aerosol State | Aerosol State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Battery Rack No. 1 fault state 1 | sbmu_1_faults1 | Status |  | Input Register |  | 2 |  | 2414 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 1 |  | /site/ess_ls
TMS Fault Level 1 | TMS Fault Level 1 | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
TMS Fault Level 2 | TMS Fault Level 2 | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Battery Rack No. 1 fault state 2 | sbmu_1_faults2 | Status |  | Input Register |  | 2 |  | 2416 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 2 |  | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 17 |  | 2418 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_3 | Status |  |  |  | 17 |  | 2436 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_4 | Status |  |  |  | 17 |  | 2454 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_5 | Status |  |  |  | 17 |  | 2472 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_6 | Status |  |  |  | 17 |  | 2490 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_7 | Status |  |  |  | 17 |  | 2508 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_8 | Status |  |  |  | 17 |  | 2526 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_9 | Status |  |  |  | 17 |  | 2544 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400

## modified_07132021
Connection Name | FlexGen_ESS_Controller
ip_address | 192.168.114.11
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Heartbeat Write | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Start/Stop/Standby Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Start/Stop/Standby Command |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
On-grid Charging/Discharging Mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | On-grid Charging/Discharging Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Active Power Setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Reactive Power Setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active Power Rising Slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active Power Droop Slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive Power Rising Slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive Power Droop Slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
Clear Faults Command | clear_faults | Control |  | Holding Register |  |  |  | 1011 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1011 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
BMS DC Contactor Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1012 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Low Speed | [11 empty] | TRUE | life_signal | 200 | life | 1000 | 98 | 10 | ess_ls | Yes
Heartbeat Read | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_ls
Chargeable Energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_ls
Dischargeable Energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_ls
Chargeable Power | chargeable_power | Status | 1 | Input Register | kW |  |  | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_ls
Dischargeable Power | dischargeable_power | Status | 1 | Input Register | kW |  |  | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_ls
System State | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_ls
Stop |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Stop
Run |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Run
Fault |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Fault
Standby |  | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Comms Status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_ls |  | 0 = online 1 = offline
PCS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | PCS Communication Status
BMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BMS Communication Status
EMS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | EMMU Communication Status
FSS Communication Offline |  | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | EMS Communication Status
External Management System Alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | External Management System (EMS) Alarms |  | /site/ess_ls
E-stop Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Disconnect Switch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Door Latch |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Surge Arrester |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Fire Alarm |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fuse Monitoring |  | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2009 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
BMS Max Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
BMS Min Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2009 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Grid Voltage 1 | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2011 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_ls
Grid Voltage 2 | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2012 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_ls
Grid Voltage 3 | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2013 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_ls
Grid Current 1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2014 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_ls
Grid Current 2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2015 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_ls
Grid Current 3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2016 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_ls
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2017 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_ls
Active Power | active_power | Status | 1 | Input Register | kW |  |  | 2018 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_ls
Reactive Power | reactive_power | Status | 1 | Input Register | kVAr |  |  | 2019 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_ls
Apparent Power | apparent_power | Status |  | Input Register | kVA |  | 10 | 2020 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2021 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_ls
DC Voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2022 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_ls
DC Current | current_dc | Status | 1 | Input Register | A |  | 10 | 2023 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_ls
DC Active Power | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2024 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_ls
PCS Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2025 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode |  | Status | 1 | Input Register |  |  |  | 2025 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2026 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Status |  | /site/ess_ls | Refer to PCS Instructions
Power up |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Initialization |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Off |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Precharge |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Wait |  | Status | 1 | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
On |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Discharge |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fault |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
LVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
OVRT |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Night |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Night DC off |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVPL |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Pre-on |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Self-diagnosis |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Filter contactors |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Premagnetization |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Bank balancing |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
CV standby |  | Status |  | Input Register |  |  |  | 2026 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Number of PCS Modules in Service | pcs_modules_in_service | Status |  | Input Register |  |  |  | 2028 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of PCS Modules Online |  | /site/ess_ls
Derating Active | derating_active | Status |  | Input Register |  |  |  | 2029 | individual_bits | 0 | 65535 | [8 empty] | Yes | Derating Active Status |  | /site/ess_ls
derating_active | derating_active | Status |  | Input Register |  |  |  | 2029 | bit | [10 empty] | Yes |  |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS Maximum Cell Voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS Minimum Cell Voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2201 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS Average Cell Voltage | bms_average_cell_voltage | Status |  | Input Register | V |  | 10000 | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Average Cell Voltage |  | /site/ess_ls
BMS Maximum Cell Temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2203 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS Minimum Cell Temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2204 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS Average Cell Temperature | bms_average_cell_temperature | Status |  | Input Register | °C |  | 100 | 2205 | int16 | -32768 | 32767 | [8 empty] | Yes | Average Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS Power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2209 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2211 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2211 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2212 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC Contactors Closed Status | dc_contactors_closed | Status |  | Input Register |  |  |  | 2213 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2213 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | 0 = contactors closed, 1 = contactors open
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2214 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2284 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2284 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2286 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2286 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2400 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2401 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2402 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2403 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2404 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2405 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2406 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2407 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2408 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2409 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2410 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2411 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2412 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2412 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
TMS Fault Level 3 | TMS Fault Level 3 | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Aerosol State Fault | Aerosol State Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Battery Rack No. 1 fault state 1 | sbmu_1_faults1 | Status |  | Input Register |  | 2 |  | 2414 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 1 |  | /site/ess_ls
TMS Fault Level 1 | TMS Fault Level 1 | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
TMS Fault Level 2 | TMS Fault Level 2 | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2416 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2414 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Battery Rack No. 1 fault state 2 | sbmu_1_faults2 | Status |  | Input Register |  | 2 |  | 2416 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status 2 |  | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 17 |  | 2418 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_3 | Status |  |  |  | 17 |  | 2436 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_4 | Status |  |  |  | 17 |  | 2454 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_5 | Status |  |  |  | 17 |  | 2472 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_6 | Status |  |  |  | 17 |  | 2490 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_7 | Status |  |  |  | 17 |  | 2508 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_8 | Status |  |  |  | 17 |  | 2526 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400
sbmu_1 | sbmu_9 | Status |  |  |  | 17 |  | 2544 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2400

## modified_06232021
Connection Name | FlexGen_ESS_Controller
ip_address | 192.168.114.11
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Life | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Control_Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Word 1 |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
Run_mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | No | Run Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | No | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Power_Set_AC | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Active_Set_AC | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active_power_rising_slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active_power_droop_slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive_power_rising_slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive_power_droop_slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
BMS_DC_Contactor_Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1011 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Clear_Faults_Command | clear_faults | Control |  | Holding Register |  |  |  | 1012 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1012 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
life_signal | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Q_charge | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_hs
Q_discharge | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_hs
W_charge | chargeable_power | Status | 1 | Input Register | kW |  | 10 | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_hs
W_discharge | dischargeable_power | Status | 1 | Input Register | kW |  | 10 | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_hs
System_state | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_hs
Stop | Stop | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Stop
Run | Run | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | Run
Fault | Fault | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | Fault
Standby | Standby | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | Standby
Com_status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_hs |  | 0 = online 1 = offline
PCS Communication Offline | PCS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | PCS Communication Status
BMS Communication Offline | BMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | BMS Communication Status
EMMU Communication Offline | EMMU Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | EMMU Communication Status
EMS Communication Offline | EMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | EMS Communication Status
Environmental management system alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | Environmental Management System (EMS) Alarms |  | /site/ess_hs
E-stop Alarm | E-stop Alarm | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs
Disconnect Switch | Disconnect Switch | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs
Door Latch | Door Latch | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs
Surge Arrester | Surge Arrester | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs
Fire Alarm | Fire Alarm | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_hs
Fuse Monitoring | Fuse Monitoring | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_hs
Uinab_RMS | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_hs
Uinbc_RMS | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_hs
Uinca_RMS | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_hs
Iina_RMS | current_l1 | Status | 1 | Input Register | A |  | 10 | 2033 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_hs
Iinb_RMS | current_l2 | Status | 1 | Input Register | A |  | 10 | 2034 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_hs
Iinc_RMS | current_l3 | Status | 1 | Input Register | A |  | 10 | 2035 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_hs
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2036 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_hs
Active Power | active_power | Status | 1 | Input Register | kW |  | 10 | 2037 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_hs
Reactive Power | reactive_power | Status | 1 | Input Register | kVar |  | 10 | 2038 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_hs
Overall apparent Power | apparent_power | Status |  | Input Register |  |  | 10 | 2039 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_hs
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2040 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_hs
Ubtra_Ever | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2041 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_hs
Ibtra_Ever | current_dc | Status | 1 | Input Register | A |  | 10 | 2042 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_hs
Pbtra | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2043 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_hs
Low Speed |  | Status | [9 empty] | TRUE | life_signal | 200 | life | 1000 | 58 | 10 | ess_ls | yes
PCS_Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2044 | bitfield | 0 | 65535 | [8 empty] | No | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) | On-grid constant current (CC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 0 | /site/ess_ls
On-grid constant voltage (CV) | On-grid constant voltage (CV) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 1 | /site/ess_ls
On-grid constant power (AC) | On-grid constant power (AC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 2 | /site/ess_ls
On-grid constant power (DC) | On-grid constant power (DC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 3 | /site/ess_ls
On-grid Mode | On-grid Mode | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 9 | /site/ess_ls
Off-grid Mode | Off-grid Mode | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 10 | /site/ess_ls
PCS_State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2045 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Overall Work State |  | /site/ess_ls | Refer to PCS Instructions
Off | Off | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Starting | Starting | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Ready | Ready | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Running | Running | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Shutdown | Shutdown | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault | Fault | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2053 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2054 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC_Contactors_Closed_Command | dc_contactors_closed | Status |  | Input Register |  |  |  | 2055 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2055 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | 0 = contactors closed, 1 = contactors open
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2066 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2068 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Unit1_Uinab_RMS | pcs1_voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2070 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 AB Line Voltage |  | /site/ess_ls
Unit1_Uinbc_RMS | pcs1_voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2071 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 BC Line Voltage |  | /site/ess_ls
Unit1_Uinca_RMS | pcs1_voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2072 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 CA Line Voltage |  | /site/ess_ls
Unit1_Iina_RMS | pcs1_current_l1 | Status | 1 | Input Register | A |  | 10 | 2073 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 A Line Current |  | /site/ess_ls
Unit1_Iinb_RMS | pcs1_current_l2 | Status | 1 | Input Register | A |  | 10 | 2074 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 B Line Current |  | /site/ess_ls
Unit1_Iinc_RMS | pcs1_current_l3 | Status | 1 | Input Register | A |  | 10 | 2075 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 C Line Current |  | /site/ess_ls
Unit1_P | pcs1_active_power | Status | 1 | Input Register | kW | 2 | 10 | 2076-2077 | int32 | -2147483648 | 2147483647 | [8 empty] | No | PCS 1 AC Active Power |  | /site/ess_ls
Unit1_Q | pcs1_reactive_power | Status | 1 | Input Register | kVar | 2 | 10 | 2078-2079 | int32 | -2147483648 | 2147483647 | [8 empty] | No | PCS 1 AC Reactive Power |  | /site/ess_ls
Unit1_Ubtra_Ever | pcs1_voltage_dc | Status | 1 | Input Register | V |  | 10 | 2080 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 DC Voltage |  | /site/ess_ls
Unit1_Ibtra_Ever | pcs1_current_dc | Status | 1 | Input Register | A |  | 10 | 2081 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 DC Current |  | /site/ess_ls
Unit1_Pbtra | pcs1_active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2082 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 DC Active Power |  | /site/ess_ls
Maximum charging power limit Unit1 | maximum_charging_power_limit_pcs1 | Status |  | Input Register | kW |  | 10 | 2083 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 Maximum Charging Power Limit |  | /site/ess_ls
Maximum discharging power limit Unit1 | maximum_discharging_power_limit_pcs1 | Status |  | Input Register | kW |  | 10 | 2084 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 Maximum Discharging Power Limit |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
PCS Module Alarms 1 | module_1_alarms1 | Status |  | Input Register |  | 2 |  | 2105 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 1 |  | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation |  |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2105 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Alarms 2 | module_1_alarms2 | Status |  | Input Register |  | 2 |  | 2107 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Alarm Status 2 |  | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2107 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS Module Faults 1 | module_1_faults1 | Status |  | Input Register |  | 2 |  | 2109 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 1 |  | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2109 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
PCS Module Faults 2 | module_1_faults2 | Status |  | Input Register |  | 2 |  | 2111 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS Module 1 Fault Status 2 |  | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2111 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
module_1 | module_2 | Status |  | Input Register |  | 7 |  | 2113 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_3 | Status |  | Input Register |  | 7 |  | 2121 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_4 | Status |  | Input Register |  | 7 |  | 2129 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_5 | Status |  | Input Register |  | 7 |  | 2137 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
module_1 | module_6 | Status |  | Input Register |  | 7 |  | 2145 | repeat | [10 empty] | Yes |  |  | /site/ess_ls |  |  | 2105
BMS maximum cell voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2186 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS minimum cell voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2187 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS maximum cell temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2188 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS minimum cell temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2189 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2190 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2191 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2192 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2193 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2194 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2195 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2195 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2197 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2197 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2199 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2200 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2201 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2202 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2203 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2204 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2205 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2206 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2207 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2208 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2209 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2211 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2212 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
TMS Fault Level 1 | TMS Fault Level 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
TMS Fault Level 2 | TMS Fault Level 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Fault Level 3 | TMS Fault Level 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Battery Rack No. 1 fault state | sbmu_1_faults | Status |  | Input Register |  | 2 |  | 2214 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status |  | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Aerosol State Fault | Aerosol State Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 15 |  | 2216 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2216 - 2231 for sbmu_2 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_3 | Status |  |  |  | 15 |  | 2232 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2232 - 2247 for sbmu_3 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_4 | Status |  |  |  | 15 |  | 2248 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2248 - 2263 for sbmu_4 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_5 | Status |  |  |  | 15 |  | 2264 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2264 - 2279 for sbmu_5 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_6 | Status |  |  |  | 15 |  | 2280 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2280 - 2295 for sbmu_6 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_7 | Status |  |  |  | 15 |  | 2296 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2296 - 2311 for sbmu_7 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_8 | Status |  |  |  | 15 |  | 2312 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2312 - 2327 for sbmu_8 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_9 | Status |  |  |  | 15 |  | 2328 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2328 - 2343 for sbmu_9 |  | /site/ess_ls |  |  | 2200

## modified_06182021
Connection Name | FlexGen_ESS_Controller
ip_address | 192.168.114.11
port | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [11 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Life | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Control_Command | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Word 1 |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
Run_mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | No | Run Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | No | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Power_Set_AC | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Active_Set_AC | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active_power_rising_slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Rising Slope |  | /site/ess_hs
Active_power_droop_slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | No | Active Power Droop Slope |  | /site/ess_hs
Reactive_power_rising_slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Rising Slope |  | /site/ess_hs
Reactive_power_droop_slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | No | Reactive Power Droop Slope |  | /site/ess_hs
BMS_DC_Contactor_Control | bms_dc_contactors | Control |  | Holding Register |  |  |  | 1011 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Clear_Faults_Command | clear_faults | Control |  | Holding Register |  |  |  | 1012 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | Control |  | Holding Register |  |  |  | 1012 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
life_signal | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Q_charge | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_hs
Q_discharge | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_hs
W_charge | chargeable_power | Status | 1 | Input Register | kW |  | 10 | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_hs
W_discharge | dischargeable_power | Status | 1 | Input Register | kW |  | 10 | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_hs
System_state | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_hs
Stop | Stop | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Stop
Run | Run | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | Run
Fault | Fault | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | Fault
Standby | Standby | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | Standby
Com_status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_hs |  | 0 = online 1 = offline
PCS Communication Offline | PCS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | PCS Communication Status
BMS Communication Offline | BMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | BMS Communication Status
EMMU Communication Offline | EMMU Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | EMMU Communication Status
EMS Communication Offline | EMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | EMS Communication Status
Environmental management system alarms | ems_alarms | Status |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | Environmental Management System (EMS) Alarms |  | /site/ess_hs
E-stop Alarm | E-stop Alarm | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs
Disconnect Switch | Disconnect Switch | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs
Door Latch | Door Latch | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs
Surge Arrester | Surge Arrester | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs
Fire Alarm | Fire Alarm | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_hs
Fuse Monitoring | Fuse Monitoring | Status |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_hs
Uinab_RMS | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_hs
Uinbc_RMS | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_hs
Uinca_RMS | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_hs
Iina_RMS | current_l1 | Status | 1 | Input Register | A |  | 10 | 2033 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_hs
Iinb_RMS | current_l2 | Status | 1 | Input Register | A |  | 10 | 2034 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_hs
Iinc_RMS | current_l3 | Status | 1 | Input Register | A |  | 10 | 2035 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_hs
Frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2036 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_hs
Active Power | active_power | Status | 1 | Input Register | kW |  | 10 | 2037 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_hs
Reactive Power | reactive_power | Status | 1 | Input Register | kVar |  | 10 | 2038 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_hs
Overall apparent Power | apparent_power | Status |  | Input Register |  |  | 10 | 2039 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_hs
Power Factor | pf | Status | 1 | Input Register |  |  | 1000 | 2040 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_hs
Ubtra_Ever | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2041 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_hs
Ibtra_Ever | current_dc | Status | 1 | Input Register | A |  | 10 | 2042 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_hs
Pbtra | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2043 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_hs
Low Speed |  | Status | [9 empty] | TRUE | life_signal | 200 | life | 1000 | 58 | 10 | ess_ls | yes
PCS_Mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2044 | bitfield | 0 | 65535 | [8 empty] | No | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) | On-grid constant current (CC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 0 | /site/ess_ls
On-grid constant voltage (CV) | On-grid constant voltage (CV) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 1 | /site/ess_ls
On-grid constant power (AC) | On-grid constant power (AC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 2 | /site/ess_ls
On-grid constant power (DC) | On-grid constant power (DC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 3 | /site/ess_ls
On-grid Mode | On-grid Mode | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 9 | /site/ess_ls
Off-grid Mode | Off-grid Mode | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | No |  | 10 | /site/ess_ls
PCS_State1 | pcs_state | Status | 1 | Input Register |  | 2 |  | 2045 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Overall Work State |  | /site/ess_ls | Refer to PCS Instructions
Off | Off | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Starting | Starting | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Ready | Ready | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Running | Running | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Shutdown | Shutdown | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault | Fault | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
BMS Power On | bms_poweron | Status |  | Input Register |  |  |  | 2053 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Status |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | Status |  | Input Register |  |  |  | 2054 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Status |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC_Contactors_Closed_Command | dc_contactors_closed | Status |  | Input Register |  |  |  | 2055 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | Status | dc_contactors_closed | Input Register |  |  |  | 2055 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | 0 = contactors closed, 1 = contactors open
ESS Faults | ess_faults | Status |  | Input Register |  |  |  | 2066 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Faults |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2066 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
ESS Alarms | ess_alarms | Status |  | Input Register |  |  |  | 2068 | bitfield | 0 | 65535 | [8 empty] | Yes | ESS Alarms |  | /site/ess_ls
BMS Max Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
BMS Min Cell Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
BMS Max Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
BMS Min Cell Temperature Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Current Max Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
BMS Current Min Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Number of Closed-in Battery Racks Below Threshold |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
BMS State of Health Below Threshold |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
PCS DC Voltage Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Number of PCS Modules Below Threshold |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
PCS Active Power Threshold Exceeded |  | Status |  | Input Register |  |  |  | 2068 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Unit1_Uinab_RMS | pcs1_voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2070 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 AB Line Voltage |  | /site/ess_ls
Unit1_Uinbc_RMS | pcs1_voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2071 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 BC Line Voltage |  | /site/ess_ls
Unit1_Uinca_RMS | pcs1_voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2072 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 CA Line Voltage |  | /site/ess_ls
Unit1_Iina_RMS | pcs1_current_l1 | Status | 1 | Input Register | A |  | 10 | 2073 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 A Line Current |  | /site/ess_ls
Unit1_Iinb_RMS | pcs1_current_l2 | Status | 1 | Input Register | A |  | 10 | 2074 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 B Line Current |  | /site/ess_ls
Unit1_Iinc_RMS | pcs1_current_l3 | Status | 1 | Input Register | A |  | 10 | 2075 | uint16 | 0 | 65535 | [8 empty] | No | PCS 1 C Line Current |  | /site/ess_ls
Unit1_P | pcs1_active_power | Status | 1 | Input Register | kW | 2 | 10 | 2076-2077 | int32 | -2147483648 | 2147483647 | [8 empty] | No | PCS 1 AC Active Power |  | /site/ess_ls
Unit1_Q | pcs1_reactive_power | Status | 1 | Input Register | kVar | 2 | 10 | 2078-2079 | int32 | -2147483648 | 2147483647 | [8 empty] | No | PCS 1 AC Reactive Power |  | /site/ess_ls
Unit1_Ubtra_Ever | pcs1_voltage_dc | Status | 1 | Input Register | V |  | 10 | 2080 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 DC Voltage |  | /site/ess_ls
Unit1_Ibtra_Ever | pcs1_current_dc | Status | 1 | Input Register | A |  | 10 | 2081 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 DC Current |  | /site/ess_ls
Unit1_Pbtra | pcs1_active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2082 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 DC Active Power |  | /site/ess_ls
Maximum charging power limit Unit1 | maximum_charging_power_limit_pcs1 | Status |  | Input Register | kW |  | 10 | 2083 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 Maximum Charging Power Limit |  | /site/ess_ls
Maximum discharging power limit Unit1 | maximum_discharging_power_limit_pcs1 | Status |  | Input Register | kW |  | 10 | 2084 | int16 | -32768 | 32767 | [8 empty] | No | PCS 1 Maximum Discharging Power Limit |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | Status |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | Status |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Status | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | Status |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | Status |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | Status |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Status | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | Status |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state5 | pcs1_alarms5 | Status |  | Input Register |  | 2 |  | 2093 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 5 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | Status |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | Status |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | Status |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Status | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Status | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Status | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Status | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | Status |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | Status |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | Status |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | Status |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Status | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Status | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state5 | pcs1_faults5 | Status |  | Input Register |  | 2 |  | 2103 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 5 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | Status |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
BMS maximum cell voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2130 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS minimum cell voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2133 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS maximum cell temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2136 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS minimum cell temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2139 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS SOC | bms_soc | Status | 1 | Input Register | % |  | 10 | 2144 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS SOH | bms_soh | Status | 1 | Input Register | % |  | 10 | 2145 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Health |  | /site/ess_ls
BMS power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2146 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2157 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2158 | uint16 | 0 | 65535 | [8 empty] | No | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS alarm state | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2163 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
BMS fault state | bms_faults | Status | 1 | Input Register |  | 2 |  | 2165 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | Status |  | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | Status |  | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | Status |  | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Status |  | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Number of Battery Racks in Service | racks_in_service | Status |  | Input Register |  |  |  | 2199 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
Battery Rack No. 1 Voltage | sbmu_1_battery_voltage | Status |  | Input Register | V | 1 |  | 2200 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | sbmu_1_battery_current | Status |  | Input Register | A | 1 |  | 2201 | int16 | -32768 | 32767 | [8 empty] | No | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | sbmu_1_max_cell_voltage | Status |  | Input Register | V | 1 |  | 2202 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | sbmu_1_max_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2203 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | sbmu_1_min_cell_voltage | Status |  | Input Register | V | 1 |  | 2204 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | sbmu_1_min_cell_voltage_position | Status |  | Input Register |  | 1 |  | 2205 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | sbmu_1_avg_cell_voltage | Status |  | Input Register | V | 1 |  | 2206 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | sbmu_1_max_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2207 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | sbmu_1_max_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2208 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | sbmu_1_min_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2209 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | sbmu_1_min_cell_temperature_position | Status |  | Input Register |  | 1 |  | 2210 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | sbmu_1_avg_cell_temperature | Status |  | Input Register | °C | 1 | 100 | 2211 | uint16 | 0 | 65535 | [8 empty] | No | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state | sbmu_1_alarms | Status |  | Input Register |  | 2 |  | 2212 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
TMS Fault Level 1 | TMS Fault Level 1 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
TMS Fault Level 2 | TMS Fault Level 2 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Fault Level 3 | TMS Fault Level 3 | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | Status |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Battery Rack No. 1 fault state | sbmu_1_faults | Status |  | Input Register |  | 2 |  | 2214 | bitfield | [10 empty] | Yes | Battery Rack 1 Fault Status |  | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Balance Warning | Balance Warning | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Status | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
MSD Fault | MSD Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 3 | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Aerosol State Fault | Aerosol State Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Rack Switch State | Rack Switch State | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Status |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
sbmu_1 | sbmu_2 | Status |  |  |  | 15 |  | 2216 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2216 - 2231 for sbmu_2 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_3 | Status |  |  |  | 15 |  | 2232 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2232 - 2247 for sbmu_3 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_4 | Status |  |  |  | 15 |  | 2248 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2248 - 2263 for sbmu_4 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_5 | Status |  |  |  | 15 |  | 2264 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2264 - 2279 for sbmu_5 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_6 | Status |  |  |  | 15 |  | 2280 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2280 - 2295 for sbmu_6 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_7 | Status |  |  |  | 15 |  | 2296 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2296 - 2311 for sbmu_7 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_8 | Status |  |  |  | 15 |  | 2312 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2312 - 2327 for sbmu_8 |  | /site/ess_ls |  |  | 2200
sbmu_1 | sbmu_9 | Status |  |  |  | 15 |  | 2328 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2328 - 2343 for sbmu_9 |  | /site/ess_ls |  |  | 2200

## modified_050521
Connection Name | FlexGen_ESS_Controller
Connection IP Address (if TCP) | 192.168.114.11
Connection Port (502 typical) | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | ess_reference | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [12 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Life | life | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Control_Command | start_stop | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Word 1 |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
Run_mode | run_mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | Run Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Power_Set_AC | active_power_setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Active_Set_AC | reactive_power_setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active_power_rising_slope | active_power_rising_slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | Yes | Active Power Rising Slope |  | /site/ess_hs
Active_power_droop_slope | active_power_droop_slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | Yes | Active Power Droop Slope |  | /site/ess_hs
Reactive_power_rising_slope | reactive_power_rising_slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | Yes | Reactive Power Rising Slope |  | /site/ess_hs
Reactive_power_droop_slope | reactive_power_droop_slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | Yes | Reactive Power Droop Slope |  | /site/ess_hs
BMS_DC_Contactor_Control | bms_dc_contactors | bms_dc_contactors |  |  | Holding Register |  |  |  | 1011 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Clear_Faults_Command | clear_faults | clear_faults |  |  | Holding Register |  |  |  | 1012 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | clear_faults |  |  | Holding Register |  |  |  | 1012 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
life_signal | /status/site:Heartbeat | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Q_charge | /components/catl_bms_ems_r:bms_remain_charge_energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_hs
Q_discharge | /components/catl_bms_ems_r:bms_remain_discharge_energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_hs
W_charge | /components/catl_bms_ems_r:bms_max_charge_allowed | chargeable_power | Status | 1 | Input Register | kW |  | 10 | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_hs
W_discharge | /components/catl_bms_ems_r:bms_max_discharge_allowed | dischargeable_power | Status | 1 | Input Register | kW |  | 10 | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_hs
System_state | system_state | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_hs
Stop | Stop | Stop | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Stop
Run | Run | Run | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | Run
Fault | Fault | Fault | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | Fault
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | Standby
Com_status | com_status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_hs |  | 0 = online 1 = offline
PCS Communication Offline | /status/pcs:CommsOK | PCS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | PCS Communication Status
BMS Communication Offline | /status/bms:CommsOK | BMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | BMS Communication Status
EMMU Communication Offline | EMMU Communication Offline | EMMU Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | EMMU Communication Status
EMS Communication Offline | EMS Communication Offline | EMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | EMS Communication Status
Environmental management system alarms | ems_alarms | ems_alarms |  |  | Input Register |  |  |  | 2008 | bitfield | 0 | 65535 | [8 empty] | Yes | Environmental Management System (EMS) Alarms |  | /site/ess_hs
E-stop Alarm | E-stop Alarm | E-stop Alarm |  |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs
Disconnect Switch | Disconnect Switch | Disconnect Switch |  |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs
Door Latch | Door Latch | Door Latch |  |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs
Surge Arrester | Surge Arrester | Surge Arrester |  |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs
Fire Alarm | Fire Alarm | Fire Alarm |  |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 4 | /site/ess_hs
Fuse Monitoring | Fuse Monitoring | Fuse Monitoring |  |  | Input Register |  |  |  | 2008 | bit | [10 empty] | Yes |  | 5 | /site/ess_hs
Uinab_RMS | /components/pcsm_grid_visualization:grid_voltage_rs | voltage_l1_l2 | Status | 1 | Input Register | V |  |  | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_hs
Uinbc_RMS | /components/pcsm_grid_visualization:grid_voltage_st | voltage_l2_l3 | Status | 1 | Input Register | V |  |  | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_hs
Uinca_RMS | /components/pcsm_grid_visualization:grid_voltage_tr | voltage_l3_l1 | Status | 1 | Input Register | V |  |  | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_hs
Iina_RMS | /components/pcsm_grid_visualization:grid_current_1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2033 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_hs
Iinb_RMS | /components/pcsm_grid_visualization:grid_current_2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2034 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_hs
Iinc_RMS | /components/pcsm_grid_visualization:grid_current_l3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2035 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_hs
Frequency | /components/pcsm_grid_visualization:grid_frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2036 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_hs
Active Power | /components/pcsm_grid_visualization:active_power | active_power | Status | 1 | Input Register | kW |  | 10 | 2037 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_hs
Reactive Power | /components/pcsm_grid_visualization:reactive_power | reactive_power | Status | 1 | Input Register | kVar |  | 10 | 2038 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_hs
Overall apparent Power | apparent_power | apparent_power |  |  | Input Register |  |  | 10 | 2039 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_hs
Power Factor | /components/pcsm_grid_visualization:cos_phi | pf | Status | 1 | Input Register |  |  | 1000 | 2040 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_hs
Ubtra_Ever | /components/catl_mbmu_summary_r:mbmu_voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2041 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_hs
Ibtra_Ever | /status/bms:BMSCurrent | current_dc | Status | 1 | Input Register | A |  | 10 | 2042 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_hs
Pbtra | active_power_dc | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2043 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_hs
Low Speed | [12 empty] | TRUE | life_signal | 200 | life | 1000 | 58 | 10 | ess_ls | yes
PCS_Mode | pcs_mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2044 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) | On-grid constant current (CC) | On-grid constant current (CC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) | On-grid constant voltage (CV) | On-grid constant voltage (CV) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) | On-grid constant power (AC) | On-grid constant power (AC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) | On-grid constant power (DC) | On-grid constant power (DC) | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode | On-grid Mode | On-grid Mode | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode | Off-grid Mode | Off-grid Mode | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS_State1 | pcs_state | pcs_state | Status | 1 | Input Register |  | 2 |  | 2045 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Overall Work State |  | /site/ess_ls | Refer to PCS Instructions
Off | Power up | Power up | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Starting | Initialization | Initialization | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Ready | Off | Off | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Running | Precharge | Precharge | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Shutdown | Start in process | Start in process | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Fault | Stop in process | Stop in process | Status | 1 | Input Register |  |  |  | 2045 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
BMS Power On | bms_poweron | bms_poweron |  |  | Input Register |  |  |  | 2053 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Power off Ready |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Power on Ready |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Power on Fault |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Power off Fault |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | bms_status |  |  | Input Register |  |  |  | 2054 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Initial status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Normal status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Full Charge status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Full Discharge status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Warning status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Fault status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC_Contactors_Closed_Command | dc_contactors_closed | dc_contactors_closed |  |  | Input Register |  |  |  | 2055 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | dc_contactors_closed | dc_contactors_closed | dc_contactors_closed | Input Register |  |  |  | 2055 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | 0 = contactors closed, 1 = contactors open
Unit1_Uinab_RMS | pcs1_voltage_l1_l2 | pcs1_voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2070 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 AB Line Voltage |  | /site/ess_ls
Unit1_Uinbc_RMS | pcs1_voltage_l2_l3 | pcs1_voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2071 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 BC Line Voltage |  | /site/ess_ls
Unit1_Uinca_RMS | pcs1_voltage_l3_l1 | pcs1_voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2072 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 CA Line Voltage |  | /site/ess_ls
Unit1_Iina_RMS | pcs1_current_l1 | pcs1_current_l1 | Status | 1 | Input Register | A |  | 10 | 2073 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 A Line Current |  | /site/ess_ls
Unit1_Iinb_RMS | pcs1_current_l2 | pcs1_current_l2 | Status | 1 | Input Register | A |  | 10 | 2074 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 B Line Current |  | /site/ess_ls
Unit1_Iinc_RMS | pcs1_current_l3 | pcs1_current_l3 | Status | 1 | Input Register | A |  | 10 | 2075 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 C Line Current |  | /site/ess_ls
Unit1_P | pcs1_active_power | pcs1_active_power | Status | 1 | Input Register | kW | 2 | 10 | 2076-2077 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 1 AC Active Power |  | /site/ess_ls
Unit1_Q | pcs1_reactive_power | pcs1_reactive_power | Status | 1 | Input Register | kVar | 2 | 10 | 2078-2079 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 1 AC Reactive Power |  | /site/ess_ls
Unit1_Ubtra_Ever | pcs1_voltage_dc | pcs1_voltage_dc | Status | 1 | Input Register | V |  | 10 | 2080 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Voltage |  | /site/ess_ls
Unit1_Ibtra_Ever | pcs1_current_dc | pcs1_current_dc | Status | 1 | Input Register | A |  | 10 | 2081 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Current |  | /site/ess_ls
Unit1_Pbtra | pcs1_active_power_dc | pcs1_active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2082 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Active Power |  | /site/ess_ls
Maximum charging power limit Unit1 | maximum_charging_power_limit_pcs1 | maximum_charging_power_limit_pcs1 |  |  | Input Register | kW |  | 10 | 2083 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 Maximum Charging Power Limit |  | /site/ess_ls
Maximum discharging power limit Unit1 | maximum_discharging_power_limit_pcs1 | maximum_discharging_power_limit_pcs1 |  |  | Input Register | kW |  | 10 | 2084 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 Maximum Discharging Power Limit |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency |  |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | (TRKNM) warning - description unknown |  |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing |  |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | pcs1_alarms2 |  |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | (NOCHN) No channel available |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | pcs1_alarms3 |  |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | pcs1_alarms4 |  |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | (RSV_W) Reserved warning |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | (BBON) Blackbox on |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | (ACTBAL) Active Balance |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state5 | pcs1_alarms5 | pcs1_alarms5 |  |  | Input Register |  | 2 |  | 2093 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 5 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | (BMSSS) System Stop BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | pcs1_faults1 |  |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | (MSF) Modules start fault |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | pcs1_faults2 |  |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | (INTCMS) Internal comms |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | pcs1_faults3 |  |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | pcs1_faults4 |  |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | (RSV_F) Reserved fault |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | (PRDID) Product ID invalid |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state5 | pcs1_faults5 | pcs1_faults5 |  |  | Input Register |  | 2 |  | 2103 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 5 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
BMS maximum cell voltage | /components/catl_mbmu_summary_r:mbmu_max_cell_voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2130 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
BMS minimum cell voltage | /components/catl_mbmu_summary_r:mbmu_min_cell_voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2133 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
BMS maximum cell temperature | /components/catl_mbmu_summary_r:mbmu_max_cell_temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2136 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
BMS minimum cell temperature | /components/catl_mbmu_summary_r:mbmu_min_cell_temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2139 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
BMS SOC | /components/catl_mbmu_summary_r:mbmu_soc | bms_soc | Status | 1 | Input Register | % |  | 10 | 2144 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS power | bms_power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2145 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
BMS Maximum charging power limit | /components/catl_bms_ems_r:bms_max_charge_allowed | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2157 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | /components/catl_bms_ems_r:bms_max_discharge_allowed | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2158 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Maximum Discharging Power Limit |  | /site/ess_ls
BMS alarm state | bms_alarms | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2163 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | System Voltage Underlimit Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Cell Extreme Temperature Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Cell Extreme Voltage Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | EMS Heartbeat Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | SOC Difference Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Fire Fault Level 2 Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
BMS fault state 1 | bms_faults1 | bms_faults1 | Status | 1 | Input Register |  | 2 |  | 2165 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Insulation error protection | Insulation error protection | Insulation error protection | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Discharge undervoltage LV1 protection of cell | Discharge undervoltage LV1 protection of cell | Discharge undervoltage LV1 protection of cell | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Charge overvoltage LV1 protection of cell | Charge overvoltage LV1 protection of cell | Charge overvoltage LV1 protection of cell | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Discharge undervoltage LV1 protection of cluster | Discharge undervoltage LV1 protection of cluster | Discharge undervoltage LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge overvoltage LV1 protection of cluster | Charge overvoltage LV1 protection of cluster | Charge overvoltage LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge overcurrent LV1 protection of cluster | Discharge overcurrent LV1 protection of cluster | Discharge overcurrent LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Charge overcurrent LV1 protection of cluster | Charge overcurrent LV1 protection of cluster | Charge overcurrent LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Discharge overcurrent LV1 protection of array | Discharge overcurrent LV1 protection of array | Discharge overcurrent LV1 protection of array | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Charge overcurrent LV1 protection of array | Charge overcurrent LV1 protection of array | Charge overcurrent LV1 protection of array | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Low-temp LV1 protection | Low-temp LV1 protection | Low-temp LV1 protection | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
High-temp LV1 protection | High-temp LV1 protection | High-temp LV1 protection | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Self-protection of BMS | Self-protection of BMS | Self-protection of BMS | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
E-stop fault | E-stop fault | E-stop fault | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Self-protection of EMMU | Self-protection of EMMU | Self-protection of EMMU | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
BMS fault state 2 | bms_faults2 | bms_faults2 |  |  | Input Register |  | 2 |  | 2167 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 2 |  | /site/ess_ls
Discharge undervoltage LV2 protection of cell | Discharge undervoltage LV2 protection of cell | Discharge undervoltage LV2 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Charge overvoltage LV2 protection of cell | Charge overvoltage LV2 protection of cell | Charge overvoltage LV2 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Discharge overcurrent LV2 protection of cluster | Discharge overcurrent LV2 protection of cluster | Discharge overcurrent LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge overcurrent LV2 protection of cluster | Charge overcurrent LV2 protection of cluster | Charge overcurrent LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge overcurrent LV2 protection of array | Discharge overcurrent LV2 protection of array | Discharge overcurrent LV2 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Charge overcurrent LV2 protection of array | Charge overcurrent LV2 protection of array | Charge overcurrent LV2 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Low-temp LV2 protection | Low-temp LV2 protection | Low-temp LV2 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
High-temp LV2 protection | High-temp LV2 protection | High-temp LV2 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Number of Battery Racks in Service | racks_in_service | racks_in_service |  |  | Input Register |  |  |  | 2199 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
Battery Rack No. 1 Voltage | /components/catl_@@BMS_ID@@/sbmu_voltage | sbmu_1_battery_voltage |  |  | Input Register | V | 1 |  | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | /components/catl_@@BMS_ID@@/sbmu_current | sbmu_1_battery_current |  |  | Input Register | A | 1 |  | 2201 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | /components/catl_@@BMS_ID@@/sbmu_max_cell_voltage | sbmu_1_max_cell_voltage |  |  | Input Register | V | 1 |  | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | rack_1_max_cell_voltage_position | sbmu_1_max_cell_voltage_position |  |  | Input Register |  | 1 |  | 2203 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | /components/catl_@@BMS_ID@@/sbmu_min_cell_voltage | sbmu_1_min_cell_voltage |  |  | Input Register | V | 1 |  | 2204 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | rack_1_min_cell_voltage_position | sbmu_1_min_cell_voltage_position |  |  | Input Register |  | 1 |  | 2205 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | /components/catl_@@BMS_ID@@/sbmu_avg_cell_voltage | sbmu_1_avg_cell_voltage |  |  | Input Register | V | 1 |  | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | /components/catl_@@BMS_ID@@/sbmu_max_cell_temperature | sbmu_1_max_cell_temperature |  |  | Input Register | °C | 1 | 100 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | rack_1_max_cell_temperature_position | sbmu_1_max_cell_temperature_position |  |  | Input Register |  | 1 |  | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | /components/catl_@@BMS_ID@@/sbmu_min_cell_temperature | sbmu_1_min_cell_temperature |  |  | Input Register | °C | 1 | 100 | 2209 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | rack_1_min_cell_temperature_position | sbmu_1_min_cell_temperature_position |  |  | Input Register |  | 1 |  | 2210 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | /components/catl_@@BMS_ID@@/sbmu_avg_cell_temperature | sbmu_1_avg_cell_temperature |  |  | Input Register | °C | 1 | 100 | 2211 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state 1 | sbmu_1_alarms1 | sbmu_1_alarms1 |  |  | Input Register |  | 2 |  | 2212 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status 1 |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | SOC Low Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | SOC Low Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | SOC Low Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
TMS Fault Level 1 | TMS Fault Level 1 | TMS Fault Level 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
TMS Fault Level 2 | TMS Fault Level 2 | TMS Fault Level 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Fault Level 3 | TMS Fault Level 3 | TMS Fault Level 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Charge Overcurrent Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Discharge Overcurrent Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Temp Difference Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Cell Extreme Temperature Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Cell Extreme Voltage Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Extreme Total Voltage Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Power Loss Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Balance Warning | Balance Warning | Balance Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Battery Rack No. 1 alarm state 2 | sbmu_1_alarms2 | sbmu_1_alarms2 |  |  | Input Register |  | 2 |  | 2214 | bitfield | [10 empty] | Yes | Battery Rack 1 Alarm Status 2 |  | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Current Sensor Abnormal Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | High Voltage Circuit Open Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
MSD Fault | MSD Fault | MSD Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Isolate Switch Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Rack Fuse Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | TMS Communication Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | TMS Mode Conflict Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 2 | Fire Fault Level 3 |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Temperature Sensor Alarm |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Smoke Sensor Alarm |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Aerosol State Fault | Aerosol State Fault | Aerosol State Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Aerosol Close Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Aerosol Open Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Rack Switch State | Rack Switch State | Rack Switch State |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Control Box Overtemperature Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
sbmu_1 |  | sbmu_2 |  |  |  |  | 15 |  | 2216 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2216 - 2231 for sbmu_2 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_3 |  |  |  |  | 15 |  | 2232 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2232 - 2247 for sbmu_3 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_4 |  |  |  |  | 15 |  | 2248 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2248 - 2263 for sbmu_4 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_5 |  |  |  |  | 15 |  | 2264 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2264 - 2279 for sbmu_5 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_6 |  |  |  |  | 15 |  | 2280 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2280 - 2295 for sbmu_6 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_7 |  |  |  |  | 15 |  | 2296 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2296 - 2311 for sbmu_7 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_8 |  |  |  |  | 15 |  | 2312 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2312 - 2327 for sbmu_8 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_9 |  |  |  |  | 15 |  | 2328 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2328 - 2343 for sbmu_9 |  | /site/ess_ls |  |  | 2200

## original
Connection Name | FlexGen_ESS_Controller
Connection IP Address (if TCP) | 192.168.114.11
Connection Port (502 typical) | 502
Device Name | FlexGen_ESS_Controller | [12 empty] | HB read | timeout | HB Write
Device ID String | /site
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | ess_reference | Reg ID | Type | Version | Register Type | Unit | Words | Scale | Address | Data Type | Range Start | Range End | Heartbeat Enabled | Component Heartbeat Read URI | Modbus Hearbeat Timeout mS | Component Heartbeat Write URI | Frequency | Device ID | Offset Time | Component ID | Include | Description | Bit | URI | Control Narrative for Register | notes | Repeat
High Speed | [12 empty] | TRUE | life_signal | 200 | life | 100 | 98 | 20 | ess_hs | Yes
Life | life | life | Control | 1 | Holding Register |  | 2 |  | 1000 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Control_Command | start_stop | start_stop | Control | 1 | Holding Register |  |  |  | 1002 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Word 1 |  | /site/ess_hs | 205 = standby, 206 = stop, 207 = start
Run_mode | run_mode | run_mode | Control | 1 | Holding Register |  |  |  | 1003 | uint16 | 0 | 65535 | [8 empty] | Yes | Run Mode |  | /site/ess_hs | 1 = ongrid CC, 2 = ongrid CV, 4 = ongrid constand power AC, 8 = ongrid constant power DC
On/Off grid mode setting | on_off_grid_mode | on_off_grid_mode | Control | 1 | Holding Register |  |  |  | 1004 | uint16 | 0 | 65535 | [8 empty] | Yes | On/Off Grid Mode Setting |  | /site/ess_hs | 85 = off grid, 170 = on grid
Power_Set_AC | active_power_setpoint | active_power_setpoint | Control | 1 | Holding Register | kW |  | 10 | 1005 | int16 | -32768 | 32767 | [8 empty] | Yes | Active Power Setpoint |  | /site/ess_hs
Active_Set_AC | reactive_power_setpoint | reactive_power_setpoint | Control | 1 | Holding Register | kVar |  | 10 | 1006 | int16 | -32768 | 32767 | [8 empty] | Yes | Reactive Power Setpoint |  | /site/ess_hs
Active_power_rising_slope | active_power_rising_slope | active_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1007 | uint16 | 0 | 65535 | [8 empty] | Yes | Active Power Rising Slope |  | /site/ess_hs
Active_power_droop_slope | active_power_droop_slope | active_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1008 | uint16 | 0 | 65535 | [8 empty] | Yes | Active Power Droop Slope |  | /site/ess_hs
Reactive_power_rising_slope | reactive_power_rising_slope | reactive_power_rising_slope | Control | 1 | Holding Register | %/s |  | 10 | 1009 | uint16 | 0 | 65535 | [8 empty] | Yes | Reactive Power Rising Slope |  | /site/ess_hs
Reactive_power_droop_slope | reactive_power_droop_slope | reactive_power_droop_slope | Control | 1 | Holding Register | %/s |  | 10 | 1010 | uint16 | 0 | 65535 | [8 empty] | Yes | Reactive Power Droop Slope |  | /site/ess_hs
BMS_DC_Contactor_Control | bms_dc_contactors | bms_dc_contactors |  |  | Holding Register |  |  |  | 1011 | uint16 | [10 empty] | Yes | BMS DC Contactor Control |  | /site/ess_hs
Clear_Faults_Command | clear_faults | clear_faults |  |  | Holding Register |  |  |  | 1012 | individual_bits | 0 | 65535 | [8 empty] | Yes | Clear Faults Command |  | /site/ess_hs
clear_faults | clear_faults | clear_faults |  |  | Holding Register |  |  |  | 1012 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Clear Faults
life_signal | /status/site:Heartbeat | life_signal | Status | 1 | Input Register | s | 2 |  | 2000-2001 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | Heartbeat |  | /site/ess_hs
Q_charge | /components/catl_bms_ems_r:bms_remain_charge_energy | chargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2002 | uint16 | 0 | 65535 | [8 empty] | Yes | Rechargeable Capacity |  | /site/ess_hs
Q_discharge | /components/catl_bms_ems_r:bms_remain_discharge_energy | dischargeable_energy | Status | 1 | Input Register | kWh |  | 10 | 2003 | uint16 | 0 | 65535 | [8 empty] | Yes | Redischargeable Capacity |  | /site/ess_hs
W_charge | /components/catl_bms_ems_r:bms_max_charge_allowed | chargeable_power | Status | 1 | Input Register | kW |  | 10 | 2004 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Chargeable Power |  | /site/ess_hs
W_discharge | /components/catl_bms_ems_r:bms_max_discharge_allowed | dischargeable_power | Status | 1 | Input Register | kW |  | 10 | 2005 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Dischargeable Power |  | /site/ess_hs
System_state | system_state | system_state | Status | 1 | Input Register |  |  |  | 2006 | bitfield | 0 | 65535 | [8 empty] | Yes | System State |  | /site/ess_hs
Stop | Stop | Stop | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | Stop
Run | Run | Run | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | Run
Fault | Fault | Fault | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | Fault
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2006 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | Standby
Com_status | com_status | com_status | Status | 1 | Input Register |  |  |  | 2007 | bitfield | 0 | 65535 | [8 empty] | Yes | Communication Status |  | /site/ess_hs |  | 0 = online 1 = offline
PCS Communication Offline | /status/pcs:CommsOK | PCS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | PCS Communication Status
BMS Communication Offline | /status/bms:CommsOK | BMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs | BMS Communication Status
EMMU Communication Offline | EMMU Communication Offline | EMMU Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs | EMMU Communication Status
EMS Communication Offline | EMS Communication Offline | EMS Communication Offline | Status | 1 | Input Register |  |  |  | 2007 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs | EMS Communication Status
PCS under power | pcs_under_power | pcs_under_power | Status | 1 | Input Register |  |  |  | 2008 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS Under Power |  | /site/ess_hs | 0 = normal, 1 = under power
PCS over power | pcs_over_power | pcs_over_power | Status | 1 | Input Register |  |  |  | 2009 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS Over Power |  | /site/ess_hs | 0 = normal, 1 = over power
Environmental management system alarms | ems_alarms | ems_alarms |  |  | Input Register |  |  |  | 2010 | bitfield | 0 | 65535 | [8 empty] | Yes | Environmental Management System (EMS) Alarms |  | /site/ess_hs
E-stop Alarm | E-stop Alarm | E-stop Alarm |  |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs
Disconnect Switch | Disconnect Switch | Disconnect Switch |  |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 1 | /site/ess_hs
Door Latch | Door Latch | Door Latch |  |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 2 | /site/ess_hs
Surge Arrester | Surge Arrester | Surge Arrester |  |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 3 | /site/ess_hs
Fire Alarm | Fire Alarm | Fire Alarm |  |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 4 | /site/ess_hs
Fuse Monitoring | Fuse Monitoring | Fuse Monitoring |  |  | Input Register |  |  |  | 2010 | bit | [10 empty] | Yes |  | 5 | /site/ess_hs
Uinab_RMS | /components/pcsm_grid_visualization:grid_voltage_rs | voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2030 | uint16 | 0 | 65535 | [8 empty] | Yes | AB Line Voltage |  | /site/ess_hs
Uinbc_RMS | /components/pcsm_grid_visualization:grid_voltage_st | voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2031 | uint16 | 0 | 65535 | [8 empty] | Yes | BC Line Voltage |  | /site/ess_hs
Uinca_RMS | /components/pcsm_grid_visualization:grid_voltage_tr | voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2032 | uint16 | 0 | 65535 | [8 empty] | Yes | CA Line Voltage |  | /site/ess_hs
Iina_RMS | /components/pcsm_grid_visualization:grid_current_1 | current_l1 | Status | 1 | Input Register | A |  | 10 | 2033 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase A Line Current |  | /site/ess_hs
Iinb_RMS | /components/pcsm_grid_visualization:grid_current_2 | current_l2 | Status | 1 | Input Register | A |  | 10 | 2034 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase B Line Current |  | /site/ess_hs
Iinc_RMS | /components/pcsm_grid_visualization:grid_current_l3 | current_l3 | Status | 1 | Input Register | A |  | 10 | 2035 | uint16 | 0 | 65535 | [8 empty] | Yes | Phase C Line Current |  | /site/ess_hs
Frequency | /components/pcsm_grid_visualization:grid_frequency | frequency | Status | 1 | Input Register | Hz |  | 100 | 2036 | uint16 | 0 | 65535 | [8 empty] | Yes | Frequency |  | /site/ess_hs
Active Power | /components/pcsm_grid_visualization:active_power | active_power | Status | 1 | Input Register | kW |  | 10 | 2037 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Active Power |  | /site/ess_hs
Reactive Power | /components/pcsm_grid_visualization:reactive_power | reactive_power | Status | 1 | Input Register | kVar |  | 10 | 2038 | int16 | -32768 | 32767 | [8 empty] | Yes | AC Reactive Power |  | /site/ess_hs
Power Factor | /components/pcsm_grid_visualization:cos_phi | pf | Status | 1 | Input Register |  |  | 1000 | 2039 | uint16 | 0 | 65535 | [8 empty] | Yes | Power Factor |  | /site/ess_hs
Ubtra_Ever | /components/catl_mbmu_summary_r:mbmu_voltage | voltage_dc | Status | 1 | Input Register | V |  | 10 | 2040 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Voltage |  | /site/ess_hs
Ibtra_Ever | /status/bms:BMSCurrent | current_dc | Status | 1 | Input Register | A |  | 10 | 2041 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Current |  | /site/ess_hs
Pbtra | active_power_dc | active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2042 | int16 | -32768 | 32767 | [8 empty] | Yes | DC Active Power |  | /site/ess_hs
Low Speed | [12 empty] | TRUE | life_signal | 200 | life | 1000 | 58 | 10 | ess_ls | yes
PCS_Mode | pcs_mode | pcs_mode | Status | 1 | Input Register |  |  |  | 2043 | bitfield | 0 | 65535 | [8 empty] | Yes | Operating Mode |  | /site/ess_ls | Refer to PCS Instructions
On-grid constant current (CC) | On-grid constant current (CC) | On-grid constant current (CC) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
On-grid constant voltage (CV) | On-grid constant voltage (CV) | On-grid constant voltage (CV) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
On-grid constant power (AC) | On-grid constant power (AC) | On-grid constant power (AC) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
On-grid constant power (DC) | On-grid constant power (DC) | On-grid constant power (DC) | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
On-grid Mode | On-grid Mode | On-grid Mode | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Off-grid Mode | Off-grid Mode | Off-grid Mode | Status | 1 | Input Register |  |  |  | 2043 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
PCS_State1 | pcs_state | pcs_state | Status | 1 | Input Register |  | 2 |  | 2044 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Overall Work State |  | /site/ess_ls | Refer to PCS Instructions
Running | Running | Running | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Key stop | Key stop | Key stop | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Emergency stop | Emergency stop | Emergency stop | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Start in process | Start in process | Start in process | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Stop in process | Stop in process | Stop in process | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Fault stop | Fault stop | Fault stop | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Alarm running | Alarm running | Alarm running | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Derating running | Derating running | Derating running | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
DSP communication error | DSP communication error | DSP communication error | Status | 1 | Input Register |  |  |  | 2044 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
PCS_State2 | pcs_state2 | pcs_state2 | Status | 1 | Input Register |  |  |  | 2046 | bitfield | 0 | 65535 | [8 empty] | Yes | Overall Charging/Discharging State |  | /site/ess_ls
Charging | Charging | Charging | Status | 1 | Input Register |  |  |  | 2046 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Charging
Discharging | Discharging | Discharging | Status | 1 | Input Register |  |  |  | 2046 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Discharging
Non-operating mode | Non-operating mode | Non-operating mode | Status | 1 | Input Register |  |  |  | 2046 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Non-operating mode
Overall_Fault | faults | faults | Status | 1 | Input Register |  |  |  | 2047 | bitfield | 0 | 65535 | [8 empty] | Yes | Fault Status |  | /site/ess_ls |  | 0 = normal, 1 = fault
Smoke Alarm | Smoke Alarm | Smoke Alarm | Status | 1 | Input Register |  |  |  | 2047 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Smoke Alarm
Door Open Protection | Door Open Protection | Door Open Protection | Status | 1 | Input Register |  |  |  | 2047 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Door Open Protection | 0 = disable, 1 = enable
Overall_Alarm | alarms | alarms | Status | 1 | Input Register |  | 2 |  | 2048 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Alarm Status |  | /site/ess_ls
Temperature & Humidity Board Communication Error | Temperature & Humidity Board Communication Error | Temperature & Humidity Board Communication Error | Status | 1 | Input Register |  |  |  | 2048 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Temperature & Humidity Board Communication Error | 0 = normal 1 = alarm
Switch Board Communication Error | Switch Board Communication Error | Switch Board Communication Error | Status | 1 | Input Register |  |  |  | 2048 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Switch Board Communication Error
Tributary Board Communication Error | Tributary Board Communication Error | Tributary Board Communication Error | Status | 1 | Input Register |  |  |  | 2048 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Tributary Board Communication Error
Overall Maximum charging power limit | overall_maximum_charging_power_limit | overall_maximum_charging_power_limit | Status | 1 | Input Register | kW |  | 10 | 2050 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Maximum Charging Power Limit |  | /site/ess_ls
Overall Maximum discharging power limit | overall_maximum_discharging_power_limit | overall_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  | 10 | 2051 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Maximum Discharging Power Limit |  | /site/ess_ls
Overall apparent Power | apparent_power | apparent_power |  |  | Input Register |  |  | 10 | 2052 | int16 | -32768 | 32767 | [8 empty] | Yes | Overall Apparent Power |  | /site/ess_ls
BMS Power On | bms_poweron | bms_poweron |  |  | Input Register |  |  |  | 2053 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS Power On Status |  | /site/ess_ls
Power off Ready | Power off Ready | Power off Ready |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Power on Ready | Power on Ready | Power on Ready |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Power on Fault | Power on Fault | Power on Fault |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Power off Fault | Power off Fault | Power off Fault |  |  | Input Register |  |  |  | 2053 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
BMS Status | bms_status | bms_status |  |  | Input Register |  |  |  | 2054 | bitfield | 0 | 65535 | [8 empty] | Yes | BMS System State |  | /site/ess_ls
Initial status | Initial status | Initial status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Normal Status | Normal status | Normal status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Full Charge status | Full Charge status | Full Charge status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Full Discharge status | Full Discharge status | Full Discharge status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Warning status | Warning status | Warning status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Fault status | Fault status | Fault status |  |  | Input Register |  |  |  | 2054 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
DC_Contactors_Closed_Command | dc_contactors_closed | dc_contactors_closed |  |  | Input Register |  |  |  | 2055 | individual_bits | 0 | 65535 | [8 empty] | Yes | DC Contactors Closed Status |  | /site/ess_ls
dc_contactors_closed | dc_contactors_closed | dc_contactors_closed | dc_contactors_closed | dc_contactors_closed | Input Register |  |  |  | 2055 | bit | [10 empty] | Yes |  | 0 | /site/ess_hs | 0 = contactors closed, 1 = contactors open
Unit1_Uinab_RMS | pcs1_voltage_l1_l2 | pcs1_voltage_l1_l2 | Status | 1 | Input Register | V |  | 10 | 2070 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 AB Line Voltage |  | /site/ess_ls
Unit1_Uinbc_RMS | pcs1_voltage_l2_l3 | pcs1_voltage_l2_l3 | Status | 1 | Input Register | V |  | 10 | 2071 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 BC Line Voltage |  | /site/ess_ls
Unit1_Uinca_RMS | pcs1_voltage_l3_l1 | pcs1_voltage_l3_l1 | Status | 1 | Input Register | V |  | 10 | 2072 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 CA Line Voltage |  | /site/ess_ls
Unit1_Iina_RMS | pcs1_current_l1 | pcs1_current_l1 | Status | 1 | Input Register | A |  | 10 | 2073 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 A Line Current |  | /site/ess_ls
Unit1_Iinb_RMS | pcs1_current_l2 | pcs1_current_l2 | Status | 1 | Input Register | A |  | 10 | 2074 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 B Line Current |  | /site/ess_ls
Unit1_Iinc_RMS | pcs1_current_l3 | pcs1_current_l3 | Status | 1 | Input Register | A |  | 10 | 2075 | uint16 | 0 | 65535 | [8 empty] | Yes | PCS 1 C Line Current |  | /site/ess_ls
Unit1_P | pcs1_active_power | pcs1_active_power | Status | 1 | Input Register | kW | 2 | 10 | 2076-2077 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 1 AC Active Power |  | /site/ess_ls
Unit1_Q | pcs1_reactive_power | pcs1_reactive_power | Status | 1 | Input Register | kVar | 2 | 10 | 2078-2079 | int32 | -2147483648 | 2147483647 | [8 empty] | Yes | PCS 1 AC Reactive Power |  | /site/ess_ls
Unit1_Ubtra_Ever | pcs1_voltage_dc | pcs1_voltage_dc | Status | 1 | Input Register | V |  | 10 | 2080 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Voltage |  | /site/ess_ls
Unit1_Ibtra_Ever | pcs1_current_dc | pcs1_current_dc | Status | 1 | Input Register | A |  | 10 | 2081 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Current |  | /site/ess_ls
Unit1_Pbtra | pcs1_active_power_dc | pcs1_active_power_dc | Status | 1 | Input Register | kW |  | 10 | 2082 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 DC Active Power |  | /site/ess_ls
Maximum charging power limit Unit1 | maximum_charging_power_limit_pcs1 | maximum_charging_power_limit_pcs1 |  |  | Input Register | kW |  | 10 | 2083 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 Maximum Charging Power Limit |  | /site/ess_ls
Maximum discharging power limit Unit1 | maximum_discharging_power_limit_pcs1 | maximum_discharging_power_limit_pcs1 |  |  | Input Register | kW |  | 10 | 2084 | int16 | -32768 | 32767 | [8 empty] | Yes | PCS 1 Maximum Discharging Power Limit |  | /site/ess_ls
Unit1_Alarm_state1 | pcs1_alarms1 | pcs1_alarms1 | Status | 1 | Input Register |  | 2 |  | 2085 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(HVAC) High input voltage | (HVAC) High input voltage | (HVAC) High input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(LVAC) Low input voltage | (LVAC) Low input voltage | (LVAC) Low input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(HFRQ) High frequency | (HFRQ) High frequency | (HFRQ) High frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(LFRQ) Low frequency | (LFRQ) Low frequency | (LFRQ) Low frequency | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NSC) No start condition | (NSC) No start condition | (NSC) No start condition | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(NOMD) No modules | (NOMD) No modules | (NOMD) No modules | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(PLIM) P limit has been reached | (PLIM) P limit has been reached | (PLIM) P limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(QLIM) Q limit has been reached | (QLIM) Q limit has been reached | (QLIM) Q limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | (ISLIM) Is limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | (IDCLIM) Idc limit has been reached | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | (PDVDC) Reduct P - A derating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(HEAET) Heating is active | (HEAET) Heating is active | (HEAET) Heating is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(NIGHT) Night mode is active | (NIGHT) Night mode is active | (NIGHT) Night mode is active | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | (LP) Low P - Active power is lower than the minimum AC power set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | (LVDC_W) Low Vdc - DC voltage is lower than the minimum DC voltage set | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | (PDT) Derating T - Inverter is limiting power due to high internal temperature | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency | (PPF) Power Per Frequency - Power is reduced due to a high frequency |  |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | (REDUN) Redun warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | (HVDC_W) High Vdc - DC voltage > 1500 V | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(UMF) Module fault | (UMF) Module fault | (UMF) Module fault | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TRKNM) warning - description unknown | (TRKNM) warning - description unknown | (TRKNM) warning - description unknown |  |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TRKLV) warning - description unknown | (TRKLV) warning - description unknown | (TRKLV) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(TRKCC) warning - description unknown | (TRKCC) warning - description unknown | (TRKCC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(TRKOC) warning - description unknown | (TRKOC) warning - description unknown | (TRKOC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(TRKBF) warning - description unknown | (TRKBF) warning - description unknown | (TRKBF) warning - description unknown | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | (LCFB) LC feedback - LC contactors are not operating adequately in the stop procedure | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing | (QFV) Curve Q vs V - Grid support QV ongoing |  |  | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | (PFV) Curve P vs V - Grid support PV ongoing | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | (VDCDS) Vdc discordance - Discordance between bus voltage and input voltage | Status | 1 | Input Register |  |  |  | 2085 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Unit1_Alarm_state2 | pcs1_alarms2 | pcs1_alarms2 |  |  | Input Register |  | 2 |  | 2087 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(OVP) AC overvoltage | (OVP) AC overvoltage | (OVP) AC overvoltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | (RTC) The RTC is not configured. Set the time | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | (MSWM) Modules version - There are one or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | (VSWM) uP DSP version - Software versions are not compatible | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NOSD) SD not present | (NOSD) SD not present | (NOSD) SD not present | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | (BMI) Battery module isolated - One or more modules with different software versions | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | (DUIUN) DU I unbalance - Current unbalance in the DU channels | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | (SPRLD) Spring loaded - Some of the circuit break triggers are not loaded | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DUVDC) warning - description unknown | (DUVDC) warning - description unknown | (DUVDC) warning - description unknown | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | (DUCOMS_W) Comms lost - There is a problem in the disconnecting unit communications | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | (CHISL) Channel isolated -DU channel isolated because it is derived, feedback has failed, or it did not measure voltage | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | (INSA) Algorithm on - Derived channels detection algorithm is running, once finished, the warning will automatically disappear | Status | 1 | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event | (DUOF) Fb open error - Problem with feedback from one of the DU channels in an opening event |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event | (DUCF) Fb close error - Problem with feedback from one of the DU channels in a closing event |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input | (OVDCP) DC overvoltage - Check the status of the disconnecting unit and J7 connector digital input |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently | (ISFLT) Isolation fault - warning not used currently |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels | (CHCOM) Acq comms error - Communications problem between the disconnecting unit and acquisition channels |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(NOCHN) No channel available | (NOCHN) No channel available | (NOCHN) No channel available |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side | (GRIDIN) Isolat flt AC grid - Isulation fault has occurred in the AC side |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing | (DUBSY) Processing cont - Contactors processing event ongoing |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected | (CHSWM) Acq version - DU acquisition channels with different versions have been detected |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown | (PCHM) warning - desciption unknown |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event | (CHCD) Current detected during DU channels opening event |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage | (CHMW) Channel miswired - One or more acquisition channels did not meaure any voltage |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent | (OC) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus | (UV) Unbal DC Bus - Unbalance between high side and low side of DC bus |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent | (DOC) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (POV) Mod. DC overvoltage (P) - Overvoltage present in DC positive side |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (NOV) Mod. DC overvoltage (N) - Overvoltage present in DC negative side |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver | (DR1) Desat R1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | (DR2P) Desat R2 (P) - Desaturation in IGBT driver | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver | (DR2N) Desat R2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2087 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state3 | pcs1_alarms3 | pcs1_alarms3 |  |  | Input Register |  | 2 |  | 2089 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver | (DR3) Desat R3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver | (DS1) Desat S1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver | (DS2P) Desat S2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver | (DS2N) Desat S2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver | (DS3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver | (DT1) Desat T1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver | (DT2P) Desat T2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver | (DT2N) Desat T2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver | (DT3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_W) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond | (FBDC) Mod. DC contactor - DC contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (FBSC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (FBAC) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (FBLC) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected | (TIGH) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGTB temperature sensor is disconnected |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUV) Mod. Great unbal DC - DC bus unbalanced more than 500V |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DIS) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (TLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PS) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMH) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation | (IDCD) Mod. Idc derivation |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation | (IACD) Mod. Iac derivation |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost | (DCOMS_W) Display comms - Communications between display and control board lost |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCF) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s | (UC) Unbalance current - A module ouptut current unbalance greater than 30A has been detected for 5s |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_W) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_W) Ambient temperature - Ambient temperature is over the maximum threshold |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_W) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus | (BUSUN_W) Vbus unbalanced - Unbalanced between the high side and low side of DC bus |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIDC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax | (HBMX_W) Half bus Vmax |  |  | Input Register |  |  |  | 2089 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state4 | pcs1_alarms4 | pcs1_alarms4 |  |  | Input Register |  | 2 |  | 2091 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_W) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown | (BACF_W) Blown AC fuse - All AC fuses have blown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(RSV_W) Reserved warning | (RSV_W) Reserved warning | (RSV_W) Reserved warning |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_W) OCAC emergency - Overcurrent has been detected in communication between module-x and central control |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control | (CCHK_W) Comms checksum - Communication error between module-x and central control |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan | (MDFN_W) Mod. fans - Feedback has not been received from the module fan |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_W) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_W) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | (CMTHR_W) Mod. common thermal - Inductance in a module has overheated | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown | (CNBFPS) warning - description unknown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown | (BFBFPS) warning - description unknown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown | (BFPSCM) warning - description unknown |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established | (ISODCCM) DC insulation monitor comms - Communication with the DC insulation monitor cannot be established |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold | (INSDC) Insulation DC - DC insulation monitor detected an insulation resistance below the threshold |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHDC) Insulation resistor high DC - DC insulation monitor has detected a higher insulation resistance than the admissible |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established | (ISOACCM) AC insulation monitor comms - Communication with the AC insulation monitor cannot be established |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold | (INSAC) Insulation AC - AC insulation monitor has detected an insulation resistance below the threshold |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible | (IRTHAC) Insulation resistor high AC - AC insulation monitor has detected a higher insulation resistance than the admissible |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established | (FNIMCM_W) Impulsion fans comms - Communication with the impulsion fans (cyclone) cannot be established |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error | (FNIMER_W) Impulsion fans - The impulsion fan (cyclone) has reported an error |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received | (FNXCER_W) Extract fans control - Feedback from extraction fans in the low voltage side has not been received |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received | (FNXMER_W) Extract fans MV - Feedback from extraction fans in the medium voltage side has not been received |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(BBON) Blackbox on | (BBON) Blackbox on | (BBON) Blackbox on |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure | (DUFB1) DU FB1 error. DC Circuit breaker (Q8) failure |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure | (DUFB2) DU FB2 error. DC Circuit breaker (Q9) failure |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(ACTBAL) Active Balance | (ACTBAL) Active Balance | (ACTBAL) Active Balance |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart | (BMSA) Battery Manage System is stopped because a BMS alarm is active. Check the BMS active alarms to restart |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied | (BMSIA) There is imbalance inside the BMS, some strings are disconnected within one bank. Power reduction is applied |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed | (SNTPF) Synchronization of NTP server has failed |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open | (EMBD) Battery bank is disabled by MPCSK (IGBTs are stopped and DC breaker is open |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded | (BMSCL) MPCSK has lost communication with BMS. Heartbeat time has been exceeded |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS | (BMSFE) Fuse Sensor Error BMS |  |  | Input Register |  |  |  | 2091 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Alarm_state5 | pcs1_alarms5 | pcs1_alarms5 |  |  | Input Register |  | 2 |  | 2093 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Alarm Status 5 |  | /site/ess_ls | Refer to PCS Instructions
(BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS | (BMSVSD) Voltage Sensor Error BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS | (BMSFSC) Current Sensor Error BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS | (BMSFF) Fan fault BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BMSSS) System Stop BMS | (BMSSS) System Stop BMS | (BMSSS) System Stop BMS |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance | (BMSSD) BMS Status Discordance |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration | (BMSWC) BMS Wrong Configuration |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative | (HVACNOP_W) HVAC Not Operative |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open | (ENCDORCN) ENC Door Contact - container battery enclosure is open |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble | (ENCALARTR) ENC Alarm/Trouble |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open | (ENCDCDIS) ENC DC Disconnect - One of the container DC switch disconnectors is open |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity | (ENCHHUM) ENC High Humidity |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery | (ENCUPSBAT) ENC UPS Battery |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected | (TRTEMP_W) Transformer over oil temperature detected |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected | (TRPRESU_W) Transformer over pressure detected |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected | (TROIL_W) Transformer oil low level detected |  |  | Input Register |  |  |  | 2093 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Unit1_Fault_state1 | pcs1_faults1 | pcs1_faults1 |  |  | Input Register |  | 2 |  | 2095 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 1 |  | /site/ess_ls | Refer to PCS Instructions
(WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | (WD) Watchdog - Fault in DSP has occurred | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | (HWVBS) HW Vbus - DC overvoltage detected. Threshold: 1520 Vdc | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | (SFTCHR) Softcharge - Wrong configuration (central AC without DU) OR Timeout, one of soft charge processes did not end successfully | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | (DISCHR) Discharge - Timeout, one of the modules has not discharged correctly (< 50 Vdc) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | (HGHVAC) High Vac - High AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | (LWVAC) Low Vac - Low AC voltage fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(HGHFRE) High frequency fault | (HGHFRE) High frequency fault | (HGHFRE) High frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(LWFRE) Low frequency fault | (LWFRE) Low frequency fault | (LWFRE) Low frequency fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | (FPGACMS) FPGA comms - 2 frames to the central FPGA are wrong | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | (MSTFPGA) Master FPGA - Central FPGA has not been configured correctly. Check that the 3 joined leds are turned on | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | (ACANTISL) Active anti-island - Fault produced by a variation in the measured frequency | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | (NOMOD) No modules enabled in the enabled busbars | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | (DRVSLT_1) Drive select - Wrong drive select configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | (SYNC) Synchronization - Wrong equipment configuration | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | (DCMSW) DC miswired - There is a problem with the DC measurement from central control. It occurs when the bus voltage < 100V during 30s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | (DUFB) DU feedback - The DU is not closing when required | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | (ACSCFB) ACSC feedback - Feedback from the soft charge contactor does not match the order during 5s | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | (ACSCNV) ACSC no voltage - The central soft charge contactor is closed, but buses are not changing at the expected rate (50% of the target value in 4s) | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(MODFLT) Module fault | (MODFLT) Module fault | (MODFLT) Module fault | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | (DUSTCK) DU stuck - Voltage during soft charge process is anomalous when the DU is open | Status | 1 | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown | (MVF) Medium V fuse - A medium voltage fuse has been blown |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage | (UNBVAC) Unbalanced Vac - Abnormal AC unbalanced voltage |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus | (HVDC_F) High Vdc - Overvoltage in the DC bus |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low | (LVDC_F) Low Vdc - Voltage is too low |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MSF) Modules start fault | (MSF) Modules start fault | (MSF) Modules start fault |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time | (PSANTISL) Passive anti-island - Fault produced when the frequency changes abruptly in a certain time |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side | (HWIDCDIF) HW Idc Dif - A current derivation has been detected on the panels side |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board | (MVCMS) MV comms - Failure in communication with the medium voltage measure board |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive | (DIAGTIM) Selfdiagnosis Fault - Triggered while performing auto diagnosis process, e.g.: there is no DU or the bus loading time is excessive |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection | (ERMDDIAG) Error Mod Selfdiagnosis - Triggered while performing auto diagnosis process after the equipment has stopped due to special protection |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event | (UNREC) Unable Reconnect - Inverter could not restart after the last grid event |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer | (HOMDIFLV) Hom Diff LV - A zero-sequence current (earth leakage) has been detected on the low voltage side of the transformer |  |  | Input Register |  |  |  | 2095 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state2 | pcs1_faults2 | pcs1_faults2 |  |  | Input Register |  | 2 |  | 2097 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 2 |  | /site/ess_ls | Refer to PCS Instructions
(MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization | (MVPRE) MV Premag - There was a problem during MV transformer premagnetization |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer | (OVOLIRLV) Ovc Inrush LV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the low voltage side of the transformer |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | (OVOLIRMV) Ovc Inrush MV - One of the current thresholds (overload, overcurrent, or inrush) has been overcome in the medium side of the transformer | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | (CUROFFLV) CurrentOff LV - A current measure has been detected in the low voltage side of the transformer while equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | (CUROFFMV) CurrentOff MV - A current measure has been detected in the medium voltage side of the transformer while the equipment is not running | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature | (OVTMPACM) AC mod overtemperature |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown | (GFDI) GFDI fault - description unknown |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked | (DCCNTLCK) DC contactor locked |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF | (EMRGSTP) Emergency stop - Stop pushbutton (at the main control cabinet door) has been pushed, or the DC disconnect switch is set to OFF |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range | (DRVSLT_2) Drive select - Drive select parameters out of range |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured | (INSL) Insulation - Isolation monitor measures an impedance value lower than the one configured |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected | (DTFLT) Data fault - Out-of-range parameters detected |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller | (WTCHDG) Watchdog uP - Fault in microcontroller |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(INTCMS) Internal comms | (INTCMS) Internal comms | (INTCMS) Internal comms |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors | (IMISLFT) IMI autotest - Periodic insulation monitoring devices auto test has finished with errors |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant | (NODUCNL) Do DU channels - All DU channels have been isolated, and it is not possible to establish a connection with the plant |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem | (PPCC) PPC comms - PPC and inverter communication problem |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) | (SCDUFB) Softcharge DU feedback - Softcharge timeout has expired and no feedback was received (DU softcharge contactors ordered to close, but did not) |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold | (EARTHL) GFDI current leak - GFDI current has exceeded the threshold |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent | (DUCNOV) DU channel overcurrent |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped | (EXT_OVGR) External fault/OVFR - Problem with external protections associated with DI6. External OVGR relay has tripped |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop | (REMRSTP) Remote emergency stop |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage | (DUMWR) DU channel miswired - Command to close DU has been received, but one or more channels are measuring negative voltage |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | (SWCMM) Control SW mismatch - Microcontroller and DSP software versions not compatible | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version | (MODSWI) Module SW mismatch - Not all modules have the same software version |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision | (MODHWI) Module HW mismatch - Not all modules have the same electronic board revision |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated | (DUSD) DU smoke detector - DU smoke detector activated |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost | (DUCOM_F) DU comms - Communication between DU and central control lost |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated | (GRNDCN) Ground connection - Ground contactor closed, but the insulator detector detects that pole is isolated |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address | (INVMAC) Invalid MAC address |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent | (ACOVCRR) Mod. AC overcurrent |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus | (UNBVDC) Unbal DC bus - Unbalance between high side and low side of DC bus |  |  | Input Register |  |  |  | 2097 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state3 | pcs1_faults3 | pcs1_faults3 |  |  | Input Register |  | 2 |  | 2099 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 3 |  | /site/ess_ls | Refer to PCS Instructions
(DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent | (DCOVCRR) Mod. DC overcurrent |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side | (DCOVVP) Mod. DC overvoltage (P) - Overvoltage present in DC positive side |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side | (DCOVVN) Mod. DC overvoltage (N) - Overvoltage present in DC negative side |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver | (DESR1) Desat R1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver | (DESR2P) Desat R2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver | (DESR2N) Desat R2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver | (DESR3) Desat R3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver | (DESS1) Desat S1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver | (DESS2P) Desat S2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver | (DESS2N) Desat S2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver | (DESS3) Desat S3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver | (DEST1) Desat T1 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver | (DEST2P) Desat T2 (P) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver | (DEST2N) Desat T2 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver | (DEST3) Desat T3 (N) - Desaturation in IGBT driver |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card | (DESMLT) Multiple unlock - Desaturation in more than one IGBT controller at the same time. Could indicate power failure in module control card |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost | (COMMS_F) Mod. Comms - Communication between central FPGA and module FPGA, or between module FPGA and DSP, is lost |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond | (DCCNT) Mod. DC contactor - DC contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond | (ACSCC) Mod. ACSC contactor - Module AC soft charge contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s | (ACCNT) Mod. AC contactor - Command to activate the AC contactors of the modules was sent, but did not close in 1s |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond | (LCLFB) Mod. LCL contactor feedback - LCL contactor is activated, but did not respond |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected | (TIGHW) Mod. IGBTs Temperature HW - The temperature of any IGBT overcomes 127 degrees, or IGBT temperature sensor is disconnected |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V | (GUNBDC) Mod. Great unbal DC - DC bus unbalanced more than 500V |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s | (DISFLT) Mod. Discharge fault - Module FPGA attempts to discharge the module bus and voltage did not drop below 50V in 40s |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened | (THLCL) Mod. Thermal LCL - Thermal LCL contactor of a module inductance has been opened |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage | (PW15V) Mod. Power 15V - Internal power supply of the board does not provide the adequate voltage |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C | (TAMHW) Mod. Amb Temperature HW - The temperature of the module's electronic board has overcome 85 degrees C |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation | (MIDCD) Mod. Idc derivation |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation | (MIACD) Mod. Iac derivation |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost | (DCOMS_F) Display comms - Communications between display and control board lost |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules | (DCFS) Mod. DC Fuse - Module DC voltage measure is below the average value of all modules |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s | (IUNB) Unbalance current - A module output current unbalance greater than 30A has been detected for 5s |  |  | Input Register |  |  |  | 2099 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state4 | pcs1_faults4 | pcs1_faults4 |  |  | Input Register |  | 2 |  | 2101 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 4 |  | /site/ess_ls | Refer to PCS Instructions
(TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold | (TIGBT_F) IGBTs temperature - The temperature of one or more IGBTs has overcome the maximum threshold |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold | (TAMB_F) Ambient temperature - Ambient temperature is over the maximum threshold |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) | (PWUNB_F) Pac/Pdc unbalanced - Unbalance between Pac and Pdc values. They differ a percentage defined (30% by default) |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus | (BUSUN_F) Vbus unbalanced - Unbalance between the high side and low side of DC bus |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown | (NRIAC) Iac not reached - Not enough bus voltage, or the 3 AC fuses have blown |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax | (HBMX_F) Half bus Vmax |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation | (LMVDC_F) Low module Vdc - Start command has been received but bus voltage is insufficient to start and maintain operation |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | (BACF_F) Blown AC fuse - All AC fuses have blown | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(RSV_F) Reserved fault | (RSV_F) Reserved fault | (RSV_F) Reserved fault |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control | (OCACE_F) OCAC emergency - Overcurrent has been detected in communication between module-x and central control |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control | (CCHK_F) Comms checksum - Cummunication error between module-x and central control |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan | (MDFN_F) Mod. fans - Feedback has not been received from the module fan |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error | (MDSN_F) Mod. sensor - One, or more, of the three current sensors of the module are not measuring properly, there is an offset error |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times | (MDSC_F) Mod. disabled DC - Disabled by DSP due to software or module has failed too many times |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated | (CMTHR) Mod. common thermal - Inductance in a module has overheated |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal | (INDTHR) Inductance thermal - Feedback not received from the LCL filter inductance thermal |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high | (MVTT) MV transformer temperature - Temperature in medium voltage transformer (PT100 readings) too high |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high | (AFLV) Air flow LV - Air flow temperature in the low voltage side is too high |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high | (AFMV) Air flow MV - Air flow temperature in the medium voltage side is too high |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error | (FNIMER_F) Impulsion fans - One of the impulsion fans (cyclone) has reported an error |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received | (FNXCER_F) Extract fans control - Feedback from low voltage extraction fans not received |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
(FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received | (FNXMER_F) Extract fans MV - Feedback from medium voltage extraction fans not received |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
(FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established | (FNIMCM_F) Impulsion comms - Communication with impulsion fans (cyclone) cannot be established |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
(MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome | (MVTTC) MV critical temperature trans - The temperature threshold of medium voltage transformer has been overcome |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
(CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open | (CPMVO) MV cell protection open - Protection contractor of medium voltage cell is open |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
(SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated | (SDMV) Smoke detector MV - Medium voltage smoke detector activated |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
(PRDID) Product ID invalid | (PRDID) Product ID invalid | (PRDID) Product ID invalid |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
(HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | (HOMDIFMV) - Hom Diff MV - A zero-sequence current (earth leakage) has been detected on medium voltage side of the transformer | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
(CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) | (CRBALVMV) Curr Bal LVMV - A current unbalance has been detected between low and medium voltage sides (measures do not match) |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
(NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted | (NEGPWLV) Neg Pow LV - Active power in the low voltage side of the transformer has overcome the threshold set during the time adjusted |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
(NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV | (NEGPWMV) Neg Pow MV |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
(CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBALV) Cur Unbl LV - Unbalance threshold between phases in low voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance |  |  | Input Register |  |  |  | 2101 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Unit1_Fault_state5 | pcs1_faults5 | pcs1_faults5 |  |  | Input Register |  | 2 |  | 2103 | bitfield | 0 | 4294967295 | [8 empty] | Yes | PCS 1 Fault Status 5 |  | /site/ess_ls | Refer to PCS Instructions
(CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance | (CRUNBAMV) Cur Unbl MV - Unbalance threshold between phases in medium voltage side has been overcome. Grid event occurs, voltage unbalance causes current unbalance |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
(CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules | (CRBLDSPMD) Cur Bal DSPMD - Current measurement made by central control does not match sum of measurements of all modules |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
(PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV | (PWBALLVMV) Pow Bal LVMV |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
(THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally | (THDIMV) THDi MV - The threshold of harmonic distortion (THDi) has been overcome during the timeout set internally |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
(CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome | (CPVF) Comb prot Volt Frq - One of the protection thresholds has been overcome |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
(CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed | (CLBV) Crit Low Vdc Batt - Voltage in any of the buses is too low and DU is closed |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
(IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected | (IEMB) Unbalance Bank - Difference between each input busbar voltage is higher than expected |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
(NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks | (NOBNK) No Banks Enabled - No battery banks have been enabled. There is a mistake in the setting, or there is a fault in all the banks |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
(HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit | (HVACCOMMS) Timeout communication fault with the HVAC control unit |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
(HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed | (HVACNOP_F) Two or more HVAC units are not operational, and the battery container cooling is not guranteed |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
(ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device | (ENCCOMMS) Enclosure Comms - TCP Modbus communication timeout failure with the device |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
(ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected | (ENCTEMPH) Temperature in some of the enclosure sensors or the average temperature higher than expected |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
(ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed | (ENCDIG) Enclosure Digital - Emergency stop press-button on battery enclosure has been pushed |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
(ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) | (ENC24VDC) Enclosure 24VDC - Voltage is out of range or the UPS is offline. 24V voltage is out of range when it is out of 3% (21-29V) |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
(ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode | (ENCPREDIS) Enclosure system is in gas pre-discharge mode |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
(ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted | (ENCAGREL) Enclosure Agent Release - System has acted |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
(ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected | (ENCTEMPL) Enclosure Temp Low - Average temperature in the enclosure is lower than expected |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
(TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer | (TRCOMMS) Communication timeout failure with medium voltage transformer |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
(TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated | (TRTEMP_F) Transformer over oil temperature alarm has been activated |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
(TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated | (TRPRESU_F) Transfomrer over pressure alarm has been activated |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
(TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated | (TROIL_F) Transformer oil low level alarm has been activated |  |  | Input Register |  |  |  | 2103 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
BMS maximum cell voltage | /components/catl_mbmu_summary_r:mbmu_max_cell_voltage | bms_maximum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2130 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage |  | /site/ess_ls
Stackindex of the BMS maximum cell voltage | stackindex_of_the_bms_maximum_cell_voltage | stackindex_of_the_bms_maximum_cell_voltage | Status | 1 | Input Register |  |  |  | 2131 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage BCMS Location |  | /site/ess_ls
Cluster index of the BMS maximum cell voltage | cluster_index_of_the_bms_maximum_cell_voltage | cluster_index_of_the_bms_maximum_cell_voltage | Status | 1 | Input Register |  |  |  | 2132 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Voltage BMU Location |  | /site/ess_ls
BMS minimum cell voltage | /components/catl_mbmu_summary_r:mbmu_min_cell_voltage | bms_minimum_cell_voltage | Status | 1 | Input Register | V |  | 10000 | 2133 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage |  | /site/ess_ls
Stackindex of the BMS minimum cell voltage | stackindex_of_the_bms_minimum_cell_voltage | stackindex_of_the_bms_minimum_cell_voltage | Status | 1 | Input Register |  |  |  | 2134 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage BCMS Location |  | /site/ess_ls
Cluster index of the BMS minimum cell voltage | cluster_index_of_the_bms_minimum_cell_voltage | cluster_index_of_the_bms_minimum_cell_voltage | Status | 1 | Input Register |  |  |  | 2135 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Voltage BMU Location |  | /site/ess_ls
BMS maximum cell temperature | /components/catl_mbmu_summary_r:mbmu_max_cell_temperature | bms_maximum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2136 | int16 | -32768 | 32767 | [8 empty] | Yes | Maximum Cell Temperature |  | /site/ess_ls
Stackindex of the BMS maximum cell temperature | stackindex_of_the_bms_maximum_cell_temperature | stackindex_of_the_bms_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2137 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature BCMS Location |  | /site/ess_ls
Cluster index of the BMS maximum cell temperature | cluster_index_of_the_bms_maximum_cell_temperature | cluster_index_of_the_bms_maximum_cell_temperature | Status | 1 | Input Register |  |  |  | 2138 | uint16 | 0 | 65535 | [8 empty] | Yes | Maximum Cell Temperature BMU Location |  | /site/ess_ls
BMS minimum cell temperature | /components/catl_mbmu_summary_r:mbmu_min_cell_temperature | bms_minimum_cell_temperature | Status | 1 | Input Register | °C |  | 100 | 2139 | int16 | -32768 | 32767 | [8 empty] | Yes | Minimum Cell Temperature |  | /site/ess_ls
Stackindex of the BMS minimum cell temperature | stackindex_of_the_bms_minimum_cell_temperature | stackindex_of_the_bms_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2140 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature BCMS Location |  | /site/ess_ls
Cluster index of the BMS minimum cell temperature | cluster_index_of_the_bms_minimum_cell_temperature | cluster_index_of_the_bms_minimum_cell_temperature | Status | 1 | Input Register |  |  |  | 2141 | uint16 | 0 | 65535 | [8 empty] | Yes | Minimum Cell Temperature BMU Location |  | /site/ess_ls
BMS bus voltage | bms_bus_voltage | bms_bus_voltage | Status | 1 | Input Register | V |  | 10 | 2142 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Bus Voltage |  | /site/ess_ls
BMS bus current | bms_bus_current | bms_bus_current | Status | 1 | Input Register | A |  | 10 | 2143 | int16 | -32768 | 32767 | [8 empty] | Yes | BMS Bus Current |  | /site/ess_ls
BMS SOC | /compoents/catl_mbmu_summary_r:mbmu_soc | bms_soc | Status | 1 | Input Register | % |  | 10 | 2144 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS State of Charge |  | /site/ess_ls
BMS power | bms_power | bms_power | Status | 1 | Input Register | kW |  | 10 | 2145 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Power |  | /site/ess_ls
Operation status | operation_status | operation_status | Status | 1 | Input Register |  |  |  | 2146 | bitfield | 0 | 65535 | [8 empty] | Yes | Operation Status |  | /site/ess_ls
Standby | Standby | Standby | Status | 1 | Input Register |  |  |  | 2146 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Standby
Charging | Charging | Charging | Status | 1 | Input Register |  |  |  | 2146 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Charging
Discharging | Discharging | Discharging | Status | 1 | Input Register |  |  |  | 2146 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Discharging
BMS current rechargeable capacity | bms_current_chargeable_capacity | bms_current_chargeable_capacity | Status | 1 | Input Register | kWh | 2 | 1000 | 2149 | uint32 | 0 | 4294967295 | [8 empty] | Yes | BMS Rechargeable Capacity |  | /site/ess_ls
BMS current dischargeable capacity | bms_current_dischargeable_capacity | bms_current_dischargeable_capacity | Status | 1 | Input Register | kWh | 2 | 1000 | 2151 | uint32 | 0 | 4294967295 | [8 empty] | Yes | BMS Dischargeable Capacity |  | /site/ess_ls
Circuit breaker control word | circuit_breaker_control_word | circuit_breaker_control_word | Status | 1 | Input Register |  | 2 |  | 2153 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Circuit Breaker Control Word |  | /site/ess_ls | Each bit represents the circuit status of each battery cluster, 0 = Switch Off, 1 = Switch On
Main circuit breaker status | main_circuit_breaker_status | main_circuit_breaker_status | Status | 1 | Input Register |  |  |  | 2155 | uint16 | 0 | 65535 | [8 empty] | Yes | Main Circuit Breaker Status |  | /site/ess_ls | 0 = Switch Off, 1 = Switch On
Control circuit breaker | control_circuit_breaker | control_circuit_breaker | Status | 1 | Input Register |  |  |  | 2156 | uint16 | 0 | 65535 | [8 empty] | Yes | Control Circuit Breaker Status |  | /site/ess_ls | 0 = Switch Off, 1 = Switch On
BMS Maximum charging power limit | /components/catl_bms_ems_r:bms_max_charge_allowed | bms_maximum_charging_power_limit | Status | 1 | Input Register | kW |  |  | 2157 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Maximum Charging Power Limit |  | /site/ess_ls
BMS Maximum discharging power limit | /components/catl_bms_ems_r:bms_max_discharge_allowed | bms_maximum_discharging_power_limit | Status | 1 | Input Register | kW |  |  | 2158 | uint16 | 0 | 65535 | [8 empty] | Yes | BMS Maximum Discharging Power Limit |  | /site/ess_ls
Power limit state 1 | power_limit_state1 | power_limit_state1 | Status | 1 | Input Register |  | 2 |  | 2159 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Power Limit Status 1 |  | /site/ess_ls
Charge overvoltage half power limit of cell | Charge overvoltage half power limit of cell | Charge overvoltage half power limit of cell | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Charge overvoltage half power limit of cluster | Charge overvoltage half power limit of cluster | Charge overvoltage half power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Charge under-temp half power limit | Charge under-temp half power limit | Charge under-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge over-temp half power limit | Charge over-temp half power limit | Charge over-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge undervoltage half power limit of cell | Discharge undervoltage half power limit of cell | Discharge undervoltage half power limit of cell | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Discharge undervoltage half power limit of cluster | Discharge undervoltage half power limit of cluster | Discharge undervoltage half power limit of cluster | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Discharge under-temp half power limit | Discharge under-temp half power limit | Discharge under-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Discharge over-temp half power limit | Discharge over-temp half power limit | Discharge over-temp half power limit | Status | 1 | Input Register |  |  |  | 2159 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Power limit state 2 | power_limit_state2 | power_limit_state2 |  |  | Input Register |  | 2 |  | 2161 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Power Limit Status 2 |  | /site/ess_ls
Charge overvoltage zero power limit of cell | Charge overvoltage zero power limit of cell | Charge overvoltage zero power limit of cell | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Charge overvoltage zero power limit of cluster | Charge overvoltage zero power limit of cluster | Charge overvoltage zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Charge overcurrent zero power limit of cluster | Charge overcurrent zero power limit of cluster | Charge overcurrent zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Charge overcurrent zero power limit of array | Charge overcurrent zero power limit of array | Charge overcurrent zero power limit of array | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Charge under-temp zero power limit | Charge under-temp zero power limit | Charge under-temp zero power limit | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge over-temp zero power limit | Charge over-temp zero power limit | Charge over-temp zero power limit | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge undervoltage zero power limit of cell | Discharge undervoltage zero power limit of cell | Discharge undervoltage zero power limit of cell | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Discharge undervoltage zero power limit of cluster | Discharge undervoltage zero power limit of cluster | Discharge undervoltage zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Discharge overcurrent zero power limit of cluster | Discharge overcurrent zero power limit of cluster | Discharge overcurrent zero power limit of cluster | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Discharge overcurrent zero power limit of array | Discharge overcurrent zero power limit of array | Discharge overcurrent zero power limit of array | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Discharge under-temp zero power limit | Discharge under-temp zero power limit | Discharge under-temp zero power limit | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Discharge over-temp zero power limit | Discharge over-temp zero power limit | Discharge over-temp zero power limit | Status | 1 | Input Register |  |  |  | 2161 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
BMS alarm state | bms_alarms | bms_alarms | Status | 1 | Input Register |  | 2 |  | 2163 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Alarm Status |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | SOC Low Warning 1 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | SOC Low Warning 2 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | SOC Low Warning 3 | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Current Overlimit Warning | Current Overlimit Warning | Current Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Single Cell Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Single Cell Temperature Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
System Voltage Overlimit Warning | System Voltage Overlimit Warning | System Voltage Overlimit Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
System Voltage Underlimit Warning | System Voltage Underlimit Warning | System Voltage Underlimit Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Inner Communication Warning | Inner Communication Warning | Inner Communication Warning | Status | 1 | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Cell Extreme Temperature Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Cell Extreme Voltage Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
EMS Heartbeat Warning | EMS Heartbeat Warning | EMS Heartbeat Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
SOC Difference Warning | SOC Difference Warning | SOC Difference Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Fire Fault Level 2 Warning | Fire Fault Level 2 Warning | Fire Fault Level 2 Warning |  |  | Input Register |  |  |  | 2163 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
BMS fault state 1 | bms_faults1 | bms_faults1 | Status | 1 | Input Register |  | 2 |  | 2165 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 1 |  | /site/ess_ls
Insulation error protection | Insulation error protection | Insulation error protection | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Discharge undervoltage LV1 protection of cell | Discharge undervoltage LV1 protection of cell | Discharge undervoltage LV1 protection of cell | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Charge overvoltage LV1 protection of cell | Charge overvoltage LV1 protection of cell | Charge overvoltage LV1 protection of cell | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Discharge undervoltage LV1 protection of cluster | Discharge undervoltage LV1 protection of cluster | Discharge undervoltage LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge overvoltage LV1 protection of cluster | Charge overvoltage LV1 protection of cluster | Charge overvoltage LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge overcurrent LV1 protection of cluster | Discharge overcurrent LV1 protection of cluster | Discharge overcurrent LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Charge overcurrent LV1 protection of cluster | Charge overcurrent LV1 protection of cluster | Charge overcurrent LV1 protection of cluster | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Discharge overcurrent LV1 protection of array | Discharge overcurrent LV1 protection of array | Discharge overcurrent LV1 protection of array | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Charge overcurrent LV1 protection of array | Charge overcurrent LV1 protection of array | Charge overcurrent LV1 protection of array | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Low-temp LV1 protection | Low-temp LV1 protection | Low-temp LV1 protection | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
High-temp LV1 protection | High-temp LV1 protection | High-temp LV1 protection | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Self-protection of BMS | Self-protection of BMS | Self-protection of BMS | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
E-stop fault | E-stop fault | E-stop fault | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Self-protection of EMMU | Self-protection of EMMU | Self-protection of EMMU | Status | 1 | Input Register |  |  |  | 2165 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
BMS fault state 2 | bms_faults2 | bms_faults2 |  |  | Input Register |  | 2 |  | 2167 | bitfield | 0 | 4294967295 | [8 empty] | Yes | BMS Fault Status 2 |  | /site/ess_ls
Discharge undervoltage LV2 protection of cell | Discharge undervoltage LV2 protection of cell | Discharge undervoltage LV2 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Charge overvoltage LV2 protection of cell | Charge overvoltage LV2 protection of cell | Charge overvoltage LV2 protection of cell | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Discharge undervoltage LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Discharge overcurrent LV2 protection of cluster | Discharge overcurrent LV2 protection of cluster | Discharge overcurrent LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Charge overcurrent LV2 protection of cluster | Charge overcurrent LV2 protection of cluster | Charge overcurrent LV2 protection of cluster | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Discharge overcurrent LV2 protection of array | Discharge overcurrent LV2 protection of array | Discharge overcurrent LV2 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Charge overcurrent LV2 protection of array | Charge overcurrent LV2 protection of array | Charge overcurrent LV2 protection of array | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Low-temp LV2 protection | Low-temp LV2 protection | Low-temp LV2 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
High-temp LV2 protection | High-temp LV2 protection | High-temp LV2 protection | Status | 1 | Input Register |  |  |  | 2167 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Number of Battery Racks in Service | racks_in_service | racks_in_service |  |  | Input Register |  |  |  | 2199 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Battery Racks Online |  | /site/ess_ls
Battery Rack No. 1 Voltage | /components/catl_@@BMS_ID@@/sbmu_voltage | sbmu_1_battery_voltage |  |  | Input Register | V | 1 |  | 2200 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Voltage |  | /site/ess_ls
Battery Rack No. 1 Current | /components/catl_@@BMS_ID@@/sbmu_current | sbmu_1_battery_current |  |  | Input Register | A | 1 |  | 2201 | int16 | -32768 | 32767 | [8 empty] | Yes | Battery Rack 1 Current |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage | /components/catl_@@BMS_ID@@/sbmu_max_cell_voltage | sbmu_1_max_cell_voltage |  |  | Input Register | V | 1 |  | 2202 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Voltage Position | rack_1_max_cell_voltage_position | sbmu_1_max_cell_voltage_position |  |  | Input Register |  | 1 |  | 2203 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage | /components/catl_@@BMS_ID@@/sbmu_min_cell_voltage | sbmu_1_min_cell_voltage |  |  | Input Register | V | 1 |  | 2204 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Min Cell Voltage Position | rack_1_min_cell_voltage_position | sbmu_1_min_cell_voltage_position |  |  | Input Register |  | 1 |  | 2205 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Voltage Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Voltage | /components/catl_@@BMS_ID@@/sbmu_avg_cell_voltage | sbmu_1_avg_cell_voltage |  |  | Input Register | V | 1 |  | 2206 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Average Cell Voltage |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature | /components/catl_@@BMS_ID@@/sbmu_max_cell_temperature | sbmu_1_max_cell_temperature |  |  | Input Register | °C | 1 | 100 | 2207 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Max Cell Temperature Position | rack_1_max_cell_temperature_position | sbmu_1_max_cell_temperature_position |  |  | Input Register |  | 1 |  | 2208 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Maximum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature | /components/catl_@@BMS_ID@@/sbmu_min_cell_temperature | sbmu_1_min_cell_temperature |  |  | Input Register | °C | 1 | 100 | 2209 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 Min Cell Temperature Position | rack_1_min_cell_temperature_position | sbmu_1_min_cell_temperature_position |  |  | Input Register |  | 1 |  | 2210 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Minimum Cell Temperature Location |  | /site/ess_ls
Battery Rack No. 1 Avg Cell Temperature | /components/catl_@@BMS_ID@@/sbmu_avg_cell_temperature | sbmu_1_avg_cell_temperature |  |  | Input Register | °C | 1 | 100 | 2211 | uint16 | 0 | 65535 | [8 empty] | Yes | Battery Rack 1 Average Cell Temperature |  | /site/ess_ls
Battery Rack No. 1 alarm state 1 | sbmu_1_alarms1 | sbmu_1_alarms1 |  |  | Input Register |  | 2 |  | 2212 | bitfield | 0 | [9 empty] | Yes | Battery Rack 1 Alarm Status 1 |  | /site/ess_ls
Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 | Single Cell Overvoltage Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 | Single Cell Overvoltage Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 | Single Cell Overvoltage Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 | Single Cell Undervoltage Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 | Single Cell Undervoltage Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 | Single Cell Undervoltage Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 | Single Cell Overtemperature Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 | Single Cell Overtemperature Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 | Single Cell Overtemperature Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 | Single Cell Undertemperature Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 | Single Cell Undertemperature Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 | Single Cell Undertemperature Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
SOC Low Warning 1 | SOC Low Warning 1 | SOC Low Warning 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
SOC Low Warning 2 | SOC Low Warning 2 | SOC Low Warning 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
SOC Low Warning 3 | SOC Low Warning 3 | SOC Low Warning 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
TMS Fault Level 1 | TMS Fault Level 1 | TMS Fault Level 1 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
TMS Fault Level 2 | TMS Fault Level 2 | TMS Fault Level 2 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
TMS Fault Level 3 | TMS Fault Level 3 | TMS Fault Level 3 |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
Charge Overcurrent Warning | Charge Overcurrent Warning | Charge Overcurrent Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
Discharge Overcurrent Warning | Discharge Overcurrent Warning | Discharge Overcurrent Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Temp Difference Warning | Temp Difference Warning | Temp Difference Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Cell Extreme Temperature Warning | Cell Extreme Temperature Warning | Cell Extreme Temperature Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 21 | /site/ess_ls
Cell Extreme Voltage Warning | Cell Extreme Voltage Warning | Cell Extreme Voltage Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 22 | /site/ess_ls
Extreme Total Voltage Warning | Extreme Total Voltage Warning | Extreme Total Voltage Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 23 | /site/ess_ls
Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault | Master Positive Relay Close Fail Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 24 | /site/ess_ls
Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault | Master Negative Relay Close Fail Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 25 | /site/ess_ls
Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault | Master Positive Relay Stuck Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 26 | /site/ess_ls
Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault | Master Negative Relay Stuck Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 27 | /site/ess_ls
Power Loss Fault | Power Loss Fault | Power Loss Fault |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 28 | /site/ess_ls
Balance Warning | Balance Warning | Balance Warning |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 29 | /site/ess_ls
Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) | Inner Communication Fault (CCAN) |  |  | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 30 | /site/ess_ls
Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Inner Communication Fault (SCAN) | Input Register |  |  |  | 2212 | bit | [10 empty] | Yes |  | 31 | /site/ess_ls
Battery Rack No. 1 alarm state 2 | sbmu_1_alarms2 | sbmu_1_alarms2 |  |  | Input Register |  | 2 |  | 2214 | bitfield | [10 empty] | Yes | Battery Rack 1 Alarm Status 2 |  | /site/ess_ls
Current Sensor Abnormal Fault | Current Sensor Abnormal Fault | Current Sensor Abnormal Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault | Single Cell Voltage Sampling Abnormal Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault | Module Temperature Sampling Abnormal Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
High Voltage Circuit Open Fault | High Voltage Circuit Open Fault | High Voltage Circuit Open Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
MSD Fault | MSD Fault | MSD Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Isolate Switch Fault | Isolate Switch Fault | Isolate Switch Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Rack Fuse Fault | Rack Fuse Fault | Rack Fuse Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
TMS Communication Fault | TMS Communication Fault | TMS Communication Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
TMS Mode Conflict Fault | TMS Mode Conflict Fault | TMS Mode Conflict Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Fire Fault Level 1 | Fire Fault Level 2 | Fire Fault Level 3 |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Temperature Sensor Alarm | Temperature Sensor Alarm | Temperature Sensor Alarm |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls
Smoke Sensor Alarm | Smoke Sensor Alarm | Smoke Sensor Alarm |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Aerosol State Fault | Aerosol State Fault | Aerosol State Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Aerosol Close Fault | Aerosol Close Fault | Aerosol Close Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Aerosol Open Fault | Aerosol Open Fault | Aerosol Open Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
Rack Switch State | Rack Switch State | Rack Switch State |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
Control Box Overtemperature Fault | Control Box Overtemperature Fault | Control Box Overtemperature Fault |  |  | Input Register |  |  |  | 2214 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
sbmu_1 |  | sbmu_2 |  |  |  |  | 15 |  | 2216 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2216 - 2231 for sbmu_2 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_3 |  |  |  |  | 15 |  | 2232 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2232 - 2247 for sbmu_3 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_4 |  |  |  |  | 15 |  | 2248 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2248 - 2263 for sbmu_4 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_5 |  |  |  |  | 15 |  | 2264 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2264 - 2279 for sbmu_5 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_6 |  |  |  |  | 15 |  | 2280 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2280 - 2295 for sbmu_6 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_7 |  |  |  |  | 15 |  | 2296 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2296 - 2311 for sbmu_7 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_8 |  |  |  |  | 15 |  | 2312 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2312 - 2327 for sbmu_8 |  | /site/ess_ls |  |  | 2200
sbmu_1 |  | sbmu_9 |  |  |  |  | 15 |  | 2328 | repeat | [10 empty] | Yes | Repeat registers 2200 - 2214 into 2328 - 2343 for sbmu_9 |  | /site/ess_ls |  |  | 2200
BAMS online status |  | offline_bams | Status | 1 | Input Register |  |  |  | 2811 | bitfield | 0 | 65535 | [8 empty] | Yes | BAMS Status |  | /site/ess_ls |  | 0 = online 1 = offline
BAMS 1 |  | BAMS 1 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | BAMS 1
BAMS 2 |  | BAMS 2 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | BAMS 2
BAMS 3 |  | BAMS 3 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | BAMS 3
BAMS 4 |  | BAMS 4 | Status | 1 | Input Register |  |  |  | 2811 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | BAMS 4
Air conditioner online status |  | offline_air_conditioners | Status | 1 | Input Register |  |  |  | 2812 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner Status |  | /site/ess_ls |  | 0 = online 1 = offline
Air Conditioner 1 |  | Air Conditioner 1 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Air Conditioner 1
Air Conditioner 2 |  | Air Conditioner 2 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Air Conditioner 2
Air Conditioner 3 |  | Air Conditioner 3 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Air Conditioner 3
Air Conditioner 4 |  | Air Conditioner 4 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Air Conditioner 4
Air Conditioner 5 |  | Air Conditioner 5 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Air Conditioner 5
Air Conditioner 6 |  | Air Conditioner 6 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls | Air Conditioner 6
Air Conditioner 7 |  | Air Conditioner 7 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls | Air Conditioner 7
Air Conditioner 8 |  | Air Conditioner 8 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls | Air Conditioner 8
Air Conditioner 9 |  | Air Conditioner 9 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls | Air Conditioner 9
Air Conditioner 10 |  | Air Conditioner 10 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls | Air Conditioner 10
Air Conditioner 11 |  | Air Conditioner 11 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 10 | /site/ess_ls | Air Conditioner 11
Air Conditioner 12 |  | Air Conditioner 12 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls | Air Conditioner 12
Air Conditioner 13 |  | Air Conditioner 13 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls | Air Conditioner 13
Air Conditioner 14 |  | Air Conditioner 14 | Status | 1 | Input Register |  |  |  | 2812 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls | Air Conditioner 14
Temperature and humidity sensor online status |  | offline_temperature_and_humidity_sensors | Status | 1 | Input Register |  |  |  | 2813 | bitfield | 0 | 65535 | [8 empty] | Yes | Temperature and Humidty Sensor Status |  | /site/ess_ls |  | 0 = online 1 = offline
Sensor 1 |  | Sensor 1 | Status | 1 | Input Register |  |  |  | 2813 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Sensor 1
Sensor 2 |  | Sensor 2 | Status | 1 | Input Register |  |  |  | 2813 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Sensor 2
Sensor 3 |  | Sensor 3 | Status | 1 | Input Register |  |  |  | 2813 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Sensor 3
Meter online status |  | meter_online_status | Status | 1 | Input Register |  |  |  | 2814 | uint16 | 0 | 65535 | [8 empty] | Yes | Meter Status |  | /site/ess_ls
Gas sensor online status |  | gas_sensor_online_status | Status | 1 | Input Register |  |  |  | 2815 | uint16 | 0 | 65535 | [8 empty] | Yes | Gas Sensor Status |  | /site/ess_ls
Number of online BAMS |  | number_of_online_bams | Status | 1 | Input Register |  |  |  | 2816 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of BAMS Online |  | /site/ess_ls
Number of online air conditioners |  | number_of_online_air_conditioners | Status | 1 | Input Register |  |  |  | 2817 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Air Conditioners Online |  | /site/ess_ls
Number of online temperature and humidity |  | number_of_online_temperature_and_humidity | Status | 1 | Input Register |  |  |  | 2818 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Temperature and Humidity Sensors Online |  | /site/ess_ls
Number of online Meters |  | number_of_online_meters | Status | 1 | Input Register |  |  |  | 2819 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Meters Online |  | /site/ess_ls
Number of online gas sensors |  | number_of_online_gas_sensors | Status | 1 | Input Register |  |  |  | 2820 | uint16 | 0 | 65535 | [8 empty] | Yes | Number of Gas Sensors Online |  | /site/ess_ls
Environmental alarm status 1 |  | emmu_alarms1 | Status | 1 | Input Register |  | 2 |  | 2821 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Environmental Alarm Status 1 |  | /site/ess_ls |  | 0 = return 1 = occur
Access control state of AC panel |  | Access control state of AC panel | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
Access control state of DC panel |  | Access control state of DC panel | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
Access control state of SYS panel |  | Access control state of SYS panel | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
SPD fault (AC) |  | SPD fault (AC) | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
FSS fault |  | FSS fault | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Single fire alarm warning |  | Single fire alarm warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Gas detector H2-1 abnormal |  | Gas detector H2-1 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 11 | /site/ess_ls
Gas detector H2-2 abnormal |  | Gas detector H2-2 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 12 | /site/ess_ls
Gas detector CO-1 abnormal |  | Gas detector CO-1 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 13 | /site/ess_ls
Gas detector CO-2 abnormal |  | Gas detector CO-2 abnormal | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 14 | /site/ess_ls
HVAC high-temp warning |  | HVAC high-temp warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 15 | /site/ess_ls
HVAC low-temp warning |  | HVAC low-temp warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 16 | /site/ess_ls
HVAC high humidity warning |  | HVAC high humidity warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 17 | /site/ess_ls
HVAC low humidity warning |  | HVAC low humidity warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 18 | /site/ess_ls
HVAC high pressure warning |  | HVAC high pressure warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 19 | /site/ess_ls
Exhaust air high-temp warning |  | Exhaust air high-temp warning | Status | 1 | Input Register |  |  |  | 2821 | bit | [10 empty] | Yes |  | 20 | /site/ess_ls
Environmental alarm status 2 |  | emmu_alarms2 |  |  | Input Register |  | 2 |  | 2823 | bitfield | 0 | 4294967295 | [8 empty] | Yes | Environmental Alarm Status 2 |  | /site/ess_ls |  | 0 = return 1 = occur
HVAC communication error warning |  | HVAC communication error warning | Status | 1 | Input Register |  |  |  | 2823 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
UPS communication error warning |  | UPS communication error warning | Status | 1 | Input Register |  |  |  | 2823 | bit | [10 empty] | Yes |  | 9 | /site/ess_ls
Emmu fault status |  | emmu_faults | Status | 1 | Input Register |  | 2 |  | 2825 | bitfield | 0 | 4294967295 | [8 empty] | Yes | DIdevice Alarm Status |  | /site/ess_ls |  | 0 = return 1 = occur
Fire composite alarm protection |  | Fire composite alarm protection | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls
E-stop of AC panel |  | E-stop of AC panel | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls
E-stop of system |  | E-stop of system | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls
Remote E-stop |  | Remote E-stop | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls
Water flood sensor |  | Water flood sensor | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls
Gas detector H2-1 abnormal |  | Gas detector H2-1 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 5 | /site/ess_ls
Gas detector H2-2 abnormal |  | Gas detector H2-2 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 6 | /site/ess_ls
Gas detector CO-1 abnormal |  | Gas detector CO-1 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 7 | /site/ess_ls
Gas detector CO-2 abnormal |  | Gas detector CO-2 abnormal | Status | 1 | Input Register |  |  |  | 2825 | bit | [10 empty] | Yes |  | 8 | /site/ess_ls
Carbon monoxide concentration |  | carbon_monoxide_concentration | Status | 1 | Input Register | ppm | 2 | 100 | 2900 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Carbon Monoxide Concentration |  | /site/ess_ls
Hydrogen concentration |  | hydrogen_concentration | Status | 1 | Input Register | ppm | 2 | 100 | 2902 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Hydrogen Concentration |  | /site/ess_ls
Oxygen concentration |  | oxygen_concentration | Status | 1 | Input Register | ppm | 2 | 100 | 2904 | uint32 | 0 | 4294967295 | [8 empty] | Yes | Oxygen Concentration |  | /site/ess_ls
Carbon monoxide alarm status |  | carbon_monoxide_alarm_status | Status | 1 | Input Register |  |  |  | 2906 | uint16 | 0 | 65535 | [8 empty] | Yes | Carbon Monoxide Alarm Status |  | /site/ess_ls | 0 = normal state, 1 = alarm state
Hydrogen alarm status |  | hydrogen_alarm_status | Status | 1 | Input Register |  |  |  | 2907 | uint16 | 0 | 65535 | [8 empty] | Yes | Hydrogen Alarm Status |  | /site/ess_ls | 0 = normal state, 1 = alarm state
Oxygen alarm status |  | oxygen_alarm_status | Status | 1 | Input Register |  |  |  | 2908 | uint16 | 0 | 65535 | [8 empty] | Yes | Oxygen Alarm Status |  | /site/ess_ls | 0 = normal state, 1 = alarm state
Temperature reading of temperature and humidty sensor No. 1 |  | temperature_reading_of_temperature_and_humidty_sensor_no_1 | Status | 1 | Input Register | °C |  | 100 | 2930 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 1 Temperature |  | /site/ess_ls
Temperature reading of temperature and humidty sensor No. 2 |  | temperature_reading_of_temperature_and_humidty_sensor_no_2 | Status | 1 | Input Register | °C |  | 100 | 2931 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 2 Temperature |  | /site/ess_ls
Temperature reading of temperature and humidty sensor No. 3 |  | temperature_reading_of_temperature_and_humidty_sensor_no_3 | Status | 1 | Input Register | °C |  | 100 | 2932 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 3 Temperature |  | /site/ess_ls
Humidity reading of temperature and humidty sensor No. 1 |  | humidity_reading_of_temperature_and_humidty_sensor_no_1 | Status | 1 | Input Register | %RH |  | 100 | 2933 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 1 Humidity |  | /site/ess_ls
Humidity reading of temperature and humidty sensor No. 2 |  | humidity_reading_of_temperature_and_humidty_sensor_no_2 | Status | 1 | Input Register | %RH |  | 100 | 2934 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 2 Humidity |  | /site/ess_ls
Humidity reading of temperature and humidty sensor No. 3 |  | humidity_reading_of_temperature_and_humidty_sensor_no_3 | Status | 1 | Input Register | %RH |  | 100 | 2935 | int16 | -32768 | 32767 | [8 empty] | Yes | Sensor 3 Humidity |  | /site/ess_ls
Air conditioner temperature limit 1 |  | air_conditioner_temperature_limit_1 | Status | 1 | Input Register | °C |  | 100 | 3000 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner Temperature Limit 1 |  | /site/ess_ls
Air conditioner temperature limit 2 |  | air_conditioner_temperature_limit_2 | Status | 1 | Input Register | °C |  | 100 | 3001 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner Temperature Limit 2 |  | /site/ess_ls
Air conditioner temperature limit 3 |  | air_conditioner_temperature_limit_3 | Status | 1 | Input Register | °C |  | 100 | 3002 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner Temperature Limit 3 |  | /site/ess_ls
Air conditioner1 current mode |  | air_conditioner_1_current_mode | Status | 1 | Input Register |  |  |  | 3003 | bitfield | 0 | 65535 | [8 empty] | Yes | Air Conditioner 1 Mode |  | /site/ess_ls
Self-control |  | Self-control | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 0 | /site/ess_ls | Self-control
Cooling |  | Cooling | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 1 | /site/ess_ls | Cooling
Supply Air |  | Supply Air | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 2 | /site/ess_ls | Supply Air
Standby |  | Standby | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 3 | /site/ess_ls | Standby
Heating |  | Heating | Status | 1 | Input Register |  |  |  | 3003 | bit | [10 empty] | Yes |  | 4 | /site/ess_ls | Heating
Air conditioner1 temperature |  | air_conditioner_1_temperature | Status | 1 | Input Register | °C |  | 100 | 3004 | int16 | -32768 | 32767 | [8 empty] | Yes | Air Conditioner 1 Temperature |  | /site/ess_ls
Air conditioner1 humidity |  | air_conditioner_1_humidity | Status | 1 | Input Register | %RH |  | 100 | 3005 | uint16 | 0 | 65535 | [8 empty] | Yes | Air Conditioner 1 Humidity |  | /site/ess_ls
air_conditioner_1 |  | air_conditioner_2 |  |  |  |  | 2 |  | 3006 | repeat | [10 empty] | Yes | Repeat registers 3003 - 3005 into 3006 - 3008 for air conditioner 2 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_3 |  |  |  |  | 2 |  | 3009 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3009 - 3011 for air conditioner 3 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_4 |  |  |  |  | 2 |  | 3012 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3012 - 3014 for air conditioner 4 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_5 |  |  |  |  | 2 |  | 3015 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3015 - 3017 for air conditioner 5 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_6 |  |  |  |  | 2 |  | 3018 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3018 - 3020 for air conditioner 6 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_7 |  |  |  |  | 2 |  | 3021 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3021 - 3023 for air conditioner 7 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_8 |  |  |  |  | 2 |  | 3024 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3024 - 3026 for air conditioner 8 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_9 |  |  |  |  | 2 |  | 3027 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3027 - 3029 for air conditioner 9 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_10 |  |  |  |  | 2 |  | 3030 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3030 - 3032 for air conditioner 10 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_11 |  |  |  |  | 2 |  | 3033 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3033 - 3035 for air conditioner 11 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_12 |  |  |  |  | 2 |  | 3036 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3036 - 3038 for air conditioner 12 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_13 |  |  |  |  | 2 |  | 3039 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3039 - 3041 for air conditioner 13 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_14 |  |  |  |  | 2 |  | 3042 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3042 - 3044 for air conditioner 14 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_15 |  |  |  |  | 2 |  | 3045 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3045 - 3047 for air conditioner 15 |  | /site/ess_ls |  |  | 3003
air_conditioner_1 |  | air_conditioner_16 |  |  |  |  | 2 |  | 3048 | repeat | [11 empty] | Repeat registers 3003 - 3005 into 3048 - 3050 for air conditioner 16 |  | /site/ess_ls |  |  | 3003