## TX10 Range (100)
Device Name | FlexGen Fleet Manager | Customer | Broad Reach Power
Device Protocol | DNP3 | Location | BRP ERCOT NOC
Device Protocol Version | 0.6 |  |  | Notes: Holding Register = AnOPInt32, Input Register = analog, Coil = CROB, Discrete Input = binary | [14 empty] | CLIENT | SERVER
Device ID String | outstation
Device IP Address (if TCP) | 172.3.27.150
Device Port (502 typical) | 20009
Master_Address | 200
Station_Address | 10
frequency | 10000
local uri | /local_##SITE_NAME##
Name | Source Device | Type | Version | Register Type | Unit | Words | Bus Scale | Scale | Address | Object | Variation | Evariation | Data Type | Range Start | Range End | Engineering Range Start | Engineering Range End | Description | Control Narrative for Register | Reg ID | URI | ID | Include | Stripped Address | Address2 | Repeat | Bit | FIMS Scale
Generation Non-Spin Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 100 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_ns_responsibility | /components/pueblo1 | gen_ns_responsibility | Yes
Generation Non-Spin Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 101 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_ns_requirement | /components/pueblo1 | gen_ns_requirement | Yes
Generation Non-Spin Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 102 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | gen_ns_schedule | /components/pueblo1 | gen_ns_schedule | Yes
Generation Regulation Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 103 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_reg_down_responsibility | /components/pueblo1 | gen_reg_down_responsibility | Yes
Generation Regulation Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 104 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_reg_down_requirement | /components/pueblo1 | gen_reg_down_requirement | Yes
Generation Regulation Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 105 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | gen_reg_down_participation | /components/pueblo1 | gen_reg_down_participation | Yes
Generation Responsive Reserve Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 106 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_rrs_responsibility | /components/pueblo1 | gen_rrs_responsibility | Yes
Generation Responsive Reserve Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 107 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_rrs_requirement | /components/pueblo1 | gen_rrs_requirement | Yes
Generation Responsive Reserve Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 108 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | gen_rrs_schedule | /components/pueblo1 | gen_rrs_schedule | Yes
Generation Regulation Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 109 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_reg_up_responsibility | /components/pueblo1 | gen_reg_up_responsibility | Yes
Generation Regulation Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 110 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_reg_up_requirement | /components/pueblo1 | gen_reg_up_requirement | Yes
Generation Regulation Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 111 | 41 |  |  | int32 |  |  |  |  | ratio of reg up responsibility to total responsibility, monitoring only |  | gen_reg_up_participation_factor | /components/pueblo1 | gen_reg_up_participation_factor | Yes
Generation FRRS Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 112 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_frrs_down_responsibility | /components/pueblo1 | gen_frrs_down_responsibility | Yes
Generation FRRS Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 113 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_frrs_down_requirement | /components/pueblo1 | gen_frrs_down_requirement | Yes
Generation FRRS Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 114 | 41 |  |  | int32 |  |  |  |  | ratio of FRRS down responsibility to total responsibility, monitoring only |  | gen_frrs_down_participation_factor | /components/pueblo1 | gen_frrs_down_participation_factor | Yes
Generation FRRS Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 115 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_frrs_up_responsibility | /components/pueblo1 | gen_frrs_up_responsibility | Yes
Generation FRRS Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 116 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_frrs_up_requirement | /components/pueblo1 | gen_frrs_up_requirement | Yes
Generation FRRS Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 117 | 41 |  |  | int32 |  |  |  |  | ratio of FRRS up responsibility to total responsibility, monitoring only |  | gen_frrs_up_participation_factor | /components/pueblo1 | gen_frrs_up_participation_factor | Yes
Generation Locational Marginal Pricing | ERCOT | Analog Out | 0.6 | AnOPInt32 | USD |  |  | 1000 | 118 | 41 |  |  | int32 | [6 empty] | gen_lmp | /components/pueblo1 | gen_lmp | Yes
Generation Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 119 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT SCED |  | gen_basepoint | /components/pueblo1 | gen_basepoint | Yes
Generation Updated Desired Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 120 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT LFC |  | gen_updated_basepoint | /components/pueblo1 | gen_updated_basepoint | Yes
Generation Resource Status | APX | Analog Out | 0.6 | AnOPInt32 | coded |  |  |  | 121 | 41 |  |  | int32 | [6 empty] | gen_resource_status | /components/pueblo1 | gen_resource_status | Yes
Controllable Load Non-Spin Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 130 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_ns_responsibility | /components/pueblo1 | load_ns_responsibility | Yes
Controllable Load Non-Spin Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 131 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_ns_requirement | /components/pueblo1 | load_ns_requirement | Yes
Controllable Load Non-Spin Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 132 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | load_ns_schedule | /components/pueblo1 | load_ns_schedule | Yes
Controllable Load Regulation Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 133 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_reg_down_responsibility | /components/pueblo1 | load_reg_down_responsibility | Yes
Controllable Load Regulation Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 134 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_reg_down_requirement | /components/pueblo1 | load_reg_down_requirement | Yes
Controllable Load Regulation Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 135 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_reg_down_participation | /components/pueblo1 | load_reg_down_participation | Yes
Controllable Load Responsive Reserve Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 136 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_rrs_responsibility | /components/pueblo1 | load_rrs_responsibility | Yes
Controllable Load Responsive Reserve Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 137 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_rrs_requirement | /components/pueblo1 | load_rrs_requirement | Yes
Controllable Load Responsive Reserve Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 138 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | load_rrs_schedule | /components/pueblo1 | load_rrs_schedule | Yes
Controllable Load Regulation Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 139 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_reg_up_responsibility | /components/pueblo1 | load_reg_up_responsibility | Yes
Controllable Load Regulation Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 140 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_reg_up_requirement | /components/pueblo1 | load_reg_up_requirement | Yes
Controllable Load Regulation Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 141 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_reg_up_participation_factor | /components/pueblo1 | load_reg_up_participation_factor | Yes
Controllable Load FRRS Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 142 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_frrs_down_responsibility | /components/pueblo1 | load_frrs_down_responsibility | Yes
Controllable Load FRRS Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 143 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_frrs_down_requirement | /components/pueblo1 | load_frrs_down_requirement | Yes
Controllable Load FRRS Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 144 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_frrs_down_participation_factor | /components/pueblo1 | load_frrs_down_participation_factor | Yes
Controllable Load FRRS Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 145 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_frrs_up_responsibility | /components/pueblo1 | load_frrs_up_responsibility | Yes
Controllable Load FRRS Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 146 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_frrs_up_requirement | /components/pueblo1 | load_frrs_up_requirement | Yes
Controllable Load FRRS Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 147 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_frrs_up_participation_factor | /components/pueblo1 | load_frrs_up_participation_factor | Yes
Controllable Load Locational Marginal Pricing | ERCOT | Analog Out | 0.6 | AnOPInt32 | USD |  |  | 1000 | 148 | 41 |  |  | int32 | [6 empty] | load_lmp | /components/pueblo1 | load_lmp | Yes
Controllable Load Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 149 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT SCED |  | load_basepoint | /components/pueblo1 | load_basepoint | Yes
Controllable Load Updated Desired Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 150 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT LFC |  | load_updated_basepoint | /components/pueblo1 | load_updated_basepoint | Yes
Controllable Load Resource Status | APX | Analog Out | 0.6 | AnOPInt32 | coded |  |  |  | 151 | 41 |  |  | int32 | [6 empty] | load_resource_status | /components/pueblo1 | load_resource_status | Yes
Calculated Generation RURS | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 152 | 41 |  |  | int32 | [6 empty] | calculated_gen_rurs | /components/pueblo1 | calculated_gen_rurs | Yes
Calculated Generation RUPF | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 153 | 41 |  |  | int32 | [6 empty] | calculated_gen_rupf | /components/pueblo1 | calculated_gen_rupf | Yes
Calculated Generation RDRS | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 154 | 41 |  |  | int32 | [6 empty] | calculated_gen_rdrs | /components/pueblo1 | calculated_gen_rdrs | Yes
Calculated Generation RDPF | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 155 | 41 |  |  | int32 | [6 empty] | calculated_gen_rdpf | /components/pueblo1 | calculated_gen_rdpf | Yes
Calculated Load RURS | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 156 | 41 |  |  | int32 | [6 empty] | calculated_load_rurs | /components/pueblo1 | calculated_load_rurs | Yes
Calculated Load RUPF | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 157 | 41 |  |  | int32 | [6 empty] | calculated_load_rupf | /components/pueblo1 | calculated_load_rupf | Yes
Calculated Load RDRS | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 158 | 41 |  |  | int32 | [6 empty] | calculated_load_rdrs | /components/pueblo1 | calculated_load_rdrs | Yes
Calculated Load RDPF | APX | Analog Out | 0.6 | AnOPInt32 |  |  |  | 1000 | 159 | 41 |  |  | int32 | [6 empty] | calculated_load_rdpf | /components/pueblo1 | calculated_load_rdpf | Yes
Generation Fast Frequency Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 160 | 41 |  |  | int32 | [6 empty] | gen_ffr_responsibility | /components/pueblo1 | gen_ffr_responsibility | Yes
Generation Fast Frequency Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 161 | 41 |  |  | int32 | [6 empty] | gen_ffr_requirement | /components/pueblo1 | gen_ffr_requirement | Yes
Generation Fast Frequency Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 162 | 41 |  |  | int32 | [6 empty] | gen_ffr_schedule | /components/pueblo1 | gen_ffr_schedule | Yes
Controllable Load Fast Frequency Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 163 | 41 |  |  | int32 | [6 empty] | load_ffr_responsibility | /components/pueblo1 | load_ffr_responsibility | Yes
Controllable Load Fast Frequency Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 164 | 41 |  |  | int32 | [6 empty] | load_ffr_requirement | /components/pueblo1 | load_ffr_requirement | Yes
Controllable Load Fast Frequency Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 165 | 41 |  |  | int32 | [6 empty] | load_ffr_schedule | /components/pueblo1 | load_ffr_schedule | Yes
Generation NET Megawatts | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 100 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net active power reported from SEL 735 at POI, including transformer losses |  | gen_net_mw | /components/pueblo1 | gen_net_mw | Yes
Generation NET Megavars | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 101 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net reactive power reported from SEL 735 at POI, including transformer losses |  | gen_net_mvar | /components/pueblo1 | gen_net_mvar | Yes
Generation Gross Megawatts | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 102 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | gross active power of site ESS before transformer losses |  | gen_gross_mw | /components/pueblo1 | gen_gross_mw | Yes
Generation Gross Megavars | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 103 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | gross reactive power of site ESS before transformer losses |  | gen_gross_mvar | /components/pueblo1 | gen_gross_mvar | Yes
Generation Normal Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 104 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of increasing change of active power dispatched by site ESS |  | gen_normal_up_ramp_rate_select | /components/pueblo1 | gen_normal_up_ramp_rate_select | Yes
Generation Normal Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 105 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of decreasing change of active power dispatched by site ESS |  | gen_normal_down_ramp_rate_select | /components/pueblo1 | gen_normal_down_ramp_rate_select | Yes
Generation Emergency Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 106 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of increasing change of active power dispatched by site ESS |  | gen_emergency_up_ramp_rate_select | /components/pueblo1 | gen_emergency_up_ramp_rate_select | Yes
Generation Emercency Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 107 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of decreasing change of active power dispatched by site ESS |  | gen_emergency_down_ramp_rate_select | /components/pueblo1 | gen_emergency_down_ramp_rate_select | Yes
Generation Maximum Operating State of Charge | Site | Analog In | 0.3 | analog | MWh |  |  | 1000 | 108 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | operational range upper limit of SOC across all running site ESS |  | gen_max_operating_soc | /components/pueblo1 | gen_max_operating_soc | Yes
Generation Minimum Operating State of Charge | Site | Analog In | 0.3 | analog | MWh |  |  | 1000 | 109 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | operational range lower limit of SOC across all running site ESS |  | gen_min_operating_soc | /components/pueblo1 | gen_min_operating_soc | Yes
Generation State of Charge | Site | Analog In | 0.3 | analog | MWh |  |  | 1000 | 110 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | state of charge across all running site ESS |  | gen_soc | /components/pueblo1 | gen_soc | Yes
Generation Maximum Operating Discharge Power Limit | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 111 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | maximum active power allowed from site ESS into grid |  | gen_max_discharge_mw_select | /components/pueblo1 | gen_max_discharge_mw_select | Yes
Generation Maximum Operating Charge Power Limit | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 112 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | maximum active power allowed into site ESS from grid |  | gen_max_charge_mw_select | /components/pueblo1 | gen_max_charge_mw_select | Yes
Generation Line Flows MW | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 113 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | MW output from site, positive for gen, negative for load |  | gen_line_flows_mw | /components/pueblo1 | gen_line_flows_mw | Yes
Generation Line Flows MVAR | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 114 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | MVAR output from site, positive for capacitive, negative for inductive |  | gen_line_flows_mvar | /components/pueblo1 | gen_line_flows_mvar | Yes
Generation Voltage | Site | Analog In | 0.3 | analog | kV |  |  | 1000 | 115 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | average voltage reported across the three phases from SEL 735 at POI |  | gen_voltage | /components/pueblo1 | gen_voltage | Yes
Generation Plant Auxiliary Load MW | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 116 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | aggregate site auxiliary active power - unused |  | gen_aux_mw | /components/pueblo1 | gen_aux_mw | Yes
Generation Plant Auxiliary Load MVAR | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 117 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | aggregate site auxiliary reactive power - unused |  | gen_aux_mvar | /components/pueblo1 | gen_aux_mvar | Yes
Controllable Load Net Load MW | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 130 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net active power reported from SEL 735 at POI, including transformer losses |  | load_net_mw | /components/pueblo1 | load_net_mw | Yes
Controllable Load Net Load MVAR | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 131 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net reactive power reported from SEL 735 at POI, including transformer losses |  | load_net_mvar | /components/pueblo1 | load_net_mvar | Yes
Controllable Load Scheduled Power Consumption | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 132 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | load_scheduled_mw | /components/pueblo1 | load_scheduled_mw | Yes
Controllable Load Scheduled Power Consumption +2 hours | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 133 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | load_scheduled_mw_2hr | /components/pueblo1 | load_scheduled_mw_2hr | Yes
Controllable Load Normal Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 134 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of increasing change of active power dispatched by site ESS |  | load_normal_up_ramp_rate_select | /components/pueblo1 | load_normal_up_ramp_rate_select | Yes
Controllable Load Normal Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 135 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of decreasing change of active power dispatched by site ESS |  | load_normal_down_ramp_rate_select | /components/pueblo1 | load_normal_down_ramp_rate_select | Yes
Controllable Load Emercency Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 136 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of increasing change of active power dispatched by site ESS |  | load_emergency_up_ramp_rate_select | /components/pueblo1 | load_emergency_up_ramp_rate_select | Yes
Controllable Load Emercency Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 137 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of decreasing change of active power dispatched by site ESS |  | load_emergency_down_ramp_rate_select | /components/pueblo1 | load_emergency_down_ramp_rate_select | Yes
Generation Resource Switches | Site | Digital In | 0.6 | binary | ST |  |  |  | 100 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_ds1_status | /components/pueblo1 | gen_ds1_status | Yes
Generation Resource Breaker Status | Site | Digital In | 0.6 | binary | ST |  |  |  | 101 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_52m_status | /components/pueblo1 | gen_52m_status | Yes
Generation Virtual Breaker Status - PSEUDO GEN | Site | Digital In | 0.6 | binary | ST |  |  |  | 102 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_pseudo_switch_status | /components/pueblo1 | gen_pseudo_switch_status | Yes
Generation Voltage Regulator Status | Site | Digital In | 0.6 | binary | ST |  |  |  | 103 | 1 |  |  | bool | [6 empty] | gen_avr_status | /components/pueblo1 | gen_avr_status | Yes
Controllable Load Virtual Breaker Status - PSEUDO LOAD | Site | Digital In | 0.6 | binary | ST |  |  |  | 130 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | load_pseudo_switch_status | /components/pueblo1 | load_pseudo_switch_status | Yes
Regulation Manual Override | BRP | Digital In | 0.6 | binary | ST |  |  |  | 131 | 1 |  |  | bool | [6 empty] | reg_manual_override | /components/pueblo1 | reg_manual_override | Yes
Generation Curtailment Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 100 | 12 |  |  | bool | [6 empty] | gen_curtailment_flag | /components/pueblo1 | gen_curtailment_flag | Yes
Generation SCCT Mitigation Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 101 | 12 |  |  | bool | [6 empty] | gen_scct_flag | /components/pueblo1 | gen_scct_flag | Yes
Generation Non-spin deployed Flag (NDPL) | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 102 | 12 |  |  | bool | [6 empty] | gen_ns_deployed_flag | /components/pueblo1 | gen_ns_deployed_flag | Yes
Controllable Load Curtailment Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 130 | 12 |  |  | bool | [6 empty] | load_curtailment_flag | /components/pueblo1 | load_curtailment_flag | Yes
Controllable Load SCCT Mitigation Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 131 | 12 |  |  | bool | [6 empty] | load_scct_flag | /components/pueblo1 | load_scct_flag | Yes
Controllable Load Non-spin deployed Flag (NDPL) | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 132 | 12 |  |  | bool | [6 empty] | load_ns_deployed_flag | /components/pueblo1 | load_ns_deployed_flag | Yes
Controllable Load Responsive Deployed Flag (RDPL) | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 133 | 12 |  |  | bool | [6 empty] | load_rrs_deployed_flag | /components/pueblo1 | load_rrs_deployed_flag | Yes
Regulation Manual Override Feedback | APX | Digital Out | 0.3 | CROB | ST |  |  |  | 134 | 12 |  |  | bool | [6 empty] | reg_manual_override_feedback | /components/pueblo1 | reg_manual_override_feedback | Yes

## TX100 Range (100)
Device Name | FlexGen Fleet Manager | Customer | Broad Reach Power
Device Protocol | DNP3 | Location | BRP ERCOT NOC
Device Protocol Version | 0.6 |  |  | Notes: Holding Register = AnOPInt32, Input Register = analog, Coil = CROB, Discrete Input = binary | [14 empty] | CLIENT | SERVER
Device ID String | outstation
Device IP Address (if TCP) | 172.3.27.150
Device Port (502 typical) | 20100
Master_Address | 200
Station_Address | 10
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical)
Stop Bits (1 typical)
RTU Device ID (1 typical) | [18 empty] | For client | For server
frequency | 10000
local uri | /local_##SITE_NAME##
Name | Source Device | Type | Version | Register Type | Unit | Words | Bus Scale | Scale | Address | Object | Variation | Evariation | Data Type | Range Start | Range End | Engineering Range Start | Engineering Range End | Description | Control Narrative for Register | Reg ID | URI | ID | Include | Stripped Address | Address2 | Repeat | Bit | FIMS Scale
Generation Non-Spin Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 100 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_ns_responsibility | /components/northfork | gen_ns_responsibility | Yes
Generation Non-Spin Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 101 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_ns_requirement | /components/northfork | gen_ns_requirement | Yes
Generation Non-Spin Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 102 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | gen_ns_schedule | /components/northfork | gen_ns_schedule | Yes
Generation Regulation Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 103 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_reg_down_responsibility | /components/northfork | gen_reg_down_responsibility | Yes
Generation Regulation Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 104 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_reg_down_requirement | /components/northfork | gen_reg_down_requirement | Yes
Generation Regulation Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 105 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | gen_reg_down_participation | /components/northfork | gen_reg_down_participation | Yes
Generation Responsive Reserve Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 106 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_rrs_responsibility | /components/northfork | gen_rrs_responsibility | Yes
Generation Responsive Reserve Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 107 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_rrs_requirement | /components/northfork | gen_rrs_requirement | Yes
Generation Responsive Reserve Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 108 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | gen_rrs_schedule | /components/northfork | gen_rrs_schedule | Yes
Generation Regulation Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 109 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_reg_up_responsibility | /components/northfork | gen_reg_up_responsibility | Yes
Generation Regulation Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 110 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_reg_up_requirement | /components/northfork | gen_reg_up_requirement | Yes
Generation Regulation Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 111 | 41 |  |  | int32 |  |  |  |  | ratio of reg up responsibility to total responsibility, monitoring only |  | gen_reg_up_participation_factor | /components/northfork | gen_reg_up_participation_factor | Yes
Generation FRRS Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 112 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_frrs_down_responsibility | /components/northfork | gen_frrs_down_responsibility | Yes
Generation FRRS Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 113 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_frrs_down_requirement | /components/northfork | gen_frrs_down_requirement | Yes
Generation FRRS Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 114 | 41 |  |  | int32 |  |  |  |  | ratio of FRRS down responsibility to total responsibility, monitoring only |  | gen_frrs_down_participation_factor | /components/northfork | gen_frrs_down_participation_factor | Yes
Generation FRRS Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 115 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | gen_frrs_up_responsibility | /components/northfork | gen_frrs_up_responsibility | Yes
Generation FRRS Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 116 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | gen_frrs_up_requirement | /components/northfork | gen_frrs_up_requirement | Yes
Generation FRRS Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 117 | 41 |  |  | int32 |  |  |  |  | ratio of FRRS up responsibility to total responsibility, monitoring only |  | gen_frrs_up_participation_factor | /components/northfork | gen_frrs_up_participation_factor | Yes
Generation Locational Marginal Pricing | ERCOT | Analog Out | 0.6 | AnOPInt32 | USD |  |  | 1000 | 118 | 41 |  |  | int32 | [6 empty] | gen_lmp | /components/northfork | gen_lmp | Yes
Generation Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 119 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT SCED |  | gen_basepoint | /components/northfork | gen_basepoint | Yes
Generation Updated Desired Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 120 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT LFC |  | gen_updated_basepoint | /components/northfork | gen_updated_basepoint | Yes
Generation Resource Status | APX | Analog Out | 0.6 | AnOPInt32 | coded |  |  |  | 121 | 41 |  |  | int32 | [6 empty] | gen_resource_status | /components/northfork | gen_resource_status | Yes
Controllable Load Non-Spin Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 130 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_ns_responsibility | /components/northfork | load_ns_responsibility | Yes
Controllable Load Non-Spin Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 131 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_ns_requirement | /components/northfork | load_ns_requirement | Yes
Controllable Load Non-Spin Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 132 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | load_ns_schedule | /components/northfork | load_ns_schedule | Yes
Controllable Load Regulation Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 133 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_reg_down_responsibility | /components/northfork | load_reg_down_responsibility | Yes
Controllable Load Regulation Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 134 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_reg_down_requirement | /components/northfork | load_reg_down_requirement | Yes
Controllable Load Regulation Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 135 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_reg_down_participation | /components/northfork | load_reg_down_participation | Yes
Controllable Load Responsive Reserve Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 136 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_rrs_responsibility | /components/northfork | load_rrs_responsibility | Yes
Controllable Load Responsive Reserve Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 137 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_rrs_requirement | /components/northfork | load_rrs_requirement | Yes
Controllable Load Responsive Reserve Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 138 | 41 |  |  | int32 |  |  |  |  | difference between responsibility and requirement, monitoring only |  | load_rrs_schedule | /components/northfork | load_rrs_schedule | Yes
Controllable Load Regulation Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 139 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_reg_up_responsibility | /components/northfork | load_reg_up_responsibility | Yes
Controllable Load Regulation Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 140 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_reg_up_requirement | /components/northfork | load_reg_up_requirement | Yes
Controllable Load Regulation Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 141 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_reg_up_participation_factor | /components/northfork | load_reg_up_participation_factor | Yes
Controllable Load FRRS Down Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 142 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_frrs_down_responsibility | /components/northfork | load_frrs_down_responsibility | Yes
Controllable Load FRRS Down Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 143 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_frrs_down_requirement | /components/northfork | load_frrs_down_requirement | Yes
Controllable Load FRRS Down Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 144 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_frrs_down_participation_factor | /components/northfork | load_frrs_down_participation_factor | Yes
Controllable Load FRRS Up Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 145 | 41 |  |  | int32 |  |  |  |  | power responsibility for this service, from COP sent to ERCOT |  | load_frrs_up_responsibility | /components/northfork | load_frrs_up_responsibility | Yes
Controllable Load FRRS Up Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 146 | 41 |  |  | int32 |  |  |  |  | power requirement (deployment) for this service, calculated from QSE requirement and COP |  | load_frrs_up_requirement | /components/northfork | load_frrs_up_requirement | Yes
Controllable Load FRRS Up Participation Factor | APX | Analog Out | 0.6 | AnOPInt32 | per unit |  |  | 1000 | 147 | 41 |  |  | int32 |  |  |  |  | ratio of reg down responsibility to total responsibility, monitoring only |  | load_frrs_up_participation_factor | /components/northfork | load_frrs_up_participation_factor | Yes
Controllable Load Locational Marginal Pricing | ERCOT | Analog Out | 0.6 | AnOPInt32 | USD |  |  | 1000 | 148 | 41 |  |  | int32 | [6 empty] | load_lmp | /components/northfork | load_lmp | Yes
Controllable Load Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 149 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT SCED |  | load_basepoint | /components/northfork | load_basepoint | Yes
Controllable Load Updated Desired Base Point | ERCOT | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 150 | 41 |  |  | int32 |  |  |  |  | active power setpoint from ERCOT LFC |  | load_updated_basepoint | /components/northfork | load_updated_basepoint | Yes
Controllable Load Resource Status | APX | Analog Out | 0.6 | AnOPInt32 | coded |  |  |  | 151 | 41 |  |  | int32 | [6 empty] | load_resource_status | /components/northfork | load_resource_status | Yes
gen kv measurement |  | Analog Out | 0.6 | AnOPInt32 | kV |  |  |  | 152 | 41 |  |  | int32 | [6 empty] | gen_kv_measurement | /components/northfork | gen_kv_measurement | Yes
gen kv target |  | Analog Out | 0.6 | AnOPInt32 | kV |  |  |  | 153 | 41 |  |  | int32 | [6 empty] | gen_kv_target | /components/northfork | gen_kv_target | Yes
load kv measurement |  | Analog Out | 0.6 | AnOPInt32 | kV |  |  |  | 154 | 41 |  |  | int32 | [6 empty] | load_kv_measurement | /components/northfork | load_kv_measurement | Yes
load kv target |  | Analog Out | 0.6 | AnOPInt32 | kV |  |  |  | 155 | 41 |  |  | int32 | [6 empty] | load_kv_target | /components/northfork | load_kv_target | Yes
Calculated Generation RURS | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 156 | 41 |  |  | int32 | [6 empty] | calculated_gen_rurs | /components/northfork | calculated_gen_rurs | Yes
Calculated Generation RUPF | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 157 | 41 |  |  | int32 | [6 empty] | calculated_gen_rupf | /components/northfork | calculated_gen_rupf | Yes
Calculated Generation RDRS | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 158 | 41 |  |  | int32 | [6 empty] | calculated_gen_rdrs | /components/northfork | calculated_gen_rdrs | Yes
Calculated Generation RDPF | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 159 | 41 |  |  | int32 | [6 empty] | calculated_gen_rdpf | /components/northfork | calculated_gen_rdpf | Yes
Calculated Load RURS | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 160 | 41 |  |  | int32 | [6 empty] | calculated_load_rurs | /components/northfork | calculated_load_rurs | Yes
Calculated Load RUPF | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 161 | 41 |  |  | int32 | [6 empty] | calculated_load_rupf | /components/northfork | calculated_load_rupf | Yes
Calculated Load RDRS | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 162 | 41 |  |  | int32 | [6 empty] | calculated_load_rdrs | /components/northfork | calculated_load_rdrs | Yes
Calculated Load RDPF | APX | Analog Out |  | AnOPInt32 |  |  |  | 1000 | 163 | 41 |  |  | int32 | [6 empty] | calculated_load_rdpf | /components/northfork | calculated_load_rdpf | Yes
Generation Fast Frequency Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 164 | 41 |  |  | int32 | [6 empty] | gen_ffr_responsibility | /components/northfork | gen_ffr_responsibility | Yes
Generation Fast Frequency Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 165 | 41 |  |  | int32 | [6 empty] | gen_ffr_requirement | /components/northfork | gen_ffr_requirement | Yes
Generation Fast Frequency Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 166 | 41 |  |  | int32 | [6 empty] | gen_ffr_schedule | /components/northfork | gen_ffr_schedule | Yes
Controllable Load Fast Frequency Responsibility | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 167 | 41 |  |  | int32 | [6 empty] | load_ffr_responsibility | /components/northfork | load_ffr_responsibility | Yes
Controllable Load Fast Frequency Requirement | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 168 | 41 |  |  | int32 | [6 empty] | load_ffr_requirement | /components/northfork | load_ffr_requirement | Yes
Controllable Load Fast Frequency Schedule | APX | Analog Out | 0.6 | AnOPInt32 | MW |  |  | 1000 | 169 | 41 |  |  | int32 | [6 empty] | load_ffr_schedule | /components/northfork | load_ffr_schedule | Yes
Generation NET Megawatts | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 100 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net active power reported from SEL 735 at POI, including transformer losses |  | gen_net_mw | /components/northfork | gen_net_mw | Yes
Generation NET Megavars | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 101 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net reactive power reported from SEL 735 at POI, including transformer losses |  | gen_net_mvar | /components/northfork | gen_net_mvar | Yes
Generation Gross Megawatts | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 102 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | gross active power of site ESS before transformer losses |  | gen_gross_mw | /components/northfork | gen_gross_mw | Yes
Generation Gross Megavars | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 103 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | gross reactive power of site ESS before transformer losses |  | gen_gross_mvar | /components/northfork | gen_gross_mvar | Yes
Generation Normal Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 104 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of increasing change of active power dispatched by site ESS |  | gen_normal_up_ramp_rate_select | /components/northfork | gen_normal_up_ramp_rate_select | Yes
Generation Normal Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 105 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of decreasing change of active power dispatched by site ESS |  | gen_normal_down_ramp_rate_select | /components/northfork | gen_normal_down_ramp_rate_select | Yes
Generation Emergency Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 106 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of increasing change of active power dispatched by site ESS |  | gen_emergency_up_ramp_rate_select | /components/northfork | gen_emergency_up_ramp_rate_select | Yes
Generation Emercency Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 107 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of decreasing change of active power dispatched by site ESS |  | gen_emergency_down_ramp_rate_select | /components/northfork | gen_emergency_down_ramp_rate_select | Yes
Generation Maximum Operating State of Charge | Site | Analog In | 0.3 | analog | MWh |  |  | 1000 | 108 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | operational range upper limit of SOC across all running site ESS |  | gen_max_operating_soc | /components/northfork | gen_max_operating_soc | Yes
Generation Minimum Operating State of Charge | Site | Analog In | 0.3 | analog | MWh |  |  | 1000 | 109 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | operational range lower limit of SOC across all running site ESS |  | gen_min_operating_soc | /components/northfork | gen_min_operating_soc | Yes
Generation State of Charge | Site | Analog In | 0.3 | analog | MWh |  |  | 1000 | 110 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | state of charge across all running site ESS |  | gen_soc | /components/northfork | gen_soc | Yes
Generation Maximum Operating Discharge Power Limit | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 111 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | maximum active power allowed from site ESS into grid |  | gen_max_discharge_mw_select | /components/northfork | gen_max_discharge_mw_select | Yes
Generation Maximum Operating Charge Power Limit | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 112 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | maximum active power allowed into site ESS from grid |  | gen_max_charge_mw_select | /components/northfork | gen_max_charge_mw_select | Yes
Generation Line Flows MW | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 113 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | MW output from site, positive for gen, negative for load |  | gen_line_flows_mw | /components/northfork | gen_line_flows_mw | Yes
Generation Line Flows MVAR | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 114 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | MVAR output from site, positive for capacitive, negative for inductive |  | gen_line_flows_mvar | /components/northfork | gen_line_flows_mvar | Yes
Generation Voltage | Site | Analog In | 0.3 | analog | kV |  |  | 1000 | 115 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | average voltage reported across the three phases from SEL 735 at POI |  | gen_voltage | /components/northfork | gen_voltage | Yes
Generation Plant Auxiliary Load MW | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 116 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | aggregate site auxiliary active power - unused |  | gen_aux_mw | /components/northfork | gen_aux_mw | Yes
Controllable Load Net Load MW | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 130 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net active power reported from SEL 735 at POI, including transformer losses |  | load_net_mw | /components/northfork | load_net_mw | Yes
Controllable Load Net Load MVAR | Site | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 131 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | net reactive power reported from SEL 735 at POI, including transformer losses |  | load_net_mvar | /components/northfork | load_net_mvar | Yes
Controllable Load Scheduled Power Consumption | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 132 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | load_scheduled_mw | /components/northfork | load_scheduled_mw | Yes
Controllable Load Scheduled Power Consumption +2 hours | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 133 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | load_scheduled_mw_2hr | /components/northfork | load_scheduled_mw_2hr | Yes
Controllable Load Normal Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 134 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of increasing change of active power dispatched by site ESS |  | load_normal_up_ramp_rate_select | /components/northfork | load_normal_up_ramp_rate_select | Yes
Controllable Load Normal Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 135 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | rate of decreasing change of active power dispatched by site ESS |  | load_normal_down_ramp_rate_select | /components/northfork | load_normal_down_ramp_rate_select | Yes
Controllable Load Emercency Up Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 136 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of increasing change of active power dispatched by site ESS |  | load_emergency_up_ramp_rate_select | /components/northfork | load_emergency_up_ramp_rate_select | Yes
Controllable Load Emercency Down Ramp Rate | Site | Analog In | 0.3 | analog | MW |  |  | 1000 | 137 | 30 | Group30Var1 | Group32Var1 | int32 |  |  |  |  | emergency rate of decreasing change of active power dispatched by site ESS |  | load_emergency_down_ramp_rate_select | /components/northfork | load_emergency_down_ramp_rate_select | Yes
High-side Voltage - 138KV |  | Analog In | 0.3 | analog | kV |  |  | 1000 | 138 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | gen_high_side_voltage | /components/northfork | gen_high_side_voltage | Yes
Low-side Voltage - 138KV |  | Analog In | 0.3 | analog | kV |  |  | 1000 | 139 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | gen_low_side_voltage | /components/northfork | gen_low_side_voltage | Yes
T1 Transformer Flow MW |  | Analog In | 0.3 | analog | MW |  |  | 1000 | 140 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | gen_transformer_flow_mw | /components/northfork | gen_transformer_flow_mw | Yes
T1 Transformer Flow MV |  | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 141 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | gen_transformer_flow_mv | /components/northfork | gen_transformer_flow_mv | Yes
Load1 MW |  | Analog In | 0.3 | analog | MW |  |  | 1000 | 142 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | gen_load_mw | /components/northfork | gen_load_mw | Yes
Load1 MV |  | Analog In | 0.3 | analog | MVAR |  |  | 1000 | 143 | 30 | Group30Var1 | Group32Var1 | int32 | [6 empty] | gen_load_mv | /components/northfork | gen_load_mv | Yes
Generation Resource Switches | Site | Digital In | 0.6 | binary | ST |  |  |  | 100 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_ds1_status | /components/northfork | gen_ds1_status | Yes
Generation Resource Breaker Status | Site | Digital In | 0.6 | binary | ST |  |  |  | 101 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_52m_status | /components/northfork | gen_52m_status | Yes
Generation Virtual Breaker Status - PSEUDO GEN | Site | Digital In | 0.6 | binary | ST |  |  |  | 102 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_pseudo_switch_status | /components/northfork | gen_pseudo_switch_status | Yes
Generation Voltage Regulator Status | Site | Digital In | 0.6 | binary | ST |  |  |  | 103 | 1 |  |  | bool | [6 empty] | gen_avr_status | /components/northfork | gen_avr_status | Yes
Controllable Load Virtual Breaker Status - PSEUDO LOAD | Site | Digital In | 0.6 | binary | ST |  |  |  | 104 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | load_pseudo_switch_status | /components/northfork | load_pseudo_switch_status | Yes
Generation Resource Switch SW-L1 |  | Digital In | 0.6 | binary | ST |  |  |  | 105 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_sw1_status | /components/northfork | gen_sw1_status | Yes
Virtual Breaker 1 Status |  | Digital In | 0.6 | binary | ST |  |  |  | 106 | 1 |  |  | bool |  |  |  |  | site breaker feedback |  | gen_pseudo_breaker_status | /components/northfork | gen_pseudo_breaker_status | Yes
Regulation Manual Override | BRP | Digital In | 0.6 | binary | ST |  |  |  | 107 | 1 |  |  | bool | [6 empty] | reg_manual_override | /components/northfork | reg_manual_override | Yes
Generation Curtailment Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 100 | 12 |  |  | bool | [6 empty] | gen_curtailment_flag | /components/northfork | gen_curtailment_flag | Yes
Generation SCCT Mitigation Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 101 | 12 |  |  | bool | [6 empty] | gen_scct_flag | /components/northfork | gen_scct_flag | Yes
Generation Non-spin deployed Flag (NDPL) | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 102 | 12 |  |  | bool | [6 empty] | gen_ns_deployed_flag | /components/northfork | gen_ns_deployed_flag | Yes
Controllable Load Curtailment Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 130 | 12 |  |  | bool | [6 empty] | load_curtailment_flag | /components/northfork | load_curtailment_flag | Yes
Controllable Load SCCT Mitigation Flag | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 131 | 12 |  |  | bool | [6 empty] | load_scct_flag | /components/northfork | load_scct_flag | Yes
Controllable Load Non-spin deployed Flag (NDPL) | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 132 | 12 |  |  | bool | [6 empty] | load_ns_deployed_flag | /components/northfork | load_ns_deployed_flag | Yes
Controllable Load Responsive Deployed Flag (RDPL) | ERCOT | Digital Out | 0.3 | CROB | ST |  |  |  | 133 | 12 |  |  | bool | [6 empty] | load_rrs_deployed_flag | /components/northfork | load_rrs_deployed_flag | Yes
Regulation Manual Override Feedback | APX | Digital Out | 0.3 | CROB | ST |  |  |  | 134 | 12 |  |  | bool | [6 empty] | reg_manual_override_feedback | /components/northfork | reg_manual_override_feedback | Yes