## Version
No. | Version | Time | Records | Reviser
1 | V1 | 2021-02-01 | Initial version | Suk
2 | V2 | 2021-03-22 | Add register addresses | Suk
2 | V3 | 2021-04-06 | Revise registers | Suk

## Read-only register
Register Address | R/W |  | Name | 标识名 | Factor/Unit | Data Type | Remark
System
20000 | R |  | Signal | EMS心跳 |  | UINT16
20001 | R |  | Communication state | 通讯状态 |  | UINT16 | bit0：PCS1(0-abnormal 1-normal) bit1：PCS2(0-abnormal 1-normal) bit2：BMS1(0-abnormal 1-normal) bit3：BMS2(0-abnormal 1-normal) bit4：EMMU1(0-abnormal 1-normal) bit5：EMMU2(0-abnormal 1-normal)
20002 | R |  | System state | PCS总运行状态 |  | UINT16 | 0-Stop(All PCS is all stop) 1-Run((At least one PCS runs) 2-Fault(At least one PCS fault and no PCS runs) 3-other
20003 | R |  | PCS under/over power | PCS过欠功率指示 |  | UINT16 | bit0：overpower-PCS1 bit1：overpowerPCS2 bit8：underpower-PCS1 bit9：underpower--PCS2
20004 | R |  | Unit power distribution | 支路分配功率状态 |  | UINT16 | Bit0: branch 1(0- non-assignable 1- assignable) Bit1: branch 2(0- non-assignable 1- assignable)
20005 | R |  | Total issued active power | 总下发有功功率 | 0.1kW | INT16
20006 | R |  | Unit1 issued active power | 支路1分配功率 | 0.1kW | INT16
20007 | R |  | Unit2 issued active power | 支路2分配功率 | 0.1kW | INT16
20008[2Regs] | R |  | BMS1 Chargeable energy | BMS1当前可充电量 | 0.001kWh | UINT32
20010[2Regs] | R |  | BMS2 Chargeable energy | BMS2当前可充电量 | 0.001kWh | UINT32
20012 | R |  | BMS1 Chargeable power | BMS1最大可充电功率 | 1kW | UINT16
20013 | R |  | BMS2 Chargeable power | BMS2最大可充电功率 | 1kW | UINT16
20014[2Regs] | R |  | BMS1 Dishargeable energy | BMS1当前可放电量 | 0.001kWh | UINT32
20016[2Regs] | R |  | BMS2 Dischargeable energy | BMS2当前可放电量 | 0.001kWh | UINT32
20018 | R |  | BMS1 Dishargeable power | BMS1最大可放电功率 | 1kW | UINT16
20019 | R |  | BMS2 Dischargeable power | BMS2最大可放电功率 | 1kW | UINT16
20020 | R |  | PCS1 running |  |  | UINT16 | 0-Stop，1-Run
20021 | R |  | BMS1 fault |  |  | UINT16 | 0-Normal，1-Fault
20022 | R |  | EMMU1 fault |  |  | UINT16 | 0-Normal，1-Fault
20023 | R |  | PCS2 running |  |  | UINT16 | 0-Stop，1-Run
20024 | R |  | BMS2 fault |  |  | UINT16 | 0-Normal，1-Fault
20025 | R |  | EMMU2 fault |  |  | UINT16 | 0-Normal，1-Fault
20026 | R |  | BMS1 discharge zero power limit |  |  | UINT16 | 0-Normal，1-Discharge zero power limit
20027 | R |  | BMS2 discharge zero power limit |  |  | UINT16 | 0-Normal，1-Discharge zero power limit
20028[2Regs] | R |  | Total Chargeable energy |  | 0.001kWh | UINT32
20030 | R |  | Total Chargeable power |  | 1kW | UINT16
20031[2Regs] | R |  | Total Dischargeable energy |  | 0.001kWh | UINT32
20033 | R |  | Total Dishargeable power |  | 1kW | UINT16
PCS1
21000 | R | Uinab_RMS1 | voltage of line AB | 交流电压AB相有效值 | 0.1V | UINT16
21001 | R | Uinbc_RMS1 | voltage of line BC | 交流电压BC相有效值 | 0.1V | UINT16
21002 | R | Uinca_RMS1 | voltage of line CA | 交流电压CA相有效值 | 0.1V | UINT16
21003 | R | Iina_RMS1 | current of phase A | 交流电流A相有效值 | 0.1A | INT16
21004 | R | Iinb_RMS1 | current of phase B | 交流电流B相有效值 | 0.1A | INT16
21005 | R | Iinc_RMS1 | current of phase C | 交流电流C相有效值 | 0.1A | INT16
21006 | R | W1 | Frequency | 电网频率 | 0.1Hz | UINT16
21007 | R | P1 | active power of AC | 有功功率 | 0.1kW | INT16
21008 | R | Q1 | reactive power of AC | 无功功率 | 0.1kVar | INT16
21009 | R |  | power factor | 功率因数 | 0.01 | INT16
21010 | R | Ubtra_Ever1 | Overall voltage of DC1 | 母线直流电压值 | 0.1V | UINT16
21011 | R | Ibtra_Ever1 | Overall current of DC1 | 母线直流电流值 | 0.1A | INT16
21012 | R | Pbtra1 | Active power of DC1 | 母线直流侧功率 | 0.1kW | INT16
21013 | R | TempA1 | IGBT temp._phase A1 | IGBT温度_A相 | 1℃ | INT16
21014 | R | TempB1 | IGBT temp._phase B1 | IGBT温度_B相 | 1℃ | INT16
21015 | R | TempC1 | IGBT temp._phase C1 | IGBT温度_C相 | 1℃ | INT16
21016 | R | PCS_Mode1 | Operating mode 1 | 运行模式 |  | UINT16 | 0x1111-PQ mode 0x2222-VF mode 0x3333-VSG mode
21017 | R | PCS_State1 | Working state1 | PCS状态机值 |  | UINT16 | 0：Initial 1-3：Starting 4：Working 5：Fault 6：Stop
21018 | R |  | System status register 0 | 系统状态寄存器0 |  | UINT16 | For PCS debug
21019 | R |  | System status register 1 | 系统状态寄存器1 |  | UINT16 | For PCS debug
21020 | R |  | System status register 2 | 系统状态寄存器2 |  | UINT16 | For PCS debug
21021 | R |  | System status register 3 | 系统状态寄存器3 |  | UINT16 | For PCS debug
21022 | R |  | System status register 4 | 系统状态寄存器4 |  | UINT16 | For PCS debug
21023 | R |  | System status register 5 | 系统状态寄存器5 |  | UINT16 | For PCS debug
21024 | R |  | System status register 6 | 系统状态寄存器6 |  | UINT16 | For PCS debug
21025 | R |  | System status register 7 | 系统状态寄存器7 |  | UINT16 | For PCS debug
21026 | R |  | System fault latch register 0 | 系统故障锁存寄存器0 |  | UINT16 | For PCS debug
21027 | R |  | System fault latch register 1 | 系统故障锁存寄存器1 |  | UINT16 | For PCS debug
21028 | R |  | System fault latch register 2 | 系统故障锁存寄存器2 |  | UINT16 | For PCS debug
21029 | R |  | System fault latch register 3 | 系统故障锁存寄存器3 |  | UINT16 | For PCS debug
21030 | R |  | System fault latch register 4 | 系统故障锁存寄存器4 |  | UINT16 | For PCS debug
21031 | R |  | System fault latch register 5 | 系统故障锁存寄存器5 |  | UINT16 | For PCS debug
21032 | R |  | System fault latch register 6 | 系统故障锁存寄存器6 |  | UINT16 | For PCS debug
21033 | R |  | System fault latch register 7 | 系统故障锁存寄存器7 |  | UINT16 | For PCS debug
PCS2
21500 | R | Uinab_RMS2 | Overall voltage of line AB | 交流电压AB相有效值 | 0.1V | UINT16
21501 | R | Uinbc_RMS2 | Overall voltage of line BC | 交流电压BC相有效值 | 0.1V | UINT16
21502 | R | Uinca_RMS2 | Overall voltage of line CA | 交流电压CA相有效值 | 0.1V | UINT16
21503 | R | Iina_RMS2 | Overall current of phase A | 交流电流A相有效值 | 0.1A | INT16
21504 | R | Iinb_RMS2 | Overall current of phase B | 交流电流B相有效值 | 0.1A | INT16
21505 | R | Iinc_RMS2 | Overall current of phase C | 交流电流C相有效值 | 0.1A | INT16
21506 | R | W2 | Frequency | 电网频率 | 0.1Hz | UINT16
21507 | R | P2 | Overall active power of AC | 有功功率 | 0.1kW | INT16
21508 | R | Q2 | Overall reactive power of AC | 无功功率 | 0.1kVar | INT16
21509 | R |  | Power factor | 功率因数 | 0.01 | INT16
21510 | R | Ubtra_Ever2 | Overall voltage of DC | 母线直流电压值 | 0.1V | UINT16
21511 | R | Ibtra_Ever2 | Overall current of DC | 母线直流电流值 | 0.1A | INT16
21512 | R | Pbtra2 | Active power of DC | 母线直流侧功率 | 0.1kW | INT16
21513 | R | TempA2 | IGBT temperature | IGBT温度_A相 | 1℃ | INT16
21514 | R | TempB2 | IGBT temperature | IGBT温度_B相 | 1℃ | INT16
21515 | R | TempC2 | IGBT temperature | IGBT温度_C相 | 1℃ | INT16
21516 | R | PCS_Mode2 | Operating mode | 运行模式 |  | UINT16 | 0x1111-PQ mode 0x2222-VF mode 0x3333-VSG mode
21517 | R | PCS_State2 | Working state | PCS状态机值 |  | UINT16 | 0：Initial 1-3：Starting 4：Working 5：Fault 6：Stop
21518 | R |  | System status register 0 | 系统状态寄存器0 |  | UINT16 | For PCS debug
21519 | R |  | System status register 1 | 系统状态寄存器1 |  | UINT16 | For PCS debug
21520 | R |  | System status register 2 | 系统状态寄存器2 |  | UINT16 | For PCS debug
21521 | R |  | System status register 3 | 系统状态寄存器3 |  | UINT16 | For PCS debug
21522 | R |  | System status register 4 | 系统状态寄存器4 |  | UINT16 | For PCS debug
21523 | R |  | System status register 5 | 系统状态寄存器5 |  | UINT16 | For PCS debug
21524 | R |  | System status register 6 | 系统状态寄存器6 |  | UINT16 | For PCS debug
21525 | R |  | System status register 7 | 系统状态寄存器7 |  | UINT16 | For PCS debug
21526 | R |  | System fault latch register 0 | 系统故障锁存寄存器0 |  | UINT16 | For PCS debug
21527 | R |  | System fault latch register 1 | 系统故障锁存寄存器1 |  | UINT16 | For PCS debug
21528 | R |  | System fault latch register 2 | 系统故障锁存寄存器2 |  | UINT16 | For PCS debug
21529 | R |  | System fault latch register 3 | 系统故障锁存寄存器3 |  | UINT16 | For PCS debug
21530 | R |  | System fault latch register 4 | 系统故障锁存寄存器4 |  | UINT16 | For PCS debug
21531 | R |  | System fault latch register 5 | 系统故障锁存寄存器5 |  | UINT16 | For PCS debug
21532 | R |  | System fault latch register 6 | 系统故障锁存寄存器6 |  | UINT16 | For PCS debug
21533 | R |  | System fault latch register 7 | 系统故障锁存寄存器7 |  | UINT16 | For PCS debug
BMS1
22000[20Regs] | R | BMS bus voltage_1 | BMS bus voltage_1 | 簇总电压 | 0.1V | UINT16
22020[20Regs] | R | BMS bus current_1 | BMS bus current_1 | 簇总电流 | 0.1A | INT16
22040[20Regs] | R |  | Average cell Voltage_1 |  | 0,0001V | UINT16
22060[20Regs] | R |  | Cluster SOC_1 |  | 0.1% | UINT16
22080[20Regs] | R |  | Cluster SOH_1 |  | 0.1% | UINT16
22100[40Regs] | R | Cluster No.1-No.20 max cell voltage and the max module No._1 | Cluster No.1-No.20 cluster max cell voltage and the max module No._1 | 簇内单体最大电压+编号 | 0.0001V | UINT16 | eg.22100:max. cell voltage in Cluster No.1 22101:No. module of max. cell voltage in Cluster No.1
22140[40Regs] | R | Cluster No.1-No.20 second max cell voltage and the second max module No._1 | Cluster No.1-No.20 second max cell voltage and the second max module No._1 | 簇内单体次最大电压+编号 | 0.0001V | UINT16
22180[40Regs] | R | Cluster No.1-No.20 min cell voltage and the min module No._1 | Cluster No.1-No.20 cluster min cell voltage and the min module No._1 | 簇内单体最小电压+编号 | 0.0001V | UINT16
22220[40Regs] | R | Cluster No.1-No.20 second min cell voltage and the second min cell pack num._1 | Cluster No.1-No.20 second min cell voltage and the second min module No._1 | 簇内单体次最小电压+编号 | 0.0001V | UINT16
22260[40Regs] | R | Cluster No.1-No.20 max cell temperature and the max module No._1 | Cluster No.1-No.20 cluster max cell temperature and the max module No._1 | 簇内单体最大温度+编号 | 0.01℃ | INT16
22300[40Regs] | R | Cluster No.1-No.20 second max cell temperature and the second max module No._1 | Cluster No.1-No.20 second max cell temperature and the second max module No._1 | 簇内单体次最大温度+编号 | 0.01℃ | INT16
22340[40Regs] | R | Cluster No.1-No.20 min cell temperature and the min module No._1 | Cluster No.1-No.20 cluster min cell temperature and the min module No._1 | 簇内单体最小温度+编号 | 0.01℃ | INT16
22380[40Regs] | R | Cluster No.1-No.20 second min cell temperatureand the second min module No._1 | Cluster No.1-No.20 second min cell temperature and the second min module No._1 | 簇内单体次最小温度+编号 | 0.01℃ | INT16
22420[40Regs] | R |  | Cluster No.1-No.20 warning status_1 |  |  | UINT32 | Each bit means one cluster. 0: warning 1:normal or warning recovery
22460[40Regs] | R |  | Cluster No.1-No.20 fault status_1 |  |  | UINT32 | Each bit means one cluster. 0: warning 1:normal or fault recovery
22500 | R | BMS maximum cell voltage_1 | BMS maximum cell voltage _1 | 堆内单体最大电压值 | 0.0001V | UINT16
22501 | R | Cluster index ofthe BMS maximum cell_1 | Cluster index of the BMS maximum cell_1 | 堆内最大电压单体簇号 |  | UINT16
22502 | R | Module index of the BMS maximum cell voltage_1 | Module index of the BMS maximum cell voltage_1 | 堆内最大电压单体模组号 |  | UINT16
22503 | R | BMS minimum cell voltage_1 | BMS minimum cell voltage_1 | 堆内单体最小电压值 | 0.0001V | UINT16
22504 | R | Cluster index of the BMS minimum cell_1 | Cluster index ofthe BMS minimum cell_1 | 堆内最小电压单体簇号 |  | UINT16
22505 | R | Module index of the BMS minimum cell voltage_1 | Module index of the BMS minimum cell voltage _1 | 堆内最小电压单体模组编号 |  | UINT16
22506 | R | BMS maximum cell temperature_1 | BMS maximum cell temperature_1 | 堆内单体最大温度值 | 0.01℃ | INT16
22507 | R | Cluster index of BMS maximum temperature_1 | Cluster index of BMS maximum temperature_1 | 堆内最大温度单体簇号 |  | UINT16
22508 | R | Module index of BMS maximum temperature_1 | Module index of BMS maximum temperature_1 | 堆内最大温度单体模组编号 |  | UINT16
22509 | R | BMS minimum cell temperature_1 | BMS minimum cell temperature | 堆内单体最小温度值 | 0.01℃ | INT16
22510 | R | Cluster index of BMS maximum temperature_1 | Cluster index of BMS maximum temperature | 堆内最小温度单体簇号 |  | UINT16
22511 | R | Module index of BMS minimum temperature_1 | Module index of BMS minimum temperature | 堆内最小温度单体模组编号 |  | UINT16
22512 | R | BMS bus voltage_1 | BMS bus voltage_1 | BMS母线电压 | 0.1V | UINT16
22513 | R | BMS bus current_1 | BMS bus current_1 | BMS母线电流 | 0.1A | INT16
22514 | R | BMS SOC_1 | BMS SOC_1 | BMS SOC值 | 0.1% | UINT16
22515 | R | BMS power_1 | BMS power_1 | BMS功率 | 0.1kW | INT16
22516 | R |  | BMS SOH_1 |  | 0.1% | UINT16
22517 | R | Operation status_1 | Operation status_1 | 充放电状态 |  | UINT16 | 0：rest 1：charge 2：discharge
22518[2Regs] | R | BMS current chargeable energy_1 | BMS current chargeable energy_1 | BMS当前可放电量 | 0.001kWh | UINT32
22520[2Regs] | R | BMS current dischargeable energy_1 | BMS current dischargeable energy_1 | BMS当前可充电量 | 0.001kWh | UINT32
22522[2Regs] | R | Power limit state_high byte_1 | Power limit state_high byte_1 | BMS限功率状态字高字 |  | UINT32
22524[2Regs] | R | Power limit state_low byte_1 | Power limit state_low byte_1 | BMS限功率状态字低字 |  | UINT32
22526[4Regs] | R |  | Power limit state_res |  |  | UINT64
22530[2Regs] | R | BMS alarm state_high byte_1 | BMS alarm state_high byte_1 | BMS告警状态字高字 |  | UINT32
22532[2Regs] | R | BMS alarm state_low byte_1 | BMS alarm state_low byte_1 | BMS告警状态字低字 |  | UINT32
22534[4Regs] | R |  | BMS alarm state_res |  |  | UINT64
22538[2Regs] | R | BMS fault state_high byte_1 | BMS fault state_high byte_1 | BMS故障状态字高字 |  | UINT32
22540[2Regs] | R | BMS fault state_low byte_1 | BMS fault state_low byte_1 | BMS故障状态字低字 |  | UINT32
22542[4Regs] | R |  | BMS fault state_res |  |  | UINT64
22546 | R |  | Cluster online number_1 | 在线的簇的数量 |  | UINT16
22547 | R | Circuit breaker control word_1 | Circuit breaker control word_1 | 断路器控制字 |  | UINT16 | One bit for one cluster, 0：open；1：close
22548 | R | Main circuit breaker status_1 | DC breaker status_1 | 总断路器 |  | UINT16 | 0：open；1：close
22549 | R | Maximum charging power limit_1 | Maximum charging power limit_1 | 最大可充电功率 | 1kW | UINT16
22550 | R | Maximum discharging power limit_1 | Maximum discharging power limit_1 | 最大可放电功率 | 1kW | UINT16
22551 | R |  | Local/Remote mode of DC breaker_1 |  |  | UINT16 | 1:Remote 2:Local
BMS2
23000[20Regs] | R | BMS bus voltage_2 | BMS bus voltage_2 | 簇总电压 | 0.1V | UINT16
23020[20Regs] | R | BMS bus current_2 | BMS bus current_2 | 簇总电流 | 0.1A | INT16
23040[20Regs] | R |  | Average cell voltage of each cluster_2 |  | 0.0001V | UINT16
23060[20Regs] | R |  | Cluster SOC_2 |  | 0.1% | UINT16
23080[20Regs] | R |  | Cluster SOH_2 |  | 0.1% | UINT16
23100[40Regs] | R | Cluster No.1-No.20 max cell voltage and the max module No._2 | Cluster No.1-No.20 cluster max cell voltage and the max module No._2 | 簇内单体最大电压+编号 | 0.0001V | UINT16 | eg.22560:max. cell voltage in Cluster No.1 22561:No. module of max. cell voltage in Cluster No.1
23140[40Regs] | R | Cluster No.1-No.20 second max cell voltage and the second max module No._2 | Cluster No.1-No.20 second max cell voltage and the second max module No._2 | 簇内单体次最大电压+编号 | 0.0001V | UINT16
23180[40Regs] | R | Cluster No.1-No.20 min cell voltage and the min module No._2 | Cluster No.1-No.20 cluster min cell voltage and the min module No._2 | 簇内单体最小电压+编号 | 0.0001V | UINT16
23220[40Regs] | R | Cluster No.1-No.20 second min cell voltage and the second min cell pack num._2 | Cluster No.1-No.20 second min cell voltage and the second min module No._2 | 簇内单体次最小电压+编号 | 0.0001V | UINT16
23260[40Regs] | R | Cluster No.1-No.20 max cell temperature and the max module No._2 | Cluster No.1-No.20 cluster max cell temperature and the max module No._2 | 簇内单体最大温度+编号 | 0.01℃ | INT16
23300[40Regs] | R | Cluster No.1-No.20 second max cell temperature and the second max module No._2 | Cluster No.1-No.20 second max celltemperature and the second max module No._2 | 簇内单体次最大温度+编号 | 0.01℃ | INT16
23340[40Regs] | R | Cluster No.1-No.20 min cell temperature and the min module No._2 | Cluster No.1-No.20 cluster min cell temperature and the min module No._2 | 簇内单体最小温度+编号 | 0.01℃ | INT16
23380[40Regs] | R | Cluster No.1-No.20 second min cell temperatureand the second min module No._2 | Cluster No.1-No.20 second min cell temperature and the second min module No._2 | 簇内单体次最小温度+编号 | 0.01℃ | INT16
23420[40Regs] | R |  | Cluster No.1-No.20 warning status_2 |  |  | UINT32 | Each bit means one cluster. 0: warning 1:normal or warning recovery
23460[40Regs] | R |  | Cluster No.1-No.20 protection status_2 |  |  | UINT32 | Each bit means one cluster. 0: warning 1:normal or fault recovery
23500 | R | BMS maximum cell voltage_2 | BMS maximum cell voltage _2 | 堆内单体最大电压值 | 0.0001V | UINT16
23501 | R | Cluster index ofthe BMS maximum cell_2 | Cluster index ofthe BMS maximum cell_2 | 堆内最大电压单体簇号 |  | UINT16
23502 | R | Module index of the BMS maximum cell voltage_2 | Module index of the BMS maximum cell voltage_2 | 堆内最大电压单体模组号 |  | UINT16
23503 | R | BMS minimum cell voltage_2 | BMS minimum cell voltage_2 | 堆内单体最小电压值 | 0.0001V | UINT16
23504 | R | Cluster index of the BMS minimum cell_2 | Cluster index ofthe BMS minimum cell_2 | 堆内最小电压单体簇号 |  | UINT16
23505 | R | Module index of the BMS minimum cell voltage_2 | Module index of the BMS minimum cell voltage _2 | 堆内最小电压单体模组编号 |  | UINT16
23506 | R | BMS maximum cell temperature_2 | BMS maximum cell temperature_2 | 堆内单体最大温度值 | 0.01℃ | INT16
23507 | R | Cluster index of BMS maximum temperature_2 | Cluster index of BMS maximum temperature_2 | 堆内最大温度单体簇号 |  | UINT16
23508 | R | Module index of BMS maximum temperature_2 | Module index of BMS maximum temperature_2 | 堆内最大温度单体模组编号 |  | UINT16
23509 | R | BMS minimum cell temperature_2 | BMS minimum cell temperature | 堆内单体最小温度值 | 0.01℃ | INT16
23510 | R | Cluster index of BMS maximum temperature_2 | Cluster index of BMS maximum temperature | 堆内最小温度单体簇号 |  | UINT16
23511 | R | Module index of BMS minimum temperature_2 | Module index of BMS minimum temperature | 堆内最小温度单体模组编号 |  | UINT16
23512 | R | BMS bus voltage_2 | BMS bus voltage_2 | BMS母线电压 | 0.1V | UINT16
23513 | R | BMS bus current_2 | BMS bus current_2 | BMS母线电流 | 0.1A | INT16
23514 | R | BMS SOC_2 | BMS SOC_2 | BMS SOC值 | 0.1% | UINT16
23515 | R | BMS power_2 | BMS power_2 | BMS功率 | 0.1kW | INT16
23516 | R |  | BMS SOH_2 |  | 0.1% | UINT16
23517 | R | Operation status_2 | Operation status_2 | 充放电状态 |  | UINT16 | 0：rest 1：charge 2：discharge
23518[2Regs] | R | BMS current chargeable energy_2 | BMS current chargeable energy_2 | BMS当前可充电量 | 0.001kWh | UINT32
23520[2Regs] | R | BMS current dischargeable energy_2 | BMS current dischargeable energy_2 | BMS当前可放电量 | 0.001kWh | UINT32
23522[2Regs] | R | Power limit state_high byte_2 | Power limit state_high byte_2 | BMS限功率状态字高字 |  | UINT32
23524[2Regs] | R | Power limit state_low byte_2 | Power limit state_low byte_2 | BMS限功率状态字低字 |  | UINT32
23526[4Regs] | R |  | Power limit state_res |  |  | UINT64
23530[2Regs] | R | BMS alarm state_high byte_2 | BMS alarm state_high byte_2 | BMS告警状态字高字 |  | UINT32
23532[2Regs] | R | BMS alarm state_low byte_2 | BMS alarm state_low byte_2 | BMS告警状态字低字 |  | UINT32
23534[4Regs] | R |  | BMS alarm state_res |  |  | UINT64
23538[2Regs] | R | BMS fault state_high byte_2 | BMS fault state_high byte_2 | BMS故障状态字高字 |  | UINT32
23540[2Regs] | R | BMS fault state_low byte_2 | BMS fault state_low byte_2 | BMS故障状态字低字 |  | UINT32
23542[4Regs] | R |  | BMS fault state_res |  |  | UINT64
23546 | R | Cluster online number_2 | Cluster online number_2 | 在线的簇的数量 |  | UINT16
23547 | R | Circuit breaker control word_2 | Circuit breaker control word_2 | 断路器控制字 |  | UINT16 | One bit for one cluster, 0：open；1：close
23548 | R | Main circuit breaker status_2 | DC breaker status_2 | 总断路器 |  | UINT16 | 0：open；1：close
23549 | R | Maximum charging power limit_2 | Maximum charging power limit_2 | 最大可充电功率 | 1kW | UINT16
23550 | R | Maximum discharging power limit_2 | Maximum discharging power limit_2 | 最大可放电功率 | 1kW | UINT16
23551 | R |  | Local/Remote mode of DC breaker_2 |  |  | UINT16 | 1+B156:H193:Remote 2:Local
预留
EMMU1 - System Data
24000 | R |  | 1-1 average temperature |  | 0.01℃ | INT16
24001 | R |  | 1-1 max. temperature |  | 0.01℃ | INT16
24002 | R |  | 1-1 Pack index of max. cell temperature |  |  | UINT16
24003 | R |  | 1-1 Cell index of max. cell temperature |  |  | UINT16
24004 | R |  | 1-1 min. temperature |  | 0.01℃ | INT16
24005 | R |  | 1-1 Pack index of min. cell temperature |  |  | UINT16
24006 | R |  | 1-1 Cell index of min. cell temperature |  |  | UINT16
24007 | R |  | 1-2 average temperature |  | 0.01℃ | INT16
24008 | R |  | 1-2 max. temperature |  | 0.01℃ | INT16
24009 | R |  | 1-2 Pack index of max. cell temperature |  |  | UINT16
24010 | R |  | 1-2 Cell index of max. cell temperature |  |  | UINT16
24011 | R |  | 1-2 min. temperature |  | 0.01℃ | INT16
24012 | R |  | 1-2 Pack index of min. cell temperature |  |  | UINT16
24013 | R |  | 1-2 Cell index of min. cell temperature |  |  | UINT16
24014 | R |  | 1-3 average temperature |  | 0.01℃ | INT16
24015 | R |  | 1-3 max. temperature |  | 0.01℃ | INT16
24016 | R |  | 1-3 Pack index of max. cell temperature |  |  | UINT16
24017 | R |  | 1-3 Cell index of max. cell temperature |  |  | UINT16
24018 | R |  | 1-3 min. temperature |  | 0.01℃ | INT16
24019 | R |  | 1-3 Pack index of min. cell temperature |  |  | UINT16
24020 | R |  | 1-3 Cell index of min. cell temperature |  |  | UINT16
24021 | R |  | 1-4 average temperature |  | 0.01℃ | INT16
24022 | R |  | 1-4 max. temperature |  | 0.01℃ | INT16
24023 | R |  | 1-4 Pack index of max. cell temperature |  |  | UINT16
24024 | R |  | 1-4 Cell index of max. cell temperature |  |  | UINT16
24025 | R |  | 1-4 min. temperature |  | 0.01℃ | INT16
24026 | R |  | 1-4 Pack index of min. cell temperature |  |  | UINT16
24027 | R |  | 1-4 Cell index of min. cell temperature |  |  | UINT16
24028 | R |  | 1-5 average temperature |  | 0.01℃ | INT16
24029 | R |  | 1-5 max. temperature |  | 0.01℃ | INT16
24030 | R |  | 1-5 Pack index of max. cell temperature |  |  | UINT16
24031 | R |  | 1-5 Cell index of max. cell temperature |  |  | UINT16
24032 | R |  | 1-5 min. temperature |  | 0.01℃ | INT16
24033 | R |  | 1-5 Pack index of min. cell temperature |  |  | UINT16
24034 | R |  | 1-5 Cell index of min. cell temperature |  |  | UINT16
24035 | R |  | 1-6 average temperature |  | 0.01℃ | INT16
24036 | R |  | 1-6 max. temperature |  | 0.01℃ | INT16
24037 | R |  | 1-6 Pack index of max. cell temperature |  |  | UINT16
24038 | R |  | 1-6 Cell index of max. cell temperature |  |  | UINT16
24039 | R |  | 1-6 min. temperature |  | 0.01℃ | INT16
24040 | R |  | 1-6 Pack index of min. cell temperature |  |  | UINT16
24041 | R |  | 1-6 Cell index of min. cell temperature |  |  | UINT16
24042 | R |  | 1-7 average temperature |  | 0.01℃ | INT16
24043 | R |  | 1-7 max. temperature |  | 0.01℃ | INT16
24044 | R |  | 1-7 Pack index of max. cell temperature |  |  | UINT16
24045 | R |  | 1-7 Cell index of max. cell temperature |  |  | UINT16
24046 | R |  | 1-7 min. temperature |  | 0.01℃ | INT16
24047 | R |  | 1-7 Pack index of min. cell temperature |  |  | UINT16
24048 | R |  | 1-7 Cell index of min. cell temperature |  |  | UINT16
24049 | R |  | 1-8 average temperature |  | 0.01℃ | INT16
24050 | R |  | 1-8 max. temperature |  | 0.01℃ | INT16
24051 | R |  | 1-8 Pack index of max. cell temperature |  |  | UINT16
24052 | R |  | 1-8 Cell index of max. cell temperature |  |  | UINT16
24053 | R |  | 1-8 min. temperature |  | 0.01℃ | INT16
24054 | R |  | 1-8 Pack index of min. cell temperature |  |  | UINT16
24055 | R |  | 1-8 Cell index of min. cell temperature |  |  | UINT16
24056 | R |  | 1-9 average temperature |  | 0.01℃ | INT16
24057 | R |  | 1-9 max. temperature |  | 0.01℃ | INT16
24058 | R |  | 1-9 Pack index of max. cell temperature |  |  | UINT16
24059 | R |  | 1-9 Cell index of max. cell temperature |  |  | UINT16
24060 | R |  | 1-9 min. temperature |  | 0.01℃ | INT16
24061 | R |  | 1-9 Pack index of min. cell temperature |  |  | UINT16
24062 | R |  | 1-9 Cell index of min. cell temperature |  |  | UINT16
24063 | R |  | 1-10 average temperature |  | 0.01℃ | INT16
24064 | R |  | 1-10 max. temperature |  | 0.01℃ | INT16
24065 | R |  | 1-10 Pack index of max. cell temperature |  |  | UINT16
24066 | R |  | 1-10 Cell index of max. cell temperature |  |  | UINT16
24067 | R |  | 1-10 min. temperature |  | 0.01℃ | INT16
24068 | R |  | 1-10 Pack index of min. cell temperature |  |  | UINT16
24069 | R |  | 1-10 Cell index of min. cell temperature |  |  | UINT16
24070 | R |  | 1-11 average temperature |  | 0.01℃ | INT16
24071 | R |  | 1-11 max. temperature |  | 0.01℃ | INT16
24072 | R |  | 1-11 Pack index of max. cell temperature |  |  | UINT16
24073 | R |  | 1-11 Cell index of max. cell temperature |  |  | UINT16
24074 | R |  | 1-11 min. temperature |  | 0.01℃ | INT16
24075 | R |  | 1-11 Pack index of min. cell temperature |  |  | UINT16
24076 | R |  | 1-11 Cell index of min. cell temperature |  |  | UINT16
24077 | R |  | 1-12 average temperature |  | 0.01℃ | INT16
24078 | R |  | 1-12 max. temperature |  | 0.01℃ | INT16
24079 | R |  | 1-12 Pack index of max. cell temperature |  |  | UINT16
24080 | R |  | 1-12 Cell index of max. cell temperature |  |  | UINT16
24081 | R |  | 1-12 min. temperature |  | 0.01℃ | INT16
24082 | R |  | 1-12 Pack index of min. cell temperature |  |  | UINT16
24083 | R |  | 1-12 Cell index of min. cell temperature |  |  | UINT16
24084 | R |  | 1-13 average temperature |  | 0.01℃ | INT16
24085 | R |  | 1-13 max. temperature |  | 0.01℃ | INT16
24086 | R |  | 1-13 Pack index of max. cell temperature |  |  | UINT16
24087 | R |  | 1-13 Cell index of max. cell temperature |  |  | UINT16
24088 | R |  | 1-13 min. temperature |  | 0.01℃ | INT16
24089 | R |  | 1-13 Pack index of min. cell temperature |  |  | UINT16
24090 | R |  | 1-13 Cell index of min. cell temperature |  |  | UINT16
24091 | R |  | 1-14 average temperature |  | 0.01℃ | INT16
24092 | R |  | 1-14 max. temperature |  | 0.01℃ | INT16
24093 | R |  | 1-14 Pack index of max. cell temperature |  |  | UINT16
24094 | R |  | 1-14 Cell index of max. cell temperature |  |  | UINT16
24095 | R |  | 1-14 min. temperature |  | 0.01℃ | INT16
24096 | R |  | 1-14 Pack index of min. cell temperature |  |  | UINT16
24097 | R |  | 1-14 Cell index of min. cell temperature |  |  | UINT16
24098 | R |  | Stack overall average cell temperature | Stack overall average cell temperature | 0.01℃ | INT16
24099 | R |  | Average ambient temperature inside the container | Average ambient temperature inside the container | 0.01℃ | INT16
24100 | R |  | Average ambient humidity inside the container | Average ambient humidity inside the container | 0.01%RH | UINT16
24101 | R |  | Maximum cell temperature | Maximum cell temperature | 0.01℃ | INT16
24102 | R |  | Cluster index of maximum cell temperature | Stack index of maximum cell temperature | 1 | UINT16
24103 | R |  | Pack index of maximum cell temperature | Cluster index of maximum cell temperature | 1 | UINT16
24104 | R |  | Cell index of Maximum cell temperature | Pack index of maximum cell temperature | 1 | UINT16
24105 | R |  | Minimum cell temperature | Minimum cell temperature | 0.01℃ | INT16
24106 | R |  | Cluster index of Minimum cell temperature | Stack index ofMinimum cell temperature | 1 | UINT16
24107 | R |  | Pack index of Minimum cell temperature | Cluster index of Minimum cell temperature | 1 | UINT16
24108 | R |  | Cell index of Minimum cell temperature | Pack index of Minimum cell temperature | 1 | UINT16
24109 | R |  | BAMS online status | BAMS online status | 1 | UINT16
24110 | R |  | Air conditioner online status | Air conditioner online status | 1 | UINT16
24111 | R |  | Temperature and humidity sensor online status | Temperature and humidity sensor online status | 1 | UINT16
24112 | R |  | Meter online status | Meter online status | 1 | UINT16
24113 | R |  | Gas sensor online status | Gas sensor online status | 1 | UINT16
24114 | R |  | Number of online BAMS | Number of online BAMS | 1 | UINT16
24115 | R |  | Number of online air conditioners | Number of online air conditioners | 1 | UINT16
24116 | R |  | Number of online temperature and humidity | Number of online temperature and humidity | 1 | UINT16
24117 | R |  | Number of online Meters | Number of online Meters | 1 | UINT16
24118 | R |  | Number of online gas sensors | Number of online gas sensors | 1 | UINT16
24119[2Regs] | R |  | ararm1_state | ararm1_state | 1 | UINT32
24121[2Regs] | R |  | ararm2_state | ararm2_state | 1 | UINT32
24123[2Regs] | R |  | fault1_state | fault1_state | 1 | UINT32
24125[2Regs] | R |  | fault2_state | fault2_state | 1 | UINT32
EMMU1 - Gas sensor Data
24200[2Regs] | R |  | Carbon monoxide concentration | Carbon monoxide concentration | 0.01ppm | UINT32
24202[2Regs] | R |  | Hydrogen concentration | Hydrogen concentration | 0.01ppm | UINT32
24204[2Regs] | R |  | Oxygen concentration | Oxygen concentration | 0.01ppm | UINT32
24206 | R |  | Carbon monoxide alarm status | Carbon monoxide alarm status | 1 | UINT16 | 0:normal 1:alarm
24207 | R |  | Hydrogen alarm status | Hydrogen alarm status | 1 | UINT16 | 0:normal 1:alarm
24208 | R |  | Oxygen alarm status | Oxygen alarm status | 1 | UINT16 | 0:normal 1:alarm
EMMU1 - Ambient temperature and humidity sensor Data
24300 | R |  | Temperature reading of temperature and humidity sensor No. 1 | Temperature reading of temperature and humidity sensor No. 1 | 0.01℃ | INT16
24301 | R |  | Temperature reading of temperature and humidity sensor No. 2 | Temperature reading of temperature and humidity sensor No. 2 | 0.01℃ | INT16
24302 | R |  | Temperature reading of temperature and humidity sensor No. 3 | Temperature reading of temperature and humidity sensor No. 3 | 0.01℃ | INT16
24303 | R |  | Humidity reading of temperature and humidity sensor No.1 | Humidity reading of temperature and humidity sensor No.1 | 0.01%RH | INT16
24304 | R |  | Humidity reading of temperature and humidity sensor No.2 | Humidity reading of temperature and humidity sensor No.2 | 0.01%RH | INT16
24305 | R |  | Humidity reading of temperature and humidity sensor No.3 | Humidity reading of temperature and humidity sensor No.3 | 0.01%RH | INT16
EMMU1 - Air conditioning data
24400 | R |  | Air conditioner1 mode | Air conditioner1 current mode | 1 | UINT16 | 0:stop 1:run
24401 | R |  | Air conditioner1 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
24402 | R |  | Air conditioner1 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
24403 | R |  | Air conditioner1 humidity |  | 0.01%RH | UINT16
24404 | R |  | Air conditioner1 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
24405 | R |  | Air conditioner1 current value |  | 0.1A | INT16
24404 | R |  | Air conditioner2 mode | Air conditioner1 current mode | 1 | UINT16
24405 | R |  | Air conditioner2 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
24406 | R |  | Air conditioner2 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
24407 | R |  | Air conditioner2 humidity |  | 0.01%RH | UINT16
24410 | R |  | Air conditioner2 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
24411 | R |  | Air conditioner2 current value |  | 0.1A | INT16
24408 | R |  | Air conditioner3 mode | Air conditioner1 current mode | 1 | UINT16
24409 | R |  | Air conditioner3 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
24410 | R |  | Air conditioner3 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
24411 | R |  | Air conditioner3 humidity |  | 0.01%RH | UINT16
24416 | R |  | Air conditioner3 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
24417 | R |  | Air conditioner3 current value |  | 0.1A | INT16
24412 | R |  | Air conditioner4 mode | Air conditioner1 current mode | 1 | UINT16
24413 | R |  | Air conditioner4 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
24414 | R |  | Air conditioner4 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
24415 | R |  | Air conditioner4 humidity |  | 0.01%RH | UINT16
24422 | R |  | Air conditioner4 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
24423 | R |  | Air conditioner4 current value |  | 0.1A | INT16
EMMU1 - Meter
24500[2Regs] | R |  | Phase A active power |  | 0.001kW | INT32
24502[2Regs] | R |  | Phase B active power |  | 0.001kW | INT32
24504[2Regs] | R |  | Phase C active power |  | 0.001kW | INT32
24506[2Regs] | R |  | Active power |  | 0.001kW | INT32
24508[2Regs] | R |  | Reactive power |  | 0.001kVar | INT32
24510 | R |  | Apparent power |  | 0.001kVA | INT32
24511 | R |  | Power factor |  | 0.001 | UINT16
24512[2Regs] | R |  | Power frequency |  | 0.01Hz | UINT16
24514[2Regs] | R |  | Forward active energy |  | 0.01kWh | INT32
24516[2Regs] | R |  | Backward active energy |  | 0.01kWh | INT32
24518[2Regs] | R |  | Total active energy |  | 0.01kWh | INT32
24520[2Regs] |  |  | Res |  |  | UINT32
24522 | R |  | Voltage unbalance |  | 0.01% | UINT16
24523 | R |  | Current unbalance |  | 0.01% | UINT16
24524 | R |  | Alarm status |  |  | UINT16
EMMU1 - Event
24600 | R |  | Event1_Year |  |  | UINT16
24601 | R |  | Event1_Month |  |  | UINT16
24602 | R |  | Event1_Day |  |  | UINT16
24603 | R |  | Event1_Hour |  |  | UINT16
24604 | R |  | Event1_Minute |  |  | UINT16
24605 | R |  | Event1_Second |  |  | UINT16
24606 | R |  | Event1_Code |  |  | UINT16
24607 | R |  | Event1_State |  |  | UINT16
24608 | R |  | Event2_Year |  |  | UINT16
24609 | R |  | Event2_Month |  |  | UINT16
24610 | R |  | Event2_Day |  |  | UINT16
24611 | R |  | Event2_Hour |  |  | UINT16
24612 | R |  | Event2_Minute |  |  | UINT16
24613 | R |  | Event2_Second |  |  | UINT16
24614 | R |  | Event2_Code |  |  | UINT16
24615 | R |  | Event2_State |  |  | UINT16
… | R |  | Event3-Event10 |  |  | UINT16
EMMU2 - System Data
25000 | R |  | 1-1 average temperature |  | 0.01℃ | INT16
25001 | R |  | 1-1 max. temperature |  | 0.01℃ | INT16
25002 | R |  | 1-1 Pack index of max. cell temperature |  |  | UINT16
25003 | R |  | 1-1 Cell index of max. cell temperature |  |  | UINT16
25004 | R |  | 1-1 min. temperature |  | 0.01℃ | INT16
25005 | R |  | 1-1 Pack index of min. cell temperature |  |  | UINT16
25006 | R |  | 1-1 Cell index of min. cell temperature |  |  | UINT16
25007 | R |  | 1-2 average temperature |  | 0.01℃ | INT16
25008 | R |  | 1-2 max. temperature |  | 0.01℃ | INT16
25009 | R |  | 1-2 Pack index of max. cell temperature |  |  | UINT16
25010 | R |  | 1-2 Cell index of max. cell temperature |  |  | UINT16
25011 | R |  | 1-2 min. temperature |  | 0.01℃ | INT16
25012 | R |  | 1-2 Pack index of min. cell temperature |  |  | UINT16
25013 | R |  | 1-2 Cell index of min. cell temperature |  |  | UINT16
25014 | R |  | 1-3 average temperature |  | 0.01℃ | INT16
25015 | R |  | 1-3 max. temperature |  | 0.01℃ | INT16
25016 | R |  | 1-3 Pack index of max. cell temperature |  |  | UINT16
25017 | R |  | 1-3 Cell index of max. cell temperature |  |  | UINT16
25018 | R |  | 1-3 min. temperature |  | 0.01℃ | INT16
25019 | R |  | 1-3 Pack index of min. cell temperature |  |  | UINT16
25020 | R |  | 1-3 Cell index of min. cell temperature |  |  | UINT16
25021 | R |  | 1-4 average temperature |  | 0.01℃ | INT16
25022 | R |  | 1-4 max. temperature |  | 0.01℃ | INT16
25023 | R |  | 1-4 Pack index of max. cell temperature |  |  | UINT16
25024 | R |  | 1-4 Cell index of max. cell temperature |  |  | UINT16
25025 | R |  | 1-4 min. temperature |  | 0.01℃ | INT16
25026 | R |  | 1-4 Pack index of min. cell temperature |  |  | UINT16
25027 | R |  | 1-4 Cell index of min. cell temperature |  |  | UINT16
25028 | R |  | 1-5 average temperature |  | 0.01℃ | INT16
25029 | R |  | 1-5 max. temperature |  | 0.01℃ | INT16
25030 | R |  | 1-5 Pack index of max. cell temperature |  |  | UINT16
25031 | R |  | 1-5 Cell index of max. cell temperature |  |  | UINT16
25032 | R |  | 1-5 min. temperature |  | 0.01℃ | INT16
25033 | R |  | 1-5 Pack index of min. cell temperature |  |  | UINT16
25034 | R |  | 1-5 Cell index of min. cell temperature |  |  | UINT16
25035 | R |  | 1-6 average temperature |  | 0.01℃ | INT16
25036 | R |  | 1-6 max. temperature |  | 0.01℃ | INT16
25037 | R |  | 1-6 Pack index of max. cell temperature |  |  | UINT16
25038 | R |  | 1-6 Cell index of max. cell temperature |  |  | UINT16
25039 | R |  | 1-6 min. temperature |  | 0.01℃ | INT16
25040 | R |  | 1-6 Pack index of min. cell temperature |  |  | UINT16
25041 | R |  | 1-6 Cell index of min. cell temperature |  |  | UINT16
25042 | R |  | 1-7 average temperature |  | 0.01℃ | INT16
25043 | R |  | 1-7 max. temperature |  | 0.01℃ | INT16
25044 | R |  | 1-7 Pack index of max. cell temperature |  |  | UINT16
25045 | R |  | 1-7 Cell index of max. cell temperature |  |  | UINT16
25046 | R |  | 1-7 min. temperature |  | 0.01℃ | INT16
25047 | R |  | 1-7 Pack index of min. cell temperature |  |  | UINT16
25048 | R |  | 1-7 Cell index of min. cell temperature |  |  | UINT16
25049 | R |  | 1-8 average temperature |  | 0.01℃ | INT16
25050 | R |  | 1-8 max. temperature |  | 0.01℃ | INT16
25051 | R |  | 1-8 Pack index of max. cell temperature |  |  | UINT16
25052 | R |  | 1-8 Cell index of max. cell temperature |  |  | UINT16
25053 | R |  | 1-8 min. temperature |  | 0.01℃ | INT16
25054 | R |  | 1-8 Pack index of min. cell temperature |  |  | UINT16
25055 | R |  | 1-8 Cell index of min. cell temperature |  |  | UINT16
25056 | R |  | 1-9 average temperature |  | 0.01℃ | INT16
25057 | R |  | 1-9 max. temperature |  | 0.01℃ | INT16
25058 | R |  | 1-9 Pack index of max. cell temperature |  |  | UINT16
25059 | R |  | 1-9 Cell index of max. cell temperature |  |  | UINT16
25060 | R |  | 1-9 min. temperature |  | 0.01℃ | INT16
25061 | R |  | 1-9 Pack index of min. cell temperature |  |  | UINT16
25062 | R |  | 1-9 Cell index of min. cell temperature |  |  | UINT16
25063 | R |  | 1-10 average temperature |  | 0.01℃ | INT16
25064 | R |  | 1-10 max. temperature |  | 0.01℃ | INT16
25065 | R |  | 1-10 Pack index of max. cell temperature |  |  | UINT16
25066 | R |  | 1-10 Cell index of max. cell temperature |  |  | UINT16
25067 | R |  | 1-10 min. temperature |  | 0.01℃ | INT16
25068 | R |  | 1-10 Pack index of min. cell temperature |  |  | UINT16
25069 | R |  | 1-10 Cell index of min. cell temperature |  |  | UINT16
25070 | R |  | 1-11 average temperature |  | 0.01℃ | INT16
25071 | R |  | 1-11 max. temperature |  | 0.01℃ | INT16
25072 | R |  | 1-11 Pack index of max. cell temperature |  |  | UINT16
25073 | R |  | 1-11 Cell index of max. cell temperature |  |  | UINT16
25074 | R |  | 1-11 min. temperature |  | 0.01℃ | INT16
25075 | R |  | 1-11 Pack index of min. cell temperature |  |  | UINT16
25076 | R |  | 1-11 Cell index of min. cell temperature |  |  | UINT16
25077 | R |  | 1-12 average temperature |  | 0.01℃ | INT16
25078 | R |  | 1-12 max. temperature |  | 0.01℃ | INT16
25079 | R |  | 1-12 Pack index of max. cell temperature |  |  | UINT16
25080 | R |  | 1-12 Cell index of max. cell temperature |  |  | UINT16
25081 | R |  | 1-12 min. temperature |  | 0.01℃ | INT16
25082 | R |  | 1-12 Pack index of min. cell temperature |  |  | UINT16
25083 | R |  | 1-12 Cell index of min. cell temperature |  |  | UINT16
25084 | R |  | 1-13 average temperature |  | 0.01℃ | INT16
25085 | R |  | 1-13 max. temperature |  | 0.01℃ | INT16
25086 | R |  | 1-13 Pack index of max. cell temperature |  |  | UINT16
25087 | R |  | 1-13 Cell index of max. cell temperature |  |  | UINT16
25088 | R |  | 1-13 min. temperature |  | 0.01℃ | INT16
25089 | R |  | 1-13 Pack index of min. cell temperature |  |  | UINT16
25090 | R |  | 1-13 Cell index of min. cell temperature |  |  | UINT16
25091 | R |  | 1-14 average temperature |  | 0.01℃ | INT16
25092 | R |  | 1-14 max. temperature |  | 0.01℃ | INT16
25093 | R |  | 1-14 Pack index of max. cell temperature |  |  | UINT16
25094 | R |  | 1-14 Cell index of max. cell temperature |  |  | UINT16
25095 | R |  | 1-14 min. temperature |  | 0.01℃ | INT16
25096 | R |  | 1-14 Pack index of min. cell temperature |  |  | UINT16
25097 | R |  | 1-14 Cell index of min. cell temperature |  |  | UINT16
25098 | R |  | Stack overall average cell temperature | Stack overall average cell temperature | 0.01℃ | INT16
25099 | R |  | Average ambient temperature inside the container | Average ambient temperature inside the container | 0.01℃ | INT16
25100 | R |  | Average ambient humidity inside the container | Average ambient humidity inside the container | 0.01%RH | UINT16
25101 | R |  | Maximum cell temperature | Maximum cell temperature | 0.01℃ | INT16
25102 | R |  | Cluster index of maximum cell temperature | Stack index of maximum cell temperature | 1 | UINT16
25103 | R |  | Pack index of maximum cell temperature | Cluster index of maximum cell temperature | 1 | UINT16
25104 | R |  | Cell index of Maximum cell temperature | Pack index of maximum cell temperature | 1 | UINT16
25105 | R |  | Minimum cell temperature | Minimum cell temperature | 0.01℃ | INT16
25106 | R |  | Cluster index of Minimum cell temperature | Stack index ofMinimum cell temperature | 1 | UINT16
25107 | R |  | Pack index of Minimum cell temperature | Cluster index of Minimum cell temperature | 1 | UINT16
25108 | R |  | Cell index of Minimum cell temperature | Pack index of Minimum cell temperature | 1 | UINT16
25109 | R |  | BAMS online status | BAMS online status | 1 | UINT16
25110 | R |  | Air conditioner online status | Air conditioner online status | 1 | UINT16
25111 | R |  | Temperature and humidity sensor online status | Temperature and humidity sensor online status | 1 | UINT16
25112 | R |  | Meter online status | Meter online status | 1 | UINT16
25113 | R |  | Gas sensor online status | Gas sensor online status | 1 | UINT16
25114 | R |  | Number of online BAMS | Number of online BAMS | 1 | UINT16
25115 | R |  | Number of online air conditioners | Number of online air conditioners | 1 | UINT16
25116 | R |  | Number of online temperature and humidity | Number of online temperature and humidity | 1 | UINT16
25117 | R |  | Number of online Meters | Number of online Meters | 1 | UINT16
25118 | R |  | Number of online gas sensors | Number of online gas sensors | 1 | UINT16
25119[2Regs] | R |  | ararm1_state | ararm1_state | 1 | UINT32
25121[2Regs] | R |  | ararm2_state | ararm2_state | 1 | UINT32
25123[2Regs] | R |  | fault1_state | fault1_state | 1 | UINT32
25125[2Regs] | R |  | fault2_state | fault2_state | 1 | UINT32
EMMU2 - Gas sensor Data
25200[2Regs] | R |  | Carbon monoxide concentration | Carbon monoxide concentration | 0.01ppm | UINT32
25202[2Regs] | R |  | Hydrogen concentration | Hydrogen concentration | 0.01ppm | UINT32
25204[2Regs] | R |  | Oxygen concentration | Oxygen concentration | 0.01ppm | UINT32
25206 | R |  | Carbon monoxide alarm status | Carbon monoxide alarm status | 1 | UINT16 | 0:normal 1:alarm
25207 | R |  | Hydrogen alarm status | Hydrogen alarm status | 1 | UINT16 | 0:normal 1:alarm
25208 | R |  | Oxygen alarm status | Oxygen alarm status | 1 | UINT16 | 0:normal 1:alarm
EMMU2 - Ambient temperature and humidity sensor Data
25300 | R |  | Temperature reading of temperature and humidity sensor No. 1 | Temperature reading of temperature and humidity sensor No. 1 | 0.01℃ | INT16
25301 | R |  | Temperature reading of temperature and humidity sensor No. 2 | Temperature reading of temperature and humidity sensor No. 2 | 0.01℃ | INT16
25302 | R |  | Temperature reading of temperature and humidity sensor No. 3 | Temperature reading of temperature and humidity sensor No. 3 | 0.01℃ | INT16
25303 | R |  | Humidity reading of temperature and humidity sensor No.1 | Humidity reading of temperature and humidity sensor No.1 | 0.01%RH | INT16
25304 | R |  | Humidity reading of temperature and humidity sensor No.2 | Humidity reading of temperature and humidity sensor No.2 | 0.01%RH | INT16
25305 | R |  | Humidity reading of temperature and humidity sensor No.3 | Humidity reading of temperature and humidity sensor No.3 | 0.01%RH | INT16
EMMU2 - Air conditioning data
25400 | R |  | Air conditioner1 mode | Air conditioner1 current mode | 1 | UINT16
25401 | R |  | Air conditioner1 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
25402 | R |  | Air conditioner1 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
25403 | R |  | Air conditioner1 humidity |  | 0.01%RH | UINT16
25404 | R |  | Air conditioner1 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
25405 | R |  | Air conditioner1 current value |  | 0.1A | INT16
25406 | R |  | Air conditioner2 mode | Air conditioner1 current mode | 1 | UINT16
25407 | R |  | Air conditioner2 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
25408 | R |  | Air conditioner2 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
25409 | R |  | Air conditioner2 humidity |  | 0.01%RH | UINT16
25410 | R |  | Air conditioner2 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
25411 | R |  | Air conditioner2 current value |  | 0.1A | INT16
25412 | R |  | Air conditioner3 mode | Air conditioner1 current mode | 1 | UINT16
25413 | R |  | Air conditioner3 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
25414 | R |  | Air conditioner3 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
25415 | R |  | Air conditioner3 humidity |  | 0.01%RH | UINT16
25416 | R |  | Air conditioner3 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
25417 | R |  | Air conditioner3 current value |  | 0.1A | INT16
25418 | R |  | Air conditioner4 mode | Air conditioner1 current mode | 1 | UINT16
25419 | R |  | Air conditioner4 temperature(Indoor) | Air conditioner1 temperature | 0.01℃ | INT16
25420 | R |  | Air conditioner4 temperature(Outdoor) | Air conditioner1 humidity | 0.01℃ | INT16
25421 | R |  | Air conditioner4 humidity |  | 0.01%RH | UINT16
25422 | R |  | Air conditioner4 exhaust gas temperature | Air conditioner1 humidity | 0.01℃ | INT16
25423 | R |  | Air conditioner4 current value |  | 0.1A | INT16
EMMU2 - Meter
25500[2Regs] | R |  | Phase A active power |  | 0.001kW | INT32
25502[2Regs] | R |  | Phase B active power |  | 0.001kW | INT32
25504[2Regs] | R |  | Phase C active power |  | 0.001kW | INT32
25506[2Regs] | R |  | Active power |  | 0.001kW | INT32
25508[2Regs] | R |  | Reactive power |  | 0.001kVar | INT32
25510 | R |  | Apparent power |  | 0.001kVA | INT32
25511 | R |  | Power factor |  | 0.001 | UINT16
25512[2Regs] | R |  | Power frequency |  | 0.01Hz | UINT16
25514[2Regs] | R |  | Forward active energy |  | 0.01kWh | INT32
25516[2Regs] | R |  | Backward active energy |  | 0.01kWh | INT32
25518[2Regs] | R |  | Total active energy |  | 0.01kWh | INT32
2520[2Regs] |  |  | Res |  |  | UINT32
25522 | R |  | Voltage unbalance |  | 0.01% | UINT16
25523 | R |  | Current unbalance |  | 0.01% | UINT16
25524 | R |  | Alarm status |  |  | UINT16
预留
EMMU2 - Event
24600 | R |  | Event1_Year |  |  | UINT16
24601 | R |  | Event1_Month |  |  | UINT16
24602 | R |  | Event1_Day |  |  | UINT16
24603 | R |  | Event1_Hour |  |  | UINT16
24604 | R |  | Event1_Minute |  |  | UINT16
24605 | R |  | Event1_Second |  |  | UINT16
24606 | R |  | Event1_Code |  |  | UINT16
24607 | R |  | Event1_State |  |  | UINT16
24608 | R |  | Event2_Year |  |  | UINT16
24609 | R |  | Event2_Month |  |  | UINT16
24610 | R |  | Event2_Day |  |  | UINT16
24611 | R |  | Event2_Hour |  |  | UINT16
24612 | R |  | Event2_Minute |  |  | UINT16
24613 | R |  | Event2_Second |  |  | UINT16
24614 | R |  | Event2_Code |  |  | UINT16
24615 | R |  | Event2_State |  |  | UINT16
… | R |  | Event3-Event10 |  |  | UINT16
预留

## Write register
Register Address | R/W | Name | Factor/Unit | Data Type | Remark
System
10000 | R/W | Heartbeat |  | UINT16 | time internal :1s
PCS1
10100 | R/W | Run_mode |  | INT16 | 0x1111-PQ mode 0x2222-VF mode 0x3333-VSG mode
10101 | R/W | Control command |  | INT16 | 0x55AA-stop 0xAA55-start
10102 | R/W | Active power set | 0.1kW | INT16 | Valid in PQ mode:charge is negative, discharge is positive Valid in VSG mode:charge is negative, discharge is positive
10103 | R/W | Reactive power set | 0.1kVar | INT16 | Valid in PQ mode: positive-absorb reactive power, negative-send reactive power
BMS1
10110 | R/W | DC Circuit breaker |  | UINT16 | 0-Open 1-Close
10111 | R/W | Cluster contactor |  | UINT16 | 0-Open 1-Close（Each bit means one cluster）
EMMU1
10120 | R/W | Cooling Point | 0.01℃ | UINT16
10121 | R/W | Cooling Sensitivity | 0.01℃ | UINT16
10122 | R/W | Heating Point | 0.01℃ | UINT16
10123 | R/W | Heating Sensitivity | 0.01℃ | UINT16
10124 | R/W | High Temperature Point | 0.01℃ | UINT16
10125 | R/W | Low Temperature Point | 0.01℃ | UINT16
10126 | R/W | High Humidity Point | 0.01%RH | INT16
PCS2
10200 | R/W | Run_mode |  | INT16 | 0x1111-PQ mode 0x2222-VF mode 0x3333-VSG mode
10201 | R/W | Control command |  | INT16 | 0x55AA-stop 0xAA55-start
10202 | R/W | Active power set | 0.1kW | INT16 | Valid in PQ mode:charge is negative, discharge is positive Valid in VSG mode:charge is negative, discharge is positive
10203 | R/W | Reactive power set | 0.1kVar | INT16 | Valid in PQ mode: positive-absorb reactive power, negative-send reactive power
BMS2
10210 | R/W | DC Circuit breaker |  | UINT16 | 0-Open 1-Close
10211 | R/W | Cluster contactor |  | UINT16 | 0-Open 1-Close（Each bit means one cluster）
EMMU2
10220 | R/W | Cooling Point | 0.01℃ | UINT16
10221 | R/W | Cooling Sensitivity | 0.01℃ | UINT16
10222 | R/W | Heating Point | 0.01℃ | UINT16
10223 | R/W | Heating Sensitivity | 0.01℃ | UINT16
10224 | R/W | High Temperature Point | 0.01℃ | UINT16
10225 | R/W | Low Temperature Point | 0.01℃ | UINT16
10226 | R/W | High Humidity Point | 0.01%RH | INT16