## HEMSW01L1
Device Name | CATL V2
Connection Name | stuff
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device ID String | hems_pcs_1
Device IP Address (if TCP) | 10.x.x.x
Device Port (502 typical)
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical) | [14 empty] | OPTIONAL for web_ui configs only |  | required for modbus server configs only
Name | Type | Ref | Register Type | Unit | Words | Bus Scale | FIMS Scale | hexAddress | Scale | Address | Data Type | Bit | Repeat | Reg ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
System voltage | Control | G0.1 | Holding Register |  | 1 |  |  | 20 |  | 32 | uint16 |  |  | bms_system_voltage | enum | 1 = Start | /components/hems_pcs_1 | pcs_start | Yes
System Current | Control |  | Holding Register |  |  |  |  | 21 |  | 33 | uint16 |  |  | bms_system_current
SOC | Control |  | Holding Register |  |  |  |  | 22 |  | 34 | uint16
SOH | Control |  | Holding Register |  |  |  |  | 23 |  | 35 | uint16
Max cell voltage | Control |  | Holding Register |  |  |  |  | 24 |  | 36 | uint16
Min cell voltage | Control |  | Holding Register |  |  |  |  | 25 |  | 37 | uint16
Avg. cell voltage | Control |  | Holding Register |  | 1 |  |  | 26 |  | 38 | uint16 |  |  | pcs_stop |  | 1 = Stop | /components/hems_pcs_1 | pcs_stop | Yes
Max cell temperature | Control |  | Holding Register |  | 1 |  |  | 27 |  | 39 | uint16 |  |  | pcs_reset |  | 1 = Reset | /components/hems_pcs_1 | pcs_reset | Yes
Min cell temperature | Control |  | Holding Register |  | 1 |  |  | 28 |  | 40 | uint16 |  |  | pcs_e_stop |  | 1 = Estop | /components/hems_pcs_1 | pcs_e_stop | Yes
Avg. cell temperature | Control |  | Input Register |  | 1 |  |  | 29 |  | 41 | uint16 |  |  | pcs_access |  |  | /components/hems_ref_pcs_1 | pcs_access | Yes
Max charge current allowed | Control |  | Input Register |  | 1 |  |  | 002a |  | 42 | uint16 |  |  | pcs_user |  |  | /components/hems_ref_pcs_1 | pcs_user | Yes
Max discharge current allowed | Control |  | Holding Register |  | 1 |  |  | 002b |  | 43 | uint16 |  |  | pcs_user_pw |  |  | /components/hems_ref_pcs_1 | pcs_user_pw | Yes
Reserve | Control |  | Holding Register |  | 1 |  |  | 002c |  | 44 | uint16 |  |  | pcs_seconds |  |  | /components/hems_ref_pcs_1 | pcs_seconds | Yes
512 ACAN data transmit field | Control |  | Holding Register |  | 1 |  |  | 303 |  | 771 | uint16 |  |  | pcs_minutes |  |  | /components/hems_ref_pcs_1 | pcs_minutes | Yes
BMS heartbeat | Control |  | Holding Register |  | 1 |  |  | 304 |  | 772 | uint16 |  |  | pcs_hours |  |  | /components/hems_ref_pcs_1 | pcs_hours | Yes
BMS_poweron | Control |  | Holding Register |  | 1 |  |  | 305 |  | 773 | uint16 |  |  | pcs_day |  |  | /components/hems_ref_pcs_1 | pcs_day | Yes
| Control |  | Holding Register |  | 1 |  |  | 306 |  | 774 | uint16 |  |  | pcs_month |  |  | /components/hems_ref_pcs_1 | pcs_month | Yes
| Control |  | Holding Register |  | 1 |  |  | 307 |  | 775 | uint16 |  |  | pcs_year |  |  | /components/hems_ref_pcs_1 | pcs_year | Yes
| Control |  | Holding Register |  | 1 |  |  | 308 |  | 776 | int16 |  |  | pcs_utc |  |  | /components/hems_ref_pcs_1 | pcs_utc | Yes | -720 to 840
BMS_status | Control |  | Holding Register |  | 1 |  |  | 309 |  | 777 | uint16 |  |  | pcs_vdc_low |  |  | /components/hems_ref_pcs_1 | pcs_vdc_low | Yes | 0 to 1500 Volts
| Control |  | Holding Register |  | 1 | 10 |  | 030a | 0.1 | 778 | uint16 |  |  | pcs_vac_low |  |  | /components/hems_ref_pcs_1 | pcs_vac_low | Yes | 80.0 to 100.0
| Control |  | Holding Register |  | 1 | 10 |  | 030b | 0.1 | 779 | uint16 |  |  | pcs_vac_high |  |  | /components/hems_ref_pcs_1 | pcs_vac_high | Yes | 100.0 to 120
| Control |  | Holding Register |  | 1 |  |  | 030c |  | 780 | uint16 |  |  | pcs_start_delay |  |  | /components/hems_ref_pcs_1 | pcs_start_delay | Yes | 0 to 600 Seconds
| Control |  | Holding Register |  | 1 |  |  | 030d |  | 781 | uint16 |  |  | pcs_conn_mod_battery |  |  | /components/hems_ref_pcs_1 | pcs_conn_mod_battery | Yes
| Control |  | Holding Register |  | 1 |  |  | 030e |  | 782 | uint16 |  |  | pcs_start_mod_battery |  |  | /components/hems_ref_pcs_1 | pcs_start_mod_battery | Yes
Reserve | Control |  | Holding Register |  | 1 |  |  | 030f |  | 783 | uint16 |  |  | pcs_isol_mod_battery |  |  | /components/hems_ref_pcs_1 | pcs_isol_mod_battery | Yes
Number of HV connected subsystem | Control | G2.4.10 | Holding Register |  | 1 |  |  | 310 |  | 784 | uint16 |  |  | pcs_reset_mod_battery |  |  | /components/hems_ref_pcs_1 | pcs_reset_mod_battery | Yes | 0 = No, 1 = yes
Reserve | Control | G2.4.11 | Holding Register |  | 1 |  |  | 311 |  | 785 | enum |  |  | pcs_battery_config | enum | 0=Disabled, 1=Central,2=Multi | /components/hems_ref_pcs_1 | pcs_battery_config | Yes
Reserve | Control | G3.1.1 | Holding Register | % | 1 | 100 |  | 312 | 0.01 | 786 | uint16 |  |  | pcs_p_limit |  |  | /components/hems_ref_pcs_1 | pcs_p_limit | Yes | 100 = 10000
System remain charge energy | Control | G3.1.2 | Holding Register | % | 1 | 100 |  | 313 | 0.01 | 787 | uint16 |  |  | pcs_q_limit |  |  | /components/hems_ref_pcs_1 | pcs_q_limit | Yes | 0 to 150 % 100=10000
System remain discharge energy | Control | G3.1.3 | Holding Register |  | 1 |  |  |  |  | 40103 | uint16 |  |  | pcs_p_q_priority | enum | 0=P, 1= Q | /components/hems_ref_pcs_1 | pcs_p_q_priority | Yes
Reserve | Control | G3.1.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40104 | unt16 |  |  | pcs_s_limit |  |  | /components/hems_ref_pcs_1 | pcs_s_limit | Yes | 0-200% 0, to 20000
Reserve | Control | G3.1.5 | Holding Register |  | 1 |  |  |  |  | 40105 | uint16 |  |  | ps_p_algo_pri | enum | 0=min, 1=P(f) priority, 2=P(v)piority | /components/hems_ref_pcs_1 | ps_p_algo_pri | Yes
Reserve | Control | G4.7.1 | Holding Register |  | 1 |  |  |  |  | 40261 | uint16 |  |  | pcs_enable | enum | 0=No, 1=Yes | /components/hems_ref_pcs_1 | pcs_enable | Yes
Reserve | Control | G4.7.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40262 | int16 |  |  | pcs_q_ref |  |  | /components/hems_ref_pcs_1 | pcs_q_ref | Yes | -100 to 100 ,100 = 10000
Reserve | Control | G4.7.3 | Holding Register | V | 1 | 1 |  |  | 1 | 40263 | uint16 |  |  | pcs_vbus_ref |  |  | /components/hems_ref_pcs_1 | pcs_vbus_ref | Yes | 961 to 1250
Reserve | Control | G4.7.4 | Holding Register |  | 1 |  |  |  |  | 40264 | enum |  |  | pcs_night_mode_act | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_night_mode_act | Yes
Max system discharge power allowed | Control | G4.8.1.1 | Holding Register |  | 1 |  |  |  |  | 40277 | enum |  |  | pcs_enable_p_1 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_p_1 | Yes
Max system charge power allowed | Control | G4.8.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40278 | uint16 |  |  | pcs_p_grad_1 |  |  | /components/hems_ref_pcs_1 | pcs_p_grad_1 | Yes | 0.1 to 30000.0 % , 0 to 30000
BMS_limit_charge_hv | Control | G4.8.1.3 | Holding Register |  | 1 |  |  |  |  | 40279 | enum |  |  | pcs_enable_q_1 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_q_1 | Yes
BMS_limit_discharge_hv | Control | G4.8.1.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40280 | uint16 |  |  | pcs_q_grad_1 |  |  | /components/hems_ref_pcs_1 | pcs_q_grad_1 | Yes | 0.1 to 30000.0 % , 0 to 30000
Reserve | Control | G4.8.2.1 | Holding Register |  | 1 |  |  |  |  | 40281 | enum |  |  | pcs_enable_p_2 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_p_2 | Yes
P Gradient | Control | G4.8.2.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40282 | uint16 |  |  | pcs_p_grad_2 |  |  | /components/hems_ref_pcs_1 | pcs_p_grad_2 | Yes
enable Q | Control | G4.8.2.3 | Holding Register |  | 1 |  |  |  |  | 40283 | enum |  |  | pcs_enable_q_2 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_q_2 | Yes
Q Gradient | Control | G4.8.2.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40284 | uint16 |  |  | pcs_q_grad_2 |  |  | /components/hems_ref_pcs_1 | pcs_q_grad_2 | Yes
enable P | Control | G4.8.3.1 | Holding Register |  | 1 |  |  |  |  | 40285 | enum |  |  | pcs_enable_p_3 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_p_3 | Yes
P Gradient | Control | G4.8.3.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40286 | uint16 |  |  | pcs_p_grad_3 |  |  | /components/hems_ref_pcs_1 | pcs_p_grad_3 | Yes
enable Q | Control | G4.8.3.3 | Holding Register |  | 1 |  |  |  |  | 40287 | enum |  |  | pcs_enable_q_3 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_q_3 | Yes
Q Gradient | Control | G4.8.3.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40288 | uint16 |  |  | pcs_q_grad_3 |  |  | /components/hems_ref_pcs_1 | pcs_q_grad_3 | Yes
enable P | Control | G4.8.4.1 | Holding Register |  | 1 |  |  |  |  | 40289 | enum |  |  | pcs_enable_p_4 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_p_4 | Yes
P Gradient | Control | G4.8.4.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40290 | uint16 |  |  | pcs_p_grad_4 |  |  | /components/hems_ref_pcs_1 | pcs_p_grad_4 | Yes
enable Q | Control | G4.8.4.3 | Holding Register |  | 1 |  |  |  |  | 40291 | enum |  |  | pcs_enable_q_4 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_q_4 | Yes
Q Gradient | Control | G4.8.4.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40292 | uint16 |  |  | pcs_q_grad_4 |  |  | /components/hems_ref_pcs_1 | pcs_q_grad_4 | Yes
Enable | Control | G4.9.1 | Holding Register |  | 1 |  |  |  |  | 40293 | uint16 |  |  | pcs_enable_1 | enum | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_1 | Yes
Vac Out | Control | G4.9.2 | Holding Register | V | 1 |  |  |  |  | 40294 | uint16 |  |  | pcs_vac_out |  |  | /components/hems_ref_pcs_1 | pcs_vac_out | Yes
Vac min | Control | G4.9.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40295 | uint16 |  |  | pcs_vac_min |  |  | /components/hems_ref_pcs_1 | pcs_vac_min | Yes | 00 to 100, 0 to 1000
Time Start | Control | G4.9.5 | Holding Register | Sec | 1 | 10 |  |  | 0.1 | 40296 | uint16 |  |  | pcs_time_start |  |  | /components/hems_ref_pcs_1 | pcs_time_start | Yes | 0.1 to 15 s , 0 to 150
Enable 4.10.1 | Control | G4.10.1 | Holding Register |  | 1 |  |  |  |  | 40821 | uint16 |  |  | pcs_enable_G4_10_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_G4_10_1 | Yes
V1 | Control | G4.10.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 40822 | uint16 |  |  | pcs_v1 |  | 100 to g4_10_3% | /components/hems_ref_pcs_1 | pcs_v1 | Yes
V2 | Control | G4.10.3 | Holding Register | % | 1 | 100 |  |  | 0.01 | 40823 | uint16 |  |  | pcs_v2 |  | G4.10.2% to 140%, G4.10.2 to 14000 | /components/hems_ref_pcs_1 | pcs_v2 | Yes
P1 | Control | G4.10.4 | Holding Register | % | 1 | 100 |  |  | 0.01 | 40824 | uint16 |  |  | pcs_p1 |  | G4.10.5% to 100%, G4.10.5 to 10000 | /components/hems_ref_pcs_1 | pcs_p1 | Yes
P2 | Control | G4.10.5 | Holding Register | % | 1 | 100 |  |  | 0.01 | 40825 | uint16 |  |  | pcs_p2 |  | 0 to G4.10.4% , 0 to G4.10.4 | /components/hems_ref_pcs_1 | pcs_p2 | Yes
Hysteresis | Control | G4.10.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40826 | uint16 |  |  | pcs_hysteresis |  | 0 to 10%, 0 to 100 | /components/hems_ref_pcs_1 | pcs_hysteresis | Yes
Delay Hysterisis | Control | G4.10.8 | Holding Register | S | 1 | 10 |  |  | 0.1 | 40828 | uint16 |  |  | pcs_delay_hysteresis |  | 0.0 to 90 Sec, 0 to 900 | /components/hems_ref_pcs_1 | pcs_delay_hysteresis | Yes
Response Time | Control | G4.10.9 | Holding Register | S | 1 | 10 |  |  | 0.1 | 40829 | uint16 |  |  | pcs_response_tiime |  | 0.0 to 90.0s, 0 to 900 | /components/hems_ref_pcs_1 | pcs_response_tiime | Yes
Ref Power Rel | Control | G4.10.10 | Holding Register |  | 1 |  |  |  |  | 40819 | uint16 |  |  | pcs_ref_power |  | 0=rel, 1= abs | /components/hems_ref_pcs_1 | pcs_ref_power | Yes
Recover Mode | Control | G4.10.11 | Holding Register |  | 1 |  |  |  |  | 40820 | uint16 |  |  | pcs_rec_mode |  | 0=Abs, 1= Rel | /components/hems_ref_pcs_1 | pcs_rec_mode | Yes
Enable G4.11.1 | Control | G4.11.1 | Holding Register |  | 1 |  |  |  |  | 40542 | uint16 |  |  | pcs_enable_g4_11_1 |  | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_enable_g4_11_11 | Yes
V1 Threshold | Control | G4.11.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40544 | uint16 |  |  | pcs_v1_threshold |  | 100.0% to G4.11.7%, 1000 to G4.11.7 | /components/hems_ref_pcs_1 | pcs_v1_threshold | Yes
V1 Hysteresis | Control | G4.11.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40546 | uint16 |  |  | pcs_v1_hysteresis |  | 0.5 to 10%, 5 to 100 | /components/hems_ref_pcs_1 | pcs_v1_hysteresis | Yes
Grad Inj Q | Control | G4.11.4 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 40547 | uint16 |  |  | pcs_grad_inject |  | 0.1 to 200.0 %/S, 1 to 2000 | /components/hems_ref_pcs_1 | pcs_grad_inject | Yes
Grad Recover Q | Control | G4.11.5 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 40550 | uint16 |  |  | pcs_grad_recover_q |  | 0.1% to 200.0%, 1 to 2000 | /components/hems_ref_pcs_1 | pcs_grad_recover_q | Yes
CosFi limit | Control | G4.11.6 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40543 | uint16 |  |  | pcs_cosfi_limit |  | 0.80 to 1.00. 80 to 100 | /components/hems_ref_pcs_1 | pcs_cosfi_limit | Yes
V2 Threshold | Control | G4.11.7 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40545 | uint16 |  |  | pcs_v2_threshold |  | G4.11.2% to 120%, G4.11.2 to 1200 | /components/hems_ref_pcs_1 | pcs_v2_threshold | Yes
V2 Hysteresis | Control | G4.11.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40548 | uint16 |  |  | pcs_v2_hysetresis |  | 0.5 to 10%, 5 to 100 | /components/hems_ref_pcs_1 | pcs_v2_hysetresis | Yes
Grad Reduction P | Control | G4.11.9 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40549 | uint16 |  |  | pcs_grad_reduction_p |  | 0.1 to 200 %/S, 1 to 2000 | /components/hems_ref_pcs_1 | pcs_grad_reduction_p | Yes
Grad Recover P | Control | G4.11.10 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 40542 | uint16 |  |  | pcs_grad_recover_p |  | 0.1% to 200.0%, 1 to 2000 | /components/hems_ref_pcs_1 | pcs_grad_recover_p | Yes
Enable G5.1.1 | Control | G5.1.1 | Holding Register |  | 1 |  |  |  |  | 40301 | bit_field |  |  | pcs_enable_g5_1_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_g5_1_1 | Yes
Slow Protection | Control | G5.1.1.0 | Holding Register |  | 1 |  |  |  |  | 40301 | bit | 0 |  | pcs_slow_protection |  |  | /components/hems_ref_pcs_1 | pcs_slow_protection | Yes
Fast Protection | Control | G5.1.1.1 | Holding Register |  | 1 |  |  |  |  | 40301 | bit | 1 |  | pcs_fast_protection |  |  | /components/hems_ref_pcs_1 | pcs_fast_protection | Yes
Fast 2 Protection | Control | G5.1.1.2 | Holding Register |  | 1 |  |  |  |  | 40301 | bit | 2 |  | pcs_fast_2_protection |  |  | /components/hems_ref_pcs_1 | pcs_fast_2_protection | Yes
Very Fast Protection | Control | G5.1.1.3 | Holding Register |  | 1 |  |  |  |  | 40301 | bit | 3 |  | pcs_very_fast_protection |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_protection | Yes
Very Fast 2 Protection | Control | G5.1.1.4 | Holding Register |  | 1 |  |  |  |  | 40301 | bit | 4 |  | pcs_very_fast_2_protection |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_2_protection | Yes
Interpolation | Control | G5.1.1b | Holding Register |  | 1 |  |  |  |  | 40309 | uint16 |  |  | pcs_interpolation |  | 0=No, 1= Yes | /components/hems_ref_pcs_1 | pcs_interpolation | Yes
Slow Protection | Control | G5.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40302 | uint16 |  |  | pcs_slow_protection_2 |  | 0 to 100%, 10 to 1000 | /components/hems_ref_pcs_1 | pcs_slow_protection | Yes
Delay Slow Protection | Control | G5.1.3 | Holding Register | S | 1 | 100 |  |  | 0.01 | 40303 | uint16 |  |  | pcs_delay_slow_protection |  | 0.0 to 6550.0S , 0 to 65500 | /components/hems_ref_pcs_1 | pcs_delay_slow_protection | Yes
Fast Protection | Control | G5.1.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40304 | uint16 |  |  | pcs_fast_protection |  | 0 to 100%, 10 to 1000 | /components/hems_ref_pcs_1 | pcs_fast_protection | Yes
Delay Fast Protection | Control | G5.1.5 | Holding Register | S | 1 | 100 |  |  | 0.01 | 40305 | uint16 |  |  | pcs_delay_fast_protection |  | 0.0 to 6550.0S , 0 to 65500 | /components/hems_ref_pcs_1 | pcs_delay_fast_protection | Yes
Fast Protection 2 | Control | G5.1.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40376 | uint16 |  |  | pcs_fast_protection_2 |  | 0 to 100%, 10 to 1000 | /components/hems_ref_pcs_1 | pcs_fast_protection_2 | Yes
Delay Fast Protection 2 | Control | G5.1.7 | Holding Register | S | 1 | 100 |  |  | 0.01 | 40377 | uint16 |  |  | pcs_delay_fast_protection_2 |  | 0.0 to 6550.0S , 0 to 65500 | /components/hems_ref_pcs_1 | pcs_delay_fast_protection_2 | Yes
Very Fast Protection | Control | G5.1.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40306 | uint16 |  |  | pcs_very_fast_protection |  | 0 to 100%, 10 to 1000 | /components/hems_ref_pcs_1 | pcs_very_fast_protection | Yes
Delay Very Fast Protection | Control | G5.1.9 | Holding Register | S | 1 | 100 |  |  | 0.01 | 40307 | uint16 |  |  | pcs_delay_very_fast_protection |  | 0.0 to 6550.0S , 0 to 65500 | /components/hems_ref_pcs_1 | pcs_delay_very_fast_protection | Yes
Very Fast Protection 2 | Control | G5.1.10 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40378 | uint16 |  |  | pcs_very_fast_protection_2 |  | 0 to 100%, 10 to 1000 | /components/hems_ref_pcs_1 | pcs_very_fast_protection_2 | Yes
Delay Very Fast Protection 2 | Control | G5.1.11 | Holding Register | S | 1 | 100 |  |  | 0.01 | 40379 | uint16 |  |  | pcs_delay_very_fast_protection_2 |  | 0.0 to 6550.0S , 0 to 65500 | /components/hems_ref_pcs_1 | pcs_delay_very_fast_protection_2 | Yes
Enable G5.3.1 | Control | G5.3.1 | Holding Register |  | 1 |  |  |  |  | 40321 | bit_field |  |  | pcs_enable_g5_3_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_g5_3_1 | Yes
Slow Protection #2 | Control | G5.3.1.0 | Holding Register |  | 1 |  |  |  |  | 40321 | bit | 0 |  | pcs_2_slow_protection |  |  | /components/hems_ref_pcs_1 | pcs_2_slow_protection | Yes
Slow 2 Protection #2 | Control | G5.3.1.1 | Holding Register |  | 1 |  |  |  |  | 40321 | bit | 1 |  | pcs_2_slow_2_protection |  |  | /components/hems_ref_pcs_1 | pcs_2_slow_2_protection | Yes
Fast Protection #2 | Control | G5.3.1.2 | Holding Register |  | 1 |  |  |  |  | 40321 | bit | 2 |  | pcs_2_fast_protection |  |  | /components/hems_ref_pcs_1 | pcs_2_fast_protection | Yes
Very Fast Protection #2 | Control | G5.3.1.3 | Holding Register |  | 1 |  |  |  |  | 40321 | bit | 3 |  | pcs_2_very_fast_protection |  |  | /components/hems_ref_pcs_1 | pcs_2_very_fast_protection | Yes
Very Fast 2 Protection #2 | Control | G5.3.1.4 | Holding Register |  | 1 |  |  |  |  | 40321 | bit | 4 |  | pcs_2_very_fast_2_protection |  |  | /components/hems_ref_pcs_1 | pcs_2_very_fast_2_protection | Yes
Slow Protection #3 | Control | G5.3.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 40322 | uint16 |  |  | pcs_slow_protection_3 |  | 0 to 100%, 10 to 1000 | /components/hems_ref_pcs_1 | pcs_slow_protection_3 | Yes
Delay Slow Protection #3 |  | G5.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40323 | uint16 |  |  | pcs_delay_slow_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_delay_slow_prot_3 | Yes
Slow 2 Protection #3 |  | G5.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40384 | uint16 |  |  | pcs_slow_2_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_slow_2_prot_3 | Yes
Delay Slow 2 Protection #3 |  | G5.3.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40385 | uint16 |  |  | pcs_delay_slow_2_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_delay_slow_2_prot_3 | Yes
Fast Protection #3 |  | G5.3.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40324 | uint16 |  |  | pcs_fast_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_fast_prot_3 | Yes
Delay Fast Protection #3 |  | G5.3.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40325 | uint16 |  |  | pcs_delay_fast_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_delay_fast_prot_3 | Yes
Very Fast Protection #3 |  | G5.3.8 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40326 | uint16 |  |  | pcs_delay_very_fast_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_delay_very_fast_prot_3 | Yes
Delay Very Fast Protection #3 |  | G5.3.9 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40327 | uint16 |  |  | pcs_very_fast_2_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_2_prot_3 | Yes
Very Fast 2 Protection #3 |  | G5.3.10 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40386 | uint16 |  |  | pcs_very_fast_2_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_2_prot_3 | Yes
Delay Very Fast 2 Protection #3 |  | G5.3.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40387 | uint16 |  |  | pcs_delay_very_fast_2_prot_3 |  |  | /components/hems_ref_pcs_1 | pcs_delay_very_fast_2_prot_3 | Yes
Enable G5.4.1 | Control | G5.4.1 | Holding Register |  | 1 |  |  |  |  | 40331 | bit_field |  |  | pcs_enable_g5_4_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_g5_1_1 | Yes
Slow Protection #4 | Control | G5.4.1.0 | Holding Register |  | 1 |  |  |  |  | 40331 | bit | 0 |  | pcs_bit_slow_protection_4 |  |  | /components/hems_ref_pcs_1 | pcs_slow_protection | Yes
Slow 2 Protection #4 | Control | G5.4.1.1 | Holding Register |  | 1 |  |  |  |  | 40331 | bit | 1 |  | pcs_bit_slow_2_protection_4 |  |  | /components/hems_ref_pcs_1 | pcs_fast_protection | Yes
Fast Protection #4 | Control | G5.4.1.2 | Holding Register |  | 1 |  |  |  |  | 40331 | bit | 2 |  | pcs_bit_fast_protection_4 |  |  | /components/hems_ref_pcs_1 | pcs_fast_2_protection | Yes
Very Fast Protection #4 | Control | G5.4.1.3 | Holding Register |  | 1 |  |  |  |  | 40331 | bit | 3 |  | pcs_bit_very_fast_protection_4 |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_protection | Yes
Very Fast 2 Protection | Control | G5.4.1.4 | Holding Register |  | 1 |  |  |  |  | 40331 | bit | 4 |  | pcs_bit_very_fast_2_protection_4 |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_2_protection | Yes
Slow Protection #4 |  | GS5.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40332 | uint16 |  |  | pcs_slow_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_slow_prot_4 | Yes
Delay Slow Protection #4 |  | GS5.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40333 | uint16 |  |  | pcs_delay_slow_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_delay_slow_prot_4 | Yes
Slow 2 Protection #4 |  | GS5.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40388 | uint16 |  |  | pcs_slow_2_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_slow_2_prot_4 | Yes
Delay Slow 2 Protection #4 |  | GS5.4.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40389 | uint16 |  |  | pcs_delay_slow_2_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_delay_slow_2_prot_4 | Yes
Fast Protection #4 |  | GS5.4.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40334 | uint16 |  |  | pcs_fast_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_fast_prot_4 | Yes
Delay Fast Protection #4 |  | GS5.4.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40335 | uint16 |  |  | pcs_delay_fast_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_delay_fast_prot_4 | Yes
Very Fast Protection #4 |  | GS5.4.8 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40336 | uint16 |  |  | pcs_very_fast_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_prot_4 | Yes
Delay Very Fast Protection #4 |  | GS5.4.9 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40337 | uint16 |  |  | pcs_delay_very_fast_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_delay_very_fast_prot_4 | Yes
Very Fast 2 Protection #4 |  | GS5.4.10 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40390 | uint16 |  |  | pcs_very_fast_2_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_very_fast_2_prot_4 | Yes
Delay Very Fast 2 Protection #4 |  | GS5.4.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40391 | uint16 |  |  | pcs_delay_very_fast_2_prot_4 |  |  | /components/hems_ref_pcs_1 | pcs_delay_very_fast_2_prot_4 | Yes
Enable 5.4b.1.1 |  | GS5.4b.1.1 | Holding Register |  | 1 |  |  |  |  | 40731 | uint16 |  |  | pcs_enable_5_4b_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_4b_1 | Yes
V1 = 120% |  | GS5.4b.1.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40732 | uint16 |  |  | pcs_5_4b_1_V1 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_1_V1 | Yes
f1 = 62.00 Hz |  | GS5.4b.1.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40733 | uint16 |  |  | pcs_5_4b_1_f1 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_1_f1 | Yes
t1 = 1.0 s |  | GS5.4b.1.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40734 | uint16 |  |  | pcs_5_4b_1_t1 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_1_t1 | Yes
Enable 5.4b.2.1 |  | GS5.4b.2.1 | Holding Register |  | 1 |  |  |  |  | 40735 | uint16 |  |  | pcs_enable_5_4b_2 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_4b_2 | Yes
V2 = 80% |  | GS5.4b.2.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40736 | uint16 |  |  | pcs_5_4b_2_V2 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_2_V2 | Yes
f2 = 62.00 Hz |  | GS5.4b.2.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40737 | uint16 |  |  | pcs_5_4b_2_f2 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_2_f2 | Yes
t2 = 1.0 s |  | GS5.4b.2.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40738 | uint16 |  |  | pcs_5_4b_2_t2 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_2_t2 | Yes
Enable 5.4b.3.1 |  | GS5.4b.3.1 | Holding Register |  | 1 |  |  |  |  | 40739 | uint16 |  |  | pcs_enable_5_4b_3 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_4b_3 | Yes
V3 = 120% |  | GS5.4b.3.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40740 | uint16 |  |  | pcs_5_4b_3_V3 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_3_V3 | Yes
f3 = 58.00 Hz |  | GS5.4b.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40741 | uint16 |  |  | pcs_5_4b_3_f3 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_3_f3 | Yes
t3 = 1.0 s |  | GS5.4b.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40742 | uint16 |  |  | pcs_5_4b_3_t3 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_3_t3 | Yes
Enable 5.4b.4.1 |  | GS5.4b.4.1 | Holding Register |  | 1 |  |  |  |  | 40473 | uint16 |  |  | pcs_enable_5_4b_4 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_4b_4 | Yes
V4 = 80% |  | GS5.4b.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40474 | uint16 |  |  | pcs_5_4b_4_V4 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_4_V4 | Yes
f4 = 58.00 Hz |  | GS5.4b.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40475 | uint16 |  |  | pcs_5_4b_4_f4 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_4_f4 | Yes
t4 = 1.0 s |  | GS5.4b.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40476 | uint16 |  |  | pcs_5_4b_4_t4 |  |  | /components/hems_ref_pcs_1 | pcs_5_4b_4_t4 | Yes
Enable 5.5.1 |  | GS5.5.1 | Holding Register |  | 1 |  |  |  |  | 40341 | bit_field |  |  | pcs_enable_5_5_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_5_1 | Yes
I unbalance |  | GS5.5.1.0 | Holding Register |  | 1 |  |  |  |  | 40341 | bit | 0 |  | pcs_bit_i_unbalance |  |  | /components/hems_ref_pcs_1 | pcs_bit_i_unbalance | Yes
v unbalance |  | GS5.5.1.1 | Holding Register |  | 1 |  |  |  |  | 40341 | bit | 1 |  | pcs_bit_v_unbalance |  |  | /components/hems_ref_pcs_1 | pcs_bit_v_unbalance | Yes
I unbalance |  | GS5.5.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40342 | uint16 |  |  | pcs_i_unbalance |  |  | /components/hems_ref_pcs_1 | pcs_i_unbalance | Yes
I unbalance min |  | GS5.5.2b | Holding Register |  | 1 | 1 |  |  | 1 | 40348 | uint16 |  |  | pcs_i_unbalance_min |  |  | /components/hems_ref_pcs_1 | pcs_i_unbalance_min | Yes
Delay I unbalance |  | GS5.5.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40343 | uint16 |  |  | pcs_delay_i_unbalance |  |  | /components/hems_ref_pcs_1 | pcs_delay_i_unbalance | Yes
Unbalance V |  | GS5.5.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40344 | uint16 |  |  | pcs_v_unbalance |  |  | /components/hems_ref_pcs_1 | pcs_v_unbalance | Yes
Delay Unbalance V |  | GS5.5.5 | Holding Register |  | 1 | 1 |  |  | 1 | 40345 | uint16 |  |  | pcs_delay_v_unbalance |  |  | /components/hems_ref_pcs_1 | pcs_delay_v_unbalance | Yes
DUI unbal thresh |  | GS5.5.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40346 | uint16 |  |  | pcs_dui_unbal_thresh |  |  | /components/hems_ref_pcs_1 | pcs_dui_unbal_thresh | Yes
DUI unbal tie |  | GS5.5.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40347 | uint16 |  |  | pcs_dui_unbal_tie |  |  | /components/hems_ref_pcs_1 | pcs_dui_unbal_tie | Yes
Enable 5.6.1 |  | GS5.6.1 | Holding Register |  | 1 |  |  |  |  | 40351 | bit_field |  |  | pcs_enable_5_6_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_6_1 | Yes
Enable 5.6.1 off |  | GS5.6.1.0 | Holding Register |  | 1 |  |  |  |  | 40351 | bit | 0 |  | pcs_bit_5_6_1_off |  |  | /components/hems_ref_pcs_1 | pcs_bit_5_6_1_off | Yes
Enable 5.6.1 Active |  | GS5.6.1.1 | Holding Register |  | 1 |  |  |  |  | 40351 | bit | 1 |  | pcs_bit_5_6_1_active |  |  | /components/hems_ref_pcs_1 | pcs_bit_5_6_1_active | Yes
Enable 5.6.1 Passive |  | GS5.6.1.2 | Holding Register |  | 1 |  |  |  |  | 40351 | bit | 2 |  | pcs_bit_5_6_1_passive |  |  | /components/hems_ref_pcs_1 | pcs_bit_5_6_1_passive | Yes
Enable 5.6.1 Simultaneous |  | GS5.6.1.3 | Holding Register |  | 1 |  |  |  |  | 40351 | bit | 3 |  | pcs_bit_5_6_1_simultaneous |  |  | /components/hems_ref_pcs_1 | pcs_bit_5_6_1_simultaneous | Yes
IGBTs temp thres fit=125 C |  | GS5.7.1 | Holding Register |  | 1 | 1 |  |  | 1 | 40361 | uint16 |  |  | pcs_igbt_temp_thres_fit |  |  | /components/hems_ref_pcs_1 | pcs_igbt_temp_thres_fit | Yes
IGBTs temp hist =10 C |  | GS5.7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40362 | uint16 |  |  | pcs_igbt_temp_hist |  |  | /components/hems_ref_pcs_1 | pcs_igbt_temp_hist | Yes
Module temp thres fit=85 C |  | GS5.7.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40363 | uint16 |  |  | pcs_module_temp_thres_fit |  |  | /components/hems_ref_pcs_1 | pcs_module_temp_thres_fit | Yes
Module temp thist=10 C |  | GS5.7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40364 | uint16 |  |  | pcs_module_temp_hist |  |  | /components/hems_ref_pcs_1 | pcs_module_temp_hist | Yes
Internal temp thres fit=85 C |  | GS5.7.5 | Holding Register |  | 1 | 1 |  |  | 1 | 40365 | uint16 |  |  | pcs_internal_temp_thres_fit |  |  | /components/hems_ref_pcs_1 | pcs_internal_temp_thres_fit | Yes
MV transformer threshold =125 deg C |  | GS5.7.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40359 | uint16 |  |  | pcs_mv_transformer_thresh |  |  | /components/hems_ref_pcs_1 | pcs_mv_transformer_thresh | Yes
MV transformer delay=120 s |  | GS5.7.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40360 | uint16 |  |  | pcs_mv_transformer_delay |  |  | /components/hems_ref_pcs_1 | pcs_mv_transformer_delay | Yes
MV trans TV crit thres = 150 deg |  | GS5.7.8 | Holding Register |  | 1 | 1 |  |  | 1 | 40400 | uint16 |  |  | pcs_mv_transformer_tv_crit_thresh |  |  | /components/hems_ref_pcs_1 | pcs_mv_transformer_tv_crit_thresh | Yes
Enable 5.8.1 |  | GS5.8.1 | Holding Register |  | 1 |  |  |  |  | 40366 | bit_field |  |  | pcs_enable_5_8_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_5_8_1 | Yes
Enable 5.8.1 No |  | GS5.8.1.0 | Holding Register |  | 1 |  |  |  |  | 40366 | bit | 0 |  | pcs_bit_5_8_1_no |  |  | /components/hems_ref_pcs_1 | pcs_bit_5_8_1_no | Yes
Enable 5.8.1 Yes |  | GS5.8.1.1 | Holding Register |  | 1 |  |  |  |  | 40366 | bit | 1 |  | pcs_bit_5_8_1_yes |  |  | /components/hems_ref_pcs_1 | pcs_bit_5_8_1_yes | Yes
Current Thresh - 4.00 A |  | GS5.8.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40367 | uint16 |  |  | pcs_current_thresh |  |  | /components/hems_ref_pcs_1 | pcs_current_thresh | Yes
Trip Time = 5.0 s |  | GS5.8.3 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40368 | uint16 |  |  | pcs_trip_time |  |  | /components/hems_ref_pcs_1 | pcs_trip_time | Yes
Measured Current=0.00A |  | GS5.8.4 | Holding Register | A | 1 | 100 |  |  | 100 | 40369 | uint16 |  |  | pcs_measured_curent |  |  | /components/hems_ref_pcs_1 | pcs_measured_curent | Yes
Contactor GFDI Open=yes |  | GS5.8.5 | Holding Register |  | 1 |  |  |  |  | 40370 | uint16 |  |  | pcs_contactor_gfdi_open |  |  | /components/hems_ref_pcs_1 | pcs_contactor_gfdi_open | Yes
HPVL Enable 5.9.1 |  | GS5.9.1 | Holding Register |  | 1 |  |  |  |  | 40392 | bit_field |  |  | pcs_hpvl_enable |  |  | /components/hems_ref_pcs_1 | pcs_hpvl_enable | Yes
HPVL Enable 5.9.1 No |  | GS5.9.1.0 | Holding Register |  | 1 |  |  |  |  | 40392 | bit | 0 |  | pcs_bit_hpvl_no |  |  | /components/hems_ref_pcs_1 | pcs_bit_hpvl_no | Yes
HPVL Enable 5.9.1 Yes |  | GS5.9.1.1 | Holding Register |  | 1 | 1 |  |  | 1 | 40392 | bit | 1 |  | pcs_bit_hpvl_yeso |  |  | /components/hems_ref_pcs_1 | pcs_bit_hpvl_yeso | Yes
HPVL Activation Level = 5% |  | GS5.9.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40393 | uint16 |  |  | pcs_hpvl_activation_level_5 |  |  | /components/hems_ref_pcs_1 | pcs_hpvl_activation_level_5 | Yes
HPVL Scale = 1000 |  | GS5.9.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40394 | uint16 |  |  | pcs_hpvl_scale_1000 |  |  | /components/hems_ref_pcs_1 | pcs_hpvl_scale_1000 | Yes
HPVL Fault Level = 0 |  | GS5.9.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40395 | uint16 |  |  | pcs_hpvl_fault_level_0 |  |  | /components/hems_ref_pcs_1 | pcs_hpvl_fault_level_0 | Yes
HVPL filter = 0.100 Hz |  | GS5.9.5 | Holding Register |  | 1 | 1000 |  |  | 0.001 | 40396 | uint16 |  |  | pcs_hvpl_filter_hz_100_hz |  |  | /components/hems_ref_pcs_1 | pcs_hvpl_filter_hz_100_hz | Yes
HPVL delay fault = 2.0 s |  | GS5.9.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40397 | uint16 |  |  | pcs_hpvl_delay_fault_s_0_s |  |  | /components/hems_ref_pcs_1 | pcs_hpvl_delay_fault_s_0_s | Yes
HPVL Start Test |  | GS5.9.7 | Holding Register |  | 1 |  |  |  |  | 40398 | bit_field |  |  | pcs_hpvl_start_test |  |  | /components/hems_ref_pcs_1 | pcs_hpvl_start_test | Yes
HPVL Start Test no |  | GS5.9.7.0 | Holding Register |  | 1 |  |  |  |  | 40398 | bit | 0 |  | pcs_bit_hpvl_testo |  |  | /components/hems_ref_pcs_1 | pcs_bit_hpvl_testo | Yes
HPVL Start Test yes |  | GS5.9.7.1 | Holding Register |  | 1 |  |  |  |  | 40398 | bit | 1 |  | pcs_bit_hpvl_testo |  |  | /components/hems_ref_pcs_1 | pcs_bit_hpvl_testo | Yes
HVPL Test Level = -20% |  | GS5.9.8 | Holding Register |  | 1 | 1 |  |  | 1 | 40399 | int16 |  |  | pcs_hvpl_test_level_20 |  |  | /components/hems_ref_pcs_1 | pcs_hvpl_test_level_20 | Yes
Earth Current |  | GS5.11.1 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40371 | uint16 |  |  | pcs_earth_current |  |  | /components/hems_ref_pcs_1 | pcs_earth_current | Yes
Delay High Vdc = 30 s |  | GS5.11.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40372 | uint16 |  |  | pcs_delay_high_vdc_s_s |  |  | /components/hems_ref_pcs_1 | pcs_delay_high_vdc_s_s | Yes
DU Overcurrent = 400.0 A |  | GS5.11.3 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40373 | uint16 |  |  | pcs_du_overcurrent_a_0_a |  |  | /components/hems_ref_pcs_1 | pcs_du_overcurrent_a_0_a | Yes
Inv Curent Prot = -350 A |  | GS5.11.3a | Holding Register |  | 1 | 10 |  |  | 0.1 | 40971 | int16 |  |  | pcs_inv_curent_prot_a_a |  |  | /components/hems_ref_pcs_1 | pcs_inv_curent_prot_a_a | Yes
DU current detection = 350.0 A |  | GS5.11.3c | Holding Register |  | 1 | 10 |  |  | 0.1 | 40375 | uint16 |  |  | pcs_du_current_detection_a_0_a |  |  | /components/hems_ref_pcs_1 | pcs_du_current_detection_a_0_a | Yes
DU neg I detect = -100.0 A |  | GS5.11.3d | Holding Register |  | 1 | 10 |  |  | 0.1 | 40972 | int16 |  |  | pcs_du_neg_i_detect_a_0_a |  |  | /components/hems_ref_pcs_1 | pcs_du_neg_i_detect_a_0_a | Yes
MV manometer fault = off |  | GS5.11.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40481 | uint16 |  |  | pcs_mv_manometer_fault_off |  |  | /components/hems_ref_pcs_1 | pcs_mv_manometer_fault_off | Yes
MV manometer delay = 10 s |  | GS5.11.5 | Holding Register |  | 1 | 1 |  |  | 1 | 40482 | uint16 |  |  | pcs_mv_manometer_delay_s_s |  |  | /components/hems_ref_pcs_1 | pcs_mv_manometer_delay_s_s | Yes
LV manometer fault = off |  | GS5.11.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40483 | uint16 |  |  | pcs_lv_manometer_fault_off |  |  | /components/hems_ref_pcs_1 | pcs_lv_manometer_fault_off | Yes
LV manometer delay = 10 s |  | GS5.11.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40484 | uint16 |  |  | pcs_lv_manometer_delay_s_s |  |  | /components/hems_ref_pcs_1 | pcs_lv_manometer_delay_s_s | Yes
Display Baudrate = 115200 |  | G6.1.1 | Holding Register |  | 1 |  |  |  |  | 40401 | uint16 |  |  | pcs_display_baudrate_115200 |  |  | /components/hems_ref_pcs_1 | pcs_display_baudrate_115200 | Yes
Modbus Address=150 |  | G6.1.2 | Holding Register |  | 1 |  |  |  |  | 40402 | uint16 |  |  | pcs_modbus_address_150 |  |  | /components/hems_ref_pcs_1 | pcs_modbus_address_150 | Yes
Modbus Baudrate=19200 bps |  | G6.1.3 | Holding Register |  | 1 |  |  |  |  | 40403 | uint16 |  |  | pcs_modbus_baudrate_bps_bps |  |  | /components/hems_ref_pcs_1 | pcs_modbus_baudrate_bps_bps | Yes
Modbus Parity |  | G6.1.4 | Holding Register |  | 1 |  |  |  |  | 40404 | uint16 |  |  | pcs_modbus_parity |  |  | /components/hems_ref_pcs_1 | pcs_modbus_parity | Yes
Modbus Stop bits |  | G6.1.5 | Holding Register |  | 1 |  |  |  |  | 40405 | uint16 |  |  | pcs_modbus_stop_bits |  |  | /components/hems_ref_pcs_1 | pcs_modbus_stop_bits | Yes
Modbus Master |  | G6.1.6 | Holding Register |  | 1 |  |  |  |  | 40406 | uint16 |  |  | pcs_modbus_master |  |  | /components/hems_ref_pcs_1 | pcs_modbus_master | Yes
Automatic IP |  | G6.2.1 | Holding Register |  | 1 |  |  |  |  | 40411 | uint16 |  |  | pcs_automatic_ip |  |  | /components/hems_ref_pcs_1 | pcs_automatic_ip | Yes
Assigned IP A |  | G6.2.1.1a | Holding Register |  | 1 |  |  |  |  | 40412 | uint16 |  |  | pcs_assigned_ip_a |  |  | /components/hems_ref_pcs_1 | pcs_assigned_ip_a | Yes
Assigned IP B |  | G6.2.1.1b | Holding Register |  | 1 |  |  |  |  | 40413 | uint16 |  |  | pcs_assigned_ip_b |  |  | /components/hems_ref_pcs_1 | pcs_assigned_ip_b | Yes
Assigned IP C |  | G6.2.1.1c | Holding Register |  | 1 |  |  |  |  | 40414 | uint16 |  |  | pcs_assigned_ip_c |  |  | /components/hems_ref_pcs_1 | pcs_assigned_ip_c | Yes
Assigned IP D |  | G6.2.1.1d | Holding Register |  | 1 |  |  |  |  | 40415 | uint16 |  |  | pcs_assigned_ip_d |  |  | /components/hems_ref_pcs_1 | pcs_assigned_ip_d | Yes
Assigned Subnet A |  | G6.2.1.2a | Holding Register |  | 1 |  |  |  |  | 40416 | uint16 |  |  | pcs_assigned_subnet_a |  |  | /components/hems_ref_pcs_1 | pcs_assigned_subnet_a | Yes
Assigned Subnet B |  | G6.2.1.2b | Holding Register |  | 1 |  |  |  |  | 40417 | uint16 |  |  | pcs_assigned_subnet_b |  |  | /components/hems_ref_pcs_1 | pcs_assigned_subnet_b | Yes
Assigned Subnet C |  | G6.2.1.2c | Holding Register |  | 1 |  |  |  |  | 40418 | uint16 |  |  | pcs_assigned_subnet_c |  |  | /components/hems_ref_pcs_1 | pcs_assigned_subnet_c | Yes
Assigned Subnet D |  | G6.2.1.2d | Holding Register |  | 1 |  |  |  |  | 40419 | uint16 |  |  | pcs_assigned_subnet_d |  |  | /components/hems_ref_pcs_1 | pcs_assigned_subnet_d | Yes
Assigned Gateway A |  | G6.2.1.3a | Holding Register |  | 1 |  |  |  |  | 40420 | uint16 |  |  | pcs_assigned_gateway_a |  |  | /components/hems_ref_pcs_1 | pcs_assigned_gateway_a | Yes
Assigned Gateway B |  | G6.2.1.3b | Holding Register |  | 1 |  |  |  |  | 40421 | uint16 |  |  | pcs_assigned_gateway_b |  |  | /components/hems_ref_pcs_1 | pcs_assigned_gateway_b | Yes
Assigned Gateway C |  | G6.2.1.3c | Holding Register |  | 1 |  |  |  |  | 40422 | uint16 |  |  | pcs_assigned_gateway_c |  |  | /components/hems_ref_pcs_1 | pcs_assigned_gateway_c | Yes
Assigned Gateway D |  | G6.2.1.3d | Holding Register |  | 1 |  |  |  |  | 40423 | uint16 |  |  | pcs_assigned_gateway_d |  |  | /components/hems_ref_pcs_1 | pcs_assigned_gateway_d | Yes
IP address A |  | G6.2.2a | Holding Register |  | 1 |  |  |  |  | 40424 | uint16 |  |  | pcs_ip_address_a |  |  | /components/hems_ref_pcs_1 | pcs_ip_address_a | Yes
IP address B |  | G6.2.2b | Holding Register |  | 1 |  |  |  |  | 40425 | uint16 |  |  | pcs_ip_address_b |  |  | /components/hems_ref_pcs_1 | pcs_ip_address_b | Yes
IP address C |  | G6.2.2c | Holding Register |  | 1 |  |  |  |  | 40426 | uint16 |  |  | pcs_ip_address_c |  |  | /components/hems_ref_pcs_1 | pcs_ip_address_c | Yes
IP address D |  | G6.2.2d | Holding Register |  | 1 |  |  |  |  | 40427 | uint16 |  |  | pcs_ip_address_d |  |  | /components/hems_ref_pcs_1 | pcs_ip_address_d | Yes
Subnet A |  | G6.2.3a | Holding Register |  | 1 |  |  |  |  | 40428 | uint16 |  |  | pcs_subnet_a |  |  | /components/hems_ref_pcs_1 | pcs_subnet_a | Yes
Subnet B |  | G6.2.3b | Holding Register |  | 1 |  |  |  |  | 40429 | uint16 |  |  | pcs_subnet_b |  |  | /components/hems_ref_pcs_1 | pcs_subnet_b | Yes
Subnet C |  | G6.2.3c | Holding Register |  | 1 |  |  |  |  | 40430 | uint16 |  |  | pcs_subnet_c |  |  | /components/hems_ref_pcs_1 | pcs_subnet_c | Yes
Subnet D |  | G6.2.3d | Holding Register |  | 1 |  |  |  |  | 40431 | uint16 |  |  | pcs_subnet_d |  |  | /components/hems_ref_pcs_1 | pcs_subnet_d | Yes
Gateway A |  | G6.2.4a | Holding Register |  | 1 |  |  |  |  | 40432 | uint16 |  |  | pcs_gateway_a |  |  | /components/hems_ref_pcs_1 | pcs_gateway_a | Yes
Gateway B |  | G6.2.4b | Holding Register |  | 1 |  |  |  |  | 40433 | uint16 |  |  | pcs_gateway_b |  |  | /components/hems_ref_pcs_1 | pcs_gateway_b | Yes
Gateway C |  | G6.2.4c | Holding Register |  | 1 |  |  |  |  | 40434 | uint16 |  |  | pcs_gateway_c |  |  | /components/hems_ref_pcs_1 | pcs_gateway_c | Yes
Gateway D |  | G6.2.4d | Holding Register |  | 1 |  |  |  |  | 40435 | uint16 |  |  | pcs_gateway_d |  |  | /components/hems_ref_pcs_1 | pcs_gateway_d | Yes
Mac A |  | G6.2.5a | Holding Register |  | 1 |  |  |  |  | 40436 | uint16 |  |  | pcs_mac_a |  |  | /components/hems_ref_pcs_1 | pcs_mac_a | Yes
Mac B |  | G6.2.5b | Holding Register |  | 1 |  |  |  |  | 40437 | uint16 |  |  | pcs_mac_b |  |  | /components/hems_ref_pcs_1 | pcs_mac_b | Yes
Mac C |  | G6.2.5c | Holding Register |  | 1 |  |  |  |  | 40438 | uint16 |  |  | pcs_mac_c |  |  | /components/hems_ref_pcs_1 | pcs_mac_c | Yes
Mac D |  | G6.2.5d | Holding Register |  | 1 |  |  |  |  | 40439 | uint16 |  |  | pcs_mac_d |  |  | /components/hems_ref_pcs_1 | pcs_mac_d | Yes
Mac E |  | G6.2.5e | Holding Register |  | 1 |  |  |  |  | 40440 | uint16 |  |  | pcs_mac_e |  |  | /components/hems_ref_pcs_1 | pcs_mac_e | Yes
Mac F |  | G6.2.5e | Holding Register |  | 1 |  |  |  |  | 40441 | uint16 |  |  | pcs_mac_f |  |  | /components/hems_ref_pcs_1 | pcs_mac_f | Yes
Reset refs time = 4s |  | G6.3.1 | Holding Register |  | 1 | 1 |  |  | 1 | 44253 | uint16 |  |  | pcs_reset_refs_time_s |  |  | /components/hems_ref_pcs_1 | pcs_reset_refs_time_s | Yes
Comms Fault time = 60 s |  | G6.3.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 44254 | uint16 |  |  | pcs_comms_fault_time_s_s |  |  | /components/hems_ref_pcs_1 | pcs_comms_fault_time_s_s | Yes
Home P ref = 0.0% |  | G6.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44255 | uint16 |  |  | pcs_home_p_ref_0_0 |  |  | /components/hems_ref_pcs_1 | pcs_home_p_ref_0_0 | Yes
Home Q ref = 0.0% |  | G6.3.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44256 | int16 |  |  | pcs_home_q_ref_0_0 |  |  | /components/hems_ref_pcs_1 | pcs_home_q_ref_0_0 | Yes
Enable G7.1 |  | G7.1 | Holding Register |  | 1 |  |  |  |  | 40501 | uint16 |  |  | pcs_enable_g_1 |  |  | /components/hems_ref_pcs_1 | pcs_enable_g_1 | Yes
Number of Retries |  | G7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40502 | uint16 |  |  | pcs_number_of_retries |  |  | /components/hems_ref_pcs_1 | pcs_number_of_retries | Yes
Delay between retries = 30 s |  | G7.3 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40503 | uint16 |  |  | pcs_delay_between_retries_s_s |  |  | /components/hems_ref_pcs_1 | pcs_delay_between_retries_s_s | Yes
Reset Retries timeout |  | G7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40504 | uint16 |  |  | pcs_reset_retries_timeout |  |  | /components/hems_ref_pcs_1 | pcs_reset_retries_timeout | Yes
All Faults enabled |  | G7.5 | Holding Register |  | 1 |  |  |  |  | 40505 | uint16 |  |  | pcs_all_faults_enabled |  |  | /components/hems_ref_pcs_1 | pcs_all_faults_enabled | Yes
Faults allowed number = 0 |  | G7.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40506 | uint16 |  |  | pcs_faults_allowed_number |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_number | Yes
Faults allowed 1 = No Faults |  | G7.6.1 | Holding Register |  | 1 | 1 |  |  | 1 | 40507 | uint16 |  |  | pcs_faults_allowed_1 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_1 | Yes
Faults allowed 2 = No Faults |  | G7.6.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40508 | uint16 |  |  | pcs_faults_allowed_2 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_2 | Yes
Faults allowed 3 = No Faults |  | G7.6.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40509 | uint16 |  |  | pcs_faults_allowed_3 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_3 | Yes
Faults allowed 4 = No Faults |  | G7.6.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40510 | uint16 |  |  | pcs_faults_allowed_4 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_4 | Yes
Faults allowed 5 = No Faults |  | G7.6.5 | Holding Register |  | 1 | 1 |  |  | 1 | 40511 | uint16 |  |  | pcs_faults_allowed_5 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_5 | Yes
Faults allowed 6 = No Faults |  | G7.6.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40512 | uint16 |  |  | pcs_faults_allowed_6 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_6 | Yes
Faults allowed 7 = No Faults |  | G7.6.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40513 | uint16 |  |  | pcs_faults_allowed_7 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_7 | Yes
Faults allowed 8 = No Faults |  | G7.6.8 | Holding Register |  | 1 | 1 |  |  | 1 | 40514 | uint16 |  |  | pcs_faults_allowed_8 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_8 | Yes
Faults allowed 9 = No Faults |  | G7.6.9 | Holding Register |  | 1 | 1 |  |  | 1 | 40515 | uint16 |  |  | pcs_faults_allowed_9 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_9 | Yes
Faults allowed 10 = No Faults |  | G7.6.10 | Holding Register |  | 1 | 1 |  |  | 1 | 40516 | uint16 |  |  | pcs_faults_allowed_10 |  |  | /components/hems_ref_pcs_1 | pcs_faults_allowed_10 | Yes
Faults exception number = 0 |  | G7.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40517 | uint16 |  |  | pcs_faults_exeption_number |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_number | Yes
Faults exception 1 = No faults |  | G7.7.1 | Holding Register |  | 1 | 1 |  |  |  | 40518 | uint16 |  |  | pcs_faults_exception_1 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_1 | Yes
Faults exception 2 = No faults |  | G.7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40519 | uint16 |  |  | pcs_faults_exception_2 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_2 | Yes
Faults exception 3 = No faults |  | G7.7.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40520 | uint16 |  |  | pcs_faults_exception_3 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_3 | Yes
Faults exception 4 = No faults |  | G7.7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40521 | uint16 |  |  | pcs_faults_exception_4 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_4 | Yes
Faults exception 5 = No faults |  | G7.7.5 | Holding Register |  | 1 | 1 |  |  | 1 | 40522 | uint16 |  |  | pcs_faults_exception_5 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_5 | Yes
Faults exception 6 = No faults |  | G7.7.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40523 | uint16 |  |  | pcs_faults_exception_6 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_6 | Yes
Faults exception 7 = No faults |  | G7.7.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40524 | uint16 |  |  | pcs_faults_exception_7 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_7 | Yes
Faults exception 8 = No faults |  | G7.7.8 | Holding Register |  | 1 | 1 |  |  | 1 | 40425 | uint16 |  |  | pcs_faults_exception_8 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_8 | Yes
Faults exception 9 = No faults |  | G7.7.9 | Holding Register |  | 1 | 1 |  |  | 1 | 40526 | uint16 |  |  | pcs_faults_exception_9 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_9 | Yes
Faults exception 10 = No faults |  | G7.7.10 | Holding Register |  | 1 | 1 |  |  | 1 | 40527 | uint16 |  |  | pcs_faults_exception10 |  |  | /components/hems_ref_pcs_1 | pcs_faults_enabled_10 | Yes
P control Mode = MPPt |  | G8.1.1 | Holding Register |  | 1 |  |  |  |  | 40551 | bit_field |  |  | pcs_p_control_mode_mppt |  |  | /components/hems_ref_pcs_1 | pcs_p_control_mode_mppt | Yes
P control Mode = I |  | G8.1.1.0 | Holding Register |  | 1 |  |  |  |  | 40551 | bit | 0 |  | pcs_bit_p_modeo |  |  | /components/hems_ref_pcs_1 | pcs_bit_p_modeo | Yes
P control mode = P |  | G8.1.1.1 | Holding Register |  | 1 |  |  |  |  | 40551 | bit | 1 |  | pcs_bit_p_modeo |  |  | /components/hems_ref_pcs_1 | pcs_bit_p_modeo | Yes
P control mode = Vdc |  | G8.1.1.2 | Holding Register |  | 1 |  |  |  |  | 40551 | bit | 2 |  | pcs_bit_p_modeo |  |  | /components/hems_ref_pcs_1 | pcs_bit_p_modeo | Yes
Q control Mode = Q |  | G8.1.2 | Holding Register |  | 1 |  |  |  |  | 40552 | bit_field |  |  | pcs_q_control_mode_q |  |  | /components/hems_ref_pcs_1 | pcs_q_control_mode_q | Yes
Q control Mode = Cos phi |  | G8.1.2.0 | Holding Register |  | 1 |  |  |  |  | 40552 | bit | 0 |  | pcs_bit_q_mode_phio |  |  | /components/hems_ref_pcs_1 | pcs_bit_q_mode_phio | Yes
Q control Mode = Q |  | G8.1.2.1 | Holding Register |  | 1 |  |  |  |  | 40552 | bit | 1 |  | pcs_bit_q_modeo |  |  | /components/hems_ref_pcs_1 | pcs_bit_q_modeo | Yes
Q control Mode = I |  | G8.1.2.2 | Holding Register |  | 1 |  |  |  |  | 40552 | bit | 2 |  | pcs_bit_q_modeo |  |  | /components/hems_ref_pcs_1 | pcs_bit_q_modeo | Yes
Q control mode = V/Q |  | G8.1.2.3 | Holding Register |  | 1 |  |  |  |  | 40552 | bit | 3 |  | pcs_bit_q_mode_qo |  |  | /components/hems_ref_pcs_1 | pcs_bit_q_mode_qo | Yes
P reference = 100% |  | G8.1.3.0.0 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40553 | uint16 |  |  | pcs_p_reference_100 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100 | Yes
Id reference = 100% |  | G8.1.3.0.1 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40554 | uint16 |  |  | pcs_id_reference_100 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100 | Yes
Vdc reference = 1100V |  | G8.1.3.0.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40556 | uint16 |  |  | pcs_vdc_reference_v |  |  | /components/hems_ref_pcs_1 | pcs_vdc_reference_v | Yes
P1 reference = 100.00% |  | G8.1.3.1.0 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44301 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id1 reference = 100.00% |  | G8.1.3.1.1 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44311 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
P2 reference = 100.00% |  | G8.1.3.1.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44302 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id2 reference = 100.00% |  | G8.1.3.1.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44312 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
P3 reference = 100.00% |  | G8.1.3.1.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44303 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id3 reference = 100.00% |  | G8.1.3.1.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44313 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
P4 reference = 100.00% |  | G8.1.3.1.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44304 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id4 reference = 100.00% |  | G8.1.3.1.6 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44314 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
P5 reference = 100.00% |  | G8.1.3.1.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44305 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id5 reference = 100.00% |  | G8.1.3.1.8 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44315 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
P6 reference = 100.00% |  | G8.1.3.1.9 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44306 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id6 reference = 100.00% |  | G8.1.3.1.10 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44316 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
P7 reference = 100.00% |  | G8.1.3.1.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44307 | int16 |  |  | pcs_p_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_p_reference_100_00 | Yes
Id7 reference = 100.00% |  | G8.1.3.1.12 | Holding Register |  | 1 | 100 |  |  | 0.01 | 44317 | int16 |  |  | pcs_id_reference_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_id_reference_100_00 | Yes
Cos phi reference = 1.000 |  | G8.1.4.0 | Holding Register |  | 1 | 1000 |  |  | 0.001 | 40556 | uint16 |  |  | pcs_cos_phi_reference_1_000 |  |  | /components/hems_ref_pcs_1 | pcs_cos_phi_reference_1_000 | Yes
Iq reference = 0 |  | G8.1.4.1 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40557 | int16 |  |  | pcs_iq_reference_0 |  |  | /components/hems_ref_pcs_1 | pcs_iq_reference_0 | Yes
Q reference = 0.0% |  | G8.1.4.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40558 | int16 |  |  | pcs_q_reference_0_0 |  |  | /components/hems_ref_pcs_1 | pcs_q_reference_0_0 | Yes
Vref = 100.00% |  | G8.1.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40576 | int16 |  |  | pcs_vref_100_00 |  |  | /components/hems_ref_pcs_1 | pcs_vref_100_00 | Yes
Excitation = Capacitive |  | G8.1.5.0 | Holding Register |  | 1 |  |  |  |  | 40559 | uint16 |  |  | pcs_excitation_capacitive |  | 0 = cap, 1 = ind | /components/hems_ref_pcs_1 | pcs_excitation_capacitive | Yes
V1=90% |  | G8.1.5.1 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40577 | uint16 |  |  | pcs_v_90 |  |  | /components/hems_ref_pcs_1 | pcs_v_90 | Yes
V2 = 92.00% |  | G8.1.6 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40578 | uint16 |  |  | pcs_v_92_00 |  |  | /components/hems_ref_pcs_1 | pcs_v_92_00 | Yes
V3 = 108.00% |  | G8.1.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40579 | uint16 |  |  | pcs_v_108_00 |  |  | /components/hems_ref_pcs_1 | pcs_v_108_00 | Yes
V4 = 110.00% |  | G8.1.8 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40580 | uint16 |  |  | pcs_v_110_00 |  |  | /components/hems_ref_pcs_1 | pcs_v_110_00 | Yes
Q1 = 48.43% |  | G8.1.9 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40581 | uint16 |  |  | pcs_q_48_43 |  |  | /components/hems_ref_pcs_1 | pcs_q_48_43 | Yes
Q2 = 0.00% |  | G8.1.10 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40582 | uint16 |  |  | pcs_q_0_00 |  |  | /components/hems_ref_pcs_1 | pcs_q_0_00 | Yes
Q3 = 0.00% |  | G8.1.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40583 | uint16 |  |  | pcs_q_0_00 |  |  | /components/hems_ref_pcs_1 | pcs_q_0_00 | Yes
Q4 = 48.43% |  | G8.1.12 | Holding Register |  | 1 | 100 |  |  | 0.01 | 40584 | uint16 |  |  | pcs_q_48_43 |  |  | /components/hems_ref_pcs_1 | pcs_q_48_43 | Yes
V hysterisis = 1.0% |  | G8.1.13 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40585 | uint16 |  |  | pcs_v_hysterisis_1_0 |  |  | /components/hems_ref_pcs_1 | pcs_v_hysterisis_1_0 | Yes
P activation = 20% |  | G8.1.14 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40586 | uint16 |  |  | pcs_p_activation_20 |  |  | /components/hems_ref_pcs_1 | pcs_p_activation_20 | Yes
P deactivation = 5.0% |  | G8.1.15 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40587 | uint16 |  |  | pcs_p_deactivation_5_0 |  |  | /components/hems_ref_pcs_1 | pcs_p_deactivation_5_0 | Yes
Response Tdelay = 0.3 s |  | G8.1.16 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40588 | uint16 |  |  | pcs_response_tdelay_s_3_s |  |  | /components/hems_ref_pcs_1 | pcs_response_tdelay_s_3_s | Yes
Response Time = 5.0 s |  | G8.1.17 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40589 | uint16 |  |  | pcs_response_time_s_0_s |  |  | /components/hems_ref_pcs_1 | pcs_response_time_s_0_s | Yes
Leak Protection Type |  | G9.1.1 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40601 | uint16 |  |  | pcs_leak_protection_type |  |  | /components/hems_ref_pcs_1 | pcs_leak_protection_type | Yes
Fault Threshold = 5.0kOhms |  | G9.1.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40602 | uint16 |  |  | pcs_fault_threshold_kohms_0kohms |  |  | /components/hems_ref_pcs_1 | pcs_fault_threshold_kohms_0kohms | Yes
Fault Recover Threshold = 115% |  | G9.1.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 40603 | uint16 |  |  | pcs_fault_recover_threshold_115 |  |  | /components/hems_ref_pcs_1 | pcs_fault_recover_threshold_115 | Yes
Warning Theshold=50.0kOhms |  | G9.1.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40604 | uint16 |  |  | pcs_warning_theshold_kohms_0kohms |  |  | /components/hems_ref_pcs_1 | pcs_warning_theshold_kohms_0kohms | Yes
Self Test xec per = 1440min |  | G9.1.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40607 | uint16 |  |  | pcs_self_test_xec_per_min |  |  | /components/hems_ref_pcs_1 | pcs_self_test_xec_per_min | Yes
Self Test Manual Cmd |  | G9.1.8 | Holding Register |  | 1 |  |  |  |  | 40608 | uint16 |  |  | pcs_self_test_manual_cmd |  |  | /components/hems_ref_pcs_1 | pcs_self_test_manual_cmd | Yes
Leak Protection Type |  | G9.2.1 | Holding Register |  | 1 |  |  |  |  | 40621 | uint16 |  |  | pcs_leak_protection_type |  |  | /components/hems_ref_pcs_1 | pcs_leak_protection_type | Yes
Fault Threshold = 5.0kOhms |  | G9.2.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40622 | uint16 |  |  | pcs_fault_threshold_kohms_0kohms |  |  | /components/hems_ref_pcs_1 | pcs_fault_threshold_kohms_0kohms | Yes
Fault Recover Threshold = 115% |  | G9.2.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 40623 | uint16 |  |  | pcs_fault_recover_threshold_115 |  |  | /components/hems_ref_pcs_1 | pcs_fault_recover_threshold_115 | Yes
Warning Theshold=50.0kOhms |  | G9.2.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 40624 | uint16 |  |  | pcs_warning_theshold_kohms_0kohms |  |  | /components/hems_ref_pcs_1 | pcs_warning_theshold_kohms_0kohms | Yes
Self Test exec per = 1440 |  | G9.2.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40627 | uint16 |  |  | pcs_self_test_exec_per_1440 |  |  | /components/hems_ref_pcs_1 | pcs_self_test_exec_per_1440 | Yes
Self Test Manual Command |  | G9.2.8 | Holding Register |  | 1 | 1 |  |  | 1 | 40628 | uint16 |  |  | pcs_self_test_manual_command |  |  | /components/hems_ref_pcs_1 | pcs_self_test_manual_command | Yes
Du Type = HEM |  | G10.1 | Holding Register |  | 1 | 1 |  |  | 1 | 40650 | uint16 |  |  | pcs_du_type_hem |  |  | /components/hems_ref_pcs_1 | pcs_du_type_hem | Yes
Working Mode = GFDI + IMI |  | G10.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40651 | uint16 |  |  | pcs_working_mode_gfdi_imi |  |  | /components/hems_ref_pcs_1 | pcs_working_mode_gfdi_imi | Yes
Enabled NEC = NEC 2017 |  | G10.2b | Holding Register |  | 1 | 1 |  |  | 1 | 40649 | uint16 |  |  | pcs_enabled_nec_nec_2017 |  |  | /components/hems_ref_pcs_1 | pcs_enabled_nec_nec_2017 | Yes
Vmeasure NEC 2014 = Central DU |  | G10.2c | Holding Register |  | 1 | 1 |  |  | 1 | 40643 | uint16 |  |  | pcs_vmeasure_nec_central_du_du |  |  | /components/hems_ref_pcs_1 | pcs_vmeasure_nec_central_du_du | Yes
Isolation meas tout =300s |  | G10.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40652 | uint16 |  |  | pcs_isolation_meas_tout_s |  |  | /components/hems_ref_pcs_1 | pcs_isolation_meas_tout_s | Yes
DU channels number = 0 |  | G10.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40653 | uint16 |  |  | pcs_du_channels_number_0 |  |  | /components/hems_ref_pcs_1 | pcs_du_channels_number_0 | Yes
DU measure boards = 0 |  | G10.4a | Holding Register |  | 1 | 1 |  |  | 1 | 40644 | uint16 |  |  | pcs_du_measure_boards_0 |  |  | /components/hems_ref_pcs_1 | pcs_du_measure_boards_0 | Yes
Channels DU meas 1 = 0 |  | G10.4b | Holding Register |  | 1 | 1 |  |  | 1 | 40645 | uint16 |  |  | pcs_channels_du_meas_1_0 |  |  | /components/hems_ref_pcs_1 | pcs_channels_du_meas_1_0 | Yes
Channels DU meas 2 = 0 |  | G10.4c | Holding Register |  | 1 | 1 |  |  | 1 | 40646 | uint16 |  |  | pcs_channels_du_meas_2_0 |  |  | /components/hems_ref_pcs_1 | pcs_channels_du_meas_2_0 | Yes
Channels DU meas 3 = 0 |  | G10.4d | Holding Register |  | 1 | 1 |  |  | 1 | 40647 | uint16 |  |  | pcs_channels_du_meas_3_0 |  |  | /components/hems_ref_pcs_1 | pcs_channels_du_meas_3_0 | Yes
Channels DU meas 4 = 0 |  | G10.4.e | Holding Register |  | 1 | 1 |  |  | 1 | 40648 | uint16 |  |  | pcs_channels_du_meas_4_0 |  |  | /components/hems_ref_pcs_1 | pcs_channels_du_meas_4_0 | Yes
Channel 1 ID = off |  | G10.4.1 | Holding Register |  | 1 | 1 |  |  | 1 | 40654 | uint16 |  |  | pcs_channel_1_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_1_id_off | Yes
Channel 2 ID = off |  | G10.4.2 | Holding Register |  | 1 | 1 |  |  | 1 | 40655 | uint16 |  |  | pcs_channel_2_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_2_id_off | Yes
Channel 3 ID = off |  | G10.4.3 | Holding Register |  | 1 | 1 |  |  | 1 | 40656 | uint16 |  |  | pcs_channel_3_d_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_3_d_off | Yes
Channel 4 ID = off |  | G10.4.4 | Holding Register |  | 1 | 1 |  |  | 1 | 40657 | uint16 |  |  | pcs_channel_4_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_4_id_off | Yes
Channel 5 ID = off |  | G10.4.5 | Holding Register |  | 1 | 1 |  |  | 1 | 40658 | uint16 |  |  | pcs_channel_5_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_5_id_off | Yes
Channel 6 ID = off |  | G10.4.6 | Holding Register |  | 1 | 1 |  |  | 1 | 40659 | uint16 |  |  | pcs_channel_6_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_6_id_off | Yes
Channel 7 ID = off |  | G10.4.7 | Holding Register |  | 1 | 1 |  |  | 1 | 40660 | uint16 |  |  | pcs_channel_7_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_7_id_off | Yes
Channel 8 ID = off |  | G10.4.8 | Holding Register |  | 1 | 1 |  |  | 1 | 40661 | uint16 |  |  | pcs_channel_8_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_8_id_off | Yes
Channel 9 ID = off |  | G10.4.9 | Holding Register |  | 1 | 1 |  |  | 1 | 40662 | uint16 |  |  | pcs_channel_id_9_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_id_9_off | Yes
Channel 10 ID = off |  | G10.4.10 | Holding Register |  | 1 | 1 |  |  | 1 | 40663 | uint16 |  |  | pcs_channel_10_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_10_id_off | Yes
Channel 11 ID = off |  | G10.4.11 | Holding Register |  | 1 | 1 |  |  | 1 | 40664 | uint16 |  |  | pcs_channel_11_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_11_id_off | Yes
Channel 12 ID = off |  | G10.4.12 | Holding Register |  | 1 | 1 |  |  | 1 | 40665 | uint16 |  |  | pcs_channel_12_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_12_id_off | Yes
Channel 13 ID = off |  | G10.4.13 | Holding Register |  | 1 | 1 |  |  | 1 | 40666 | uint16 |  |  | pcs_channel_13_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_13_id_off | Yes
Channel 14 ID = off |  | G10.4.14 | Holding Register |  | 1 | 1 |  |  | 1 | 40667 | uint16 |  |  | pcs_channel_14_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_14_id_off | Yes
Channel 15 ID = off |  | G10.4.15 | Holding Register |  | 1 | 1 |  |  | 1 | 40668 | uint16 |  |  | pcs_channel_15_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_15_id_off | Yes
Channel 16 ID = off |  | G10.4.16 | Holding Register |  | 1 | 1 |  |  | 1 | 40669 | uint16 |  |  | pcs_channel_16_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_16_id_off | Yes
Channel 17 ID = off |  | G10.4.17 | Holding Register |  | 1 | 1 |  |  | 1 | 40670 | uint16 |  |  | pcs_channel_17_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_17_id_off | Yes
Channel 18 ID = off |  | G10.4.18 | Holding Register |  | 1 | 1 |  |  | 1 | 40671 | uint16 |  |  | pcs_channel_18_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_18_id_off | Yes
Channel 19 ID = off |  | G10.4.19 | Holding Register |  | 1 | 1 |  |  | 1 | 40672 | uint16 |  |  | pcs_channel_19_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_19_id_off | Yes
Channel 20 ID = off |  | G10.4.20 | Holding Register |  | 1 | 1 |  |  | 1 | 40673 | uint16 |  |  | pcs_channel_20_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_20_id_off | Yes
Channel 21 ID = off |  | G10.4.21 | Holding Register |  | 1 | 1 |  |  | 1 | 40674 | uint16 |  |  | pcs_channel_21_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_21_id_off | Yes
Channel 22 ID = off |  | G10.4.22 | Holding Register |  | 1 | 1 |  |  | 1 | 40675 | uint16 |  |  | pcs_channel_22_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_22_id_off | Yes
Channel 23 ID = off |  | G10.4.23 | Holding Register |  | 1 | 1 |  |  | 1 | 40676 | uint16 |  |  | pcs_channel_23_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_23_id_off | Yes
Channel 24 ID = off |  | G10.4.24 | Holding Register |  | 1 |  |  |  |  | 40677 | uint16 |  |  | pcs_channel_24_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_24_id_off | Yes
Channel 25 ID = off |  | G10.4.25 | Holding Register |  | 1 |  |  |  |  | 40678 | uint16 |  |  | pcs_channel_25_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_25_id_off | Yes
Channel 26 ID = off |  | G10.4.26 | Holding Register |  | 1 |  |  |  |  | 40679 | uint16 |  |  | pcs_channel_26_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_26_id_off | Yes
Channel 27 ID = off |  | G10.4.27 | Holding Register |  | 1 |  |  |  |  | 40680 | uint16 |  |  | pcs_channel_27_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_27_id_off | Yes
Channel 28 ID = off |  | G10.4.28 | Holding Register |  | 1 |  |  |  |  | 40681 | uint16 |  |  | pcs_channel_28_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_28_id_off | Yes
Channel 29 ID = off |  | G10.4.29 | Holding Register |  | 1 |  |  |  |  | 40682 | uint16 |  |  | pcs_channel_29_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_29_id_off | Yes
Channel 30 ID = off |  | G10.4.30 | Holding Register |  | 1 |  |  |  |  | 40683 | uint16 |  |  | pcs_channel_30_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_30_id_off | Yes
Channel 31 ID = off |  | G10.4.31 | Holding Register |  | 1 |  |  |  |  | 40684 | uint16 |  |  | pcs_channel_31_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_31_id_off | Yes
Channel 32 ID = off |  | G10.4.32 | Holding Register |  | 1 |  |  |  |  | 40685 | uint16 |  |  | pcs_channel_32_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_32_id_off | Yes
Channel 33 ID = off |  | G10.4.33 | Holding Register |  | 1 |  |  |  |  | 40686 | uint16 |  |  | pcs_channel_33_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_33_id_off | Yes
Channel 34 ID = off |  | G10.4.34 | Holding Register |  | 1 |  |  |  |  | 40687 | uint16 |  |  | pcs_channel_34_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_34_id_off | Yes
Channel 35 ID = off |  | G10.4.35 | Holding Register |  | 1 |  |  |  |  | 40688 | uint16 |  |  | pcs_channel_35_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_35_id_off | Yes
Channel 36 ID = off |  | G10.4.36 | Holding Register |  | 1 |  |  |  |  | 40689 | uint16 |  |  | pcs_channel_36_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_36_id_off | Yes
Channel 37 ID = off |  | G10.4.37 | Holding Register |  | 1 |  |  |  |  | 40690 | uint16 |  |  | pcs_channel_37_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_37_id_off | Yes
Channel 38 ID = off |  | G10.4.38 | Holding Register |  | 1 |  |  |  |  | 40691 | uint16 |  |  | pcs_channel_38_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_38_id_off | Yes
Channel 39 ID = off |  | G10.4.39 | Holding Register |  | 1 |  |  |  |  | 40692 | uint16 |  |  | pcs_channel_39_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_39_id_off | Yes
Channel 40 ID = off |  | G10.4.40 | Holding Register |  | 1 |  |  |  |  | 40693 | uint16 |  |  | pcs_channel_40_id_off |  |  | /components/hems_ref_pcs_1 | pcs_channel_40_id_off | Yes
Select Action = Disabled |  | G10.5 | Holding Register |  | 1 |  |  |  |  | 40694 | uint16 |  |  | pcs_select_action_disabled |  |  | /components/hems_ref_pcs_1 | pcs_select_action_disabled | Yes
Max Power = 10KW |  | G12.1.1 | Holding Register | kW | 1 | 1 |  |  | 1 | 40811 | uint16 |  |  | pcs_max_power_kw |  |  | /components/hems_cmd_pcs_1 | pcs_max_power_kw | Yes
Delay Max Power fault = 10s |  | G12.1.2 | Holding Register | S | 1 | 1 |  |  | 1 | 40812 | uint16 |  |  | pcs_delay_max_power_fault_s |  |  | /components/hems_cmd_pcs_1 | pcs_delay_max_power_fault_s | Yes
Max Current = 100A |  | G12.1.3 | Holding Register | A | 1 | 1 |  |  | 1 | 40813 | uint16 |  |  | pcs_max_current_a |  |  | /components/hems_cmd_pcs_1 | pcs_max_current_a | Yes
Delay Max Current Fault - 1 s |  | G12.1.4 | Holding Register | S | 1 | 1 |  |  | 1 | 40814 | uint16 |  |  | pcs_delay_max_current_fault_s_s |  |  | /components/hems_cmd_pcs_1 | pcs_delay_max_current_fault_s_s | Yes
Max Voltage Fault - 120% |  | G12.1.5 | Holding Register | % | 1 | 1 |  |  | 1 | 40815 | uint16 |  |  | pcs_max_voltage_fault_120 |  |  | /components/hems_cmd_pcs_1 | pcs_max_voltage_fault_120 | Yes
Min Voltage Fault = 88% |  | G12.1.6 | Holding Register | % | 1 | 1 |  |  | 1 | 40816 | uint16 |  |  | pcs_min_voltage_fault_88 |  |  | /components/hems_cmd_pcs_1 | pcs_min_voltage_fault_88 | Yes
Enable G12.2 |  | G12.2 | Holding Register |  | 1 |  |  |  |  | 40801 | uint16 |  |  | pcs_enable_g_2 |  |  |  | pcs_enable_g_2 | Yes
BFPS status |  | G12.3 | Holding Register |  | 1 |  |  |  |  | 40802 | bit_field |  |  | pcs_bfps_status |  |  |  | pcs_bfps_status | Yes
BFPS online |  | G12.3.0 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 0 |  | pcs_bit_bfpso |  |  |  | pcs_bit_bfpso | Yes
BFPS Contactor |  | G123.1 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 1 |  | pcs_bit_bfpso |  |  |  | pcs_bit_bfpso | Yes
BFPS Feeback Contactor |  | G12.3.2 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 2 |  | pcs_bit_bfps_contactoro |  |  |  | pcs_bit_bfps_contactoro | Yes
BFPS current present error |  | G12.3.3 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 3 |  | pcs_bit_bfps_presento |  |  |  | pcs_bit_bfps_presento | Yes
BFPS Feedback close error |  | G12.3.4 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 4 |  | pcs_bit_bfps_closeo |  |  |  | pcs_bit_bfps_closeo | Yes
BFPS Feedback opn error |  | G12.3.5 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 5 |  | pcs_bit_bfps_opno |  |  |  | pcs_bit_bfps_opno | Yes
BFPS comms error |  | G12.3.6 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 6 |  | pcs_bit_bfps_erroro |  |  |  | pcs_bit_bfps_erroro | Yes
BFPS No conditions error |  | G12.3.7 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 7 |  | pcs_bit_bfps_conditionso |  |  |  | pcs_bit_bfps_conditionso | Yes
BFPS Max power fault |  | G12.3.8 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 8 |  | pcs_bit_bfps_powero |  |  |  | pcs_bit_bfps_powero | Yes
BFPS Max Current Fault |  | G12.3.9 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 9 |  | pcs_bit_bfps_currento |  |  |  | pcs_bit_bfps_currento | Yes
BFPS High voltage fault |  | G12.3.10 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 10 |  | pcs_bit_bfps_voltageo |  |  |  | pcs_bit_bfps_voltageo | Yes
BFPS Low voltage fault |  | G12.3.11 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 11 |  | pcs_bit_bfps_voltageo |  |  |  | pcs_bit_bfps_voltageo | Yes
BFPS Contactor fault |  | G12.3.12 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 12 |  | pcs_bit_bfps_faulto |  |  |  | pcs_bit_bfps_faulto | Yes
BFPS Blown Fuse fault |  | G12.3.13 | Holding Register |  | 1 |  |  |  |  | 40802 | bit | 13 |  | pcs_bit_bfps_fuseo |  |  |  | pcs_bit_bfps_fuseo | Yes
Action = Disabled |  | G12.4 | Holding Register |  | 1 |  |  |  |  | 40803 | uint16 |  |  | pcs_action_disabled |  |  | /components/hems_cmd_pcs_1 | pcs_action_disabled | Yes
Current Measureed = 0.0 A |  | G12.5 | Input Register | A | 1 | 10 |  |  | 0.1 | 40804 | uint16 |  |  | pcs_current_measureed_a_0_a |  |  | /components/hems_mon_pcs_1 | pcs_current_measureed_a_0_a | Yes
Voltage Measureed | Control | G12.6 | Input Register | V | 1 | 10 |  |  | 0.1 | 40805 | uint16 |  |  | pcs_voltage_measureed |  | 0.1% to 200.0%, 1 to 2000 | /components/hems_mon_pcs_1 | pcs_voltage_measureed | Yes
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A13: Tony Olivo: Do not add rows below this line, the script will break
Note on A14: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B14: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D14: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E14: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F14: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G14: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H14: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J14: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on K14: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on L14: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on M14: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on N14: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on O14: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on P14: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on Q14: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on R14: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on S14: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on T14: Tony Olivo: Yes/No whether to include in the client/server config
Note on U14: Tony Olivo: For humans
Note on V14: Tony Olivo: For humans
Note on W14: Tony Olivo: Ranges are for humans only