## SC1725
Connection Name | Sungrow PCS SC1725
Connection Name | Sungrow PCS SC1725
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device Name | sungrow_pcs_sc1725
Device ID String | sungrow_pcs_sc1725
ip_address | 127.0.0.1
port | 502
Device Port (502 typical)
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address | Address Original | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
Running information | [15 empty] | pcs_running_info | TRUE | life_signal | life | 200 | 200 | 10000 | 20 | 98
Protocol number |  |  | Input Register |  | 2 |  |  |  |  | 3200 |  | uint32 |  |  | protocol_num | [11 empty] | /components/pcs_running_info |  | Yes
Protocol version |  |  | Input Register |  | 2 |  |  |  |  | 3202 |  | uint32 |  |  | protocol_version | [11 empty] | /components/pcs_running_info |  | Yes
Serial Number |  |  | Input Register | [6 empty] | 3204 |  | uint16 |  |  | serial_num | [11 empty] | /components/pcs_running_info |  | Yes
Device Type Code |  |  | Input Register | [6 empty] | 3250 |  | uint16 |  |  | device_type_code | [11 empty] | /components/pcs_running_info |  | Yes
Overall Fault State |  |  | Input Register | [6 empty] | 3288 |  | uint16 |  |  | fault_state | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: overall fault state
Overall Alarm State |  |  | Input Register |  | 2 |  |  |  |  | 3289 |  | uint32 |  |  | alarm_state | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: overall alarm state
MV Node State |  |  | Input Register |  | 2 |  |  |  |  | 3291 |  | uint32 |  |  | mv_node_state | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: MV node state
Transformer Oil Temperature |  |  | Input Register | °C |  | 0.1 |  |  | 10 | 3293 |  | int16 |  |  | trans_oil_temp | [11 empty] | /components/pcs_running_info |  | Yes
Heartbeat Count |  |  | Input Register | [6 empty] | 3294 |  | uint16 |  |  | heartbeat | [11 empty] | /components/pcs_running_info |  | Yes | Increase once every 1s
Leakage Current |  |  | Input Register |  |  | 0.01 |  |  | 100 | 3297 |  | uint16 |  |  | leakage_current | [11 empty] | /components/pcs_running_info |  | Yes
MV Node State 1 |  |  | Input Register |  | 2 |  |  |  |  | 3298 |  | uint32 |  |  | mv_node_state_1 | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: mv node state 1
MV Node State 2 |  |  | Input Register |  | 2 |  |  |  |  | 3300 |  | uint32 |  |  | mv_node_state_2 | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: mv node state 2
Winding Temperature |  |  | Input Register |  |  | 0.1 |  |  | 10 | 3302 |  | int16 |  |  | winding_temp | [11 empty] | /components/pcs_running_info |  | Yes
Module Temperature 1 |  |  | Input Register | °C |  | 0.1 |  |  | 10 | 3304 |  | int16 |  |  | module_temp_1 | [11 empty] | /components/pcs_running_info |  | Yes
Module Temperature 2 |  |  | Input Register | °C |  | 0.1 |  |  | 10 | 3305 |  | int16 |  |  | module_temp_2 | [11 empty] | /components/pcs_running_info |  | Yes
Module Temperature 3 |  |  | Input Register | °C |  | 0.1 |  |  | 10 | 3306 |  | int16 |  |  | module_temp_3 | [11 empty] | /components/pcs_running_info |  | Yes
DC Voltage |  |  | Input Register | V |  | 0.1 |  |  | 10 | 3310 |  | int16 |  |  | dc_voltage | [11 empty] | /components/pcs_running_info |  | Yes
DC Current |  |  | Input Register | A |  | 0.1 |  |  | 10 | 3311 |  | int16 |  |  | dc_current | [11 empty] | /components/pcs_running_info |  | Yes
DC Power |  |  | Input Register | kW |  | 0.1 |  |  | 10 | 3312 |  | int16 |  |  | dc_power | [11 empty] | /components/pcs_running_info |  | Yes
Grid Voltage Vab |  |  | Input Register | V |  | 0.1 |  |  | 10 | 3313 |  | uint16 |  |  | grid_voltage_vab | [11 empty] | /components/pcs_running_info |  | Yes
Grid Voltage Vbc |  |  | Input Register | V |  | 0.1 |  |  | 10 | 3314 |  | uint16 |  |  | grid_voltage_vbc | [11 empty] | /components/pcs_running_info |  | Yes
Grid Voltage Vca |  |  | Input Register | V |  | 0.1 |  |  | 10 | 3315 |  | uint16 |  |  | grid_voltage_vca | [11 empty] | /components/pcs_running_info |  | Yes
Phase A Current |  |  | Input Register | A |  | 0.1 |  |  | 10 | 3316 |  | uint16 |  |  | phase_a_current | [11 empty] | /components/pcs_running_info |  | Yes
Phase B Current |  |  | Input Register | A |  | 0.1 |  |  | 10 | 3317 |  | uint16 |  |  | phase_b_current | [11 empty] | /components/pcs_running_info |  | Yes
Phase C Current |  |  | Input Register | A |  | 0.1 |  |  | 10 | 3318 |  | uint16 |  |  | phase_c_current | [11 empty] | /components/pcs_running_info |  | Yes
Active Power |  |  | Input Register | kW | 2 | 0.1 |  |  | 10 | 3319 |  | int32 |  |  | active_power | [11 empty] | /components/pcs_running_info |  | Yes
Reactive Power |  |  | Input Register | kVar | 2 | 0.1 |  |  | 10 | 3321 |  | int32 |  |  | reactive_power | [11 empty] | /components/pcs_running_info |  | Yes
Positive Impedance to Ground |  |  | Input Register | kΩ | 2 | 0.01 |  |  |  | 3323 |  | uint32 |  |  | pos_ground_impedence | [11 empty] | /components/pcs_running_info |  | Yes
Negative Impedance to Ground |  |  | Input Register | kΩ | 2 | 0.01 |  |  |  | 3325 |  | uint32 |  |  | neg_ground_impedence | [11 empty] | /components/pcs_running_info |  | Yes
Alarm Running State 1 |  |  | Input Register | [6 empty] | 3327 |  | uint16 |  |  | alarm_running_state_1 | [11 empty] | /components/pcs_running_info |  | Yes | Refer to table: Alarm running state 1
Alarm Running State 2 |  |  | Input Register | [6 empty] | 3328 |  | uint16 |  |  | alarm_running_state_2 | [11 empty] | /components/pcs_running_info |  | Yes | Refer to table: Alarm running state 2
Fault State 1 |  |  | Input Register |  | 2 |  |  |  |  | 3329 |  | uint32 |  |  | fault_state_1 | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: Fault state 1 of unit 1
Fault State 2 |  |  | Input Register |  | 2 |  |  |  |  | 3331 |  | uint32 |  |  | fault_state_2 | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: Fault state 2 of unit 1
Charging/Discharging State |  |  | Input Register | [6 empty] | 3333 |  | uint16 |  |  | charge_state | [11 empty] | /components/pcs_running_info |  | Yes | 0: Charging, 1: Discharging, 2: Non-operating mode
Daily Charging |  |  | Input Register | kWh | 2 | 0.1 |  |  |  | 3334 |  | uint32 |  |  | daily_charging | [11 empty] | /components/pcs_running_info |  | Yes
Daily Discharging |  |  | Input Register | kWh | 2 | 0.1 |  |  |  | 3336 |  | uint32 |  |  | daily_discharging | [11 empty] | /components/pcs_running_info |  | Yes
Total Charging |  |  | Input Register | kWh | 2 |  |  |  |  | 3338 |  | uint32 |  |  | total_charging | [11 empty] | /components/pcs_running_info |  | Yes
Total Discharging |  |  | Input Register | kWh | 2 |  |  |  |  | 3340 |  | uint32 |  |  | total_discharging | [11 empty] | /components/pcs_running_info |  | Yes
Work State |  |  | Input Register |  | 2 |  |  |  |  | 3342 |  | uint32 |  |  | work_state | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: Working state
Operating Mode |  |  | Input Register | [6 empty] | 3344 |  | uint16 |  |  | operating_mode | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: Operating mode
Nominal Output Power |  |  | Input Register | kW |  | 0.1 |  |  |  | 3348 |  | uint16 |  |  | nominal_output_power | [11 empty] | /components/pcs_running_info |  | Yes
Nominal Reactive Output Power |  |  | Input Register | kVar |  | 0.1 |  |  |  | 3349 |  | uint16 |  |  | nominal_reactive_output_power | [11 empty] | /components/pcs_running_info |  | Yes
Grid Status |  |  | Input Register | [6 empty] | 3351 |  | uint16 |  |  | grid_status | [11 empty] | /components/pcs_running_info |  | Yes | 0: disconnect, 1: connect
Grid Frequency |  |  | Input Register | Hz |  | 0.01 |  |  |  | 3352 |  | uint16 |  |  | grid_frequency | [11 empty] | /components/pcs_running_info |  | Yes
Power Factor |  |  | Input Register |  |  | 0.001 |  |  |  | 3353 |  | uint16 |  |  | power_factor | [11 empty] | /components/pcs_running_info |  | Yes
Ambient Temperature |  |  | Input Register | °C |  | 0.1 |  |  |  | 3354 |  | int16 |  |  | ambient_temp | [11 empty] | /components/pcs_running_info |  | Yes
Node State |  |  | Input Register |  | 2 |  |  |  |  | 3355 |  | uint32 |  |  | node_state | [11 empty] | /components/pcs_running_info |  | Yes | Refer to appendix: Node state
Daily Charging Hours |  |  | Input Register | min | [5 empty] | 3357 |  | uint16 |  |  | daily_charging_hr | [11 empty] | /components/pcs_running_info |  | Yes
Daily Discharging Hours |  |  | Input Register | min | [5 empty] | 3358 |  | uint16 |  |  | daily_discharging_hr | [11 empty] | /components/pcs_running_info |  | Yes
Total Charging Hours |  |  | Input Register | h | 2 |  |  |  |  | 3359 |  | uint32 |  |  | total_charging_hr | [11 empty] | /components/pcs_running_info |  | Yes
Total Discharging Hours |  |  | Input Register | h | 2 |  |  |  |  | 3361 |  | uint32 |  |  | total_discharging_hr | [11 empty] | /components/pcs_running_info |  | Yes
Max Charging Power |  |  | Input Register | kW |  | 0.1 |  |  | 10 | 3363 |  | int16 |  |  | max_charging_power | [11 empty] | /components/pcs_running_info |  | Yes
Max Discharging Power |  |  | Input Register | kW |  | 0.1 |  |  | 10 | 3364 |  | int16 |  |  | max_discharging_power | [11 empty] | /components/pcs_running_info |  | Yes
Max Inductive Reactive Power |  |  | Input Register | kVar |  | 0.1 |  |  | 10 | 3365 |  | int16 |  |  | max_inductive_reactive_power | [11 empty] | /components/pcs_running_info |  | Yes
Max Capacitive Reactive Power |  |  | Input Register | kVar |  | 0.1 |  |  | 10 | 3366 |  | int16 |  |  | max_capacitive_reactive_power | [11 empty] | /components/pcs_running_info |  | Yes
Current Number of Black Start Beats |  |  | Input Register | [6 empty] | 3369 |  | uint16 |  |  | num_black_start_beats | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 1 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4000 |  | int16 |  |  | branch_current_1 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 2 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4001 |  | int16 |  |  | branch_current_2 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 3 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4002 |  | int16 |  |  | branch_current_3 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 4 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4003 |  | int16 |  |  | branch_current_4 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 5 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4004 |  | int16 |  |  | branch_current_5 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 6 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4005 |  | int16 |  |  | branch_current_6 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 7 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4006 |  | int16 |  |  | branch_current_7 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 8 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4007 |  | int16 |  |  | branch_current_8 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 9 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4008 |  | int16 |  |  | branch_current_9 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 10 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4009 |  | int16 |  |  | branch_current_10 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 11 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4010 |  | int16 |  |  | branch_current_11 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 12 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4011 |  | int16 |  |  | branch_current_12 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 13 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4012 |  | int16 |  |  | branch_current_13 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 14 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4013 |  | int16 |  |  | branch_current_14 | [11 empty] | /components/pcs_running_info |  | Yes
Branch Current 15 |  |  | Input Register | A |  | 0.1 |  |  | 10 | 4014 |  | int16 |  |  | branch_current_15 | [11 empty] | /components/pcs_running_info |  | Yes
Parameter Setting | [15 empty] | pcs_parameter_setting | TRUE | life_signal | life | 200 | 200 | 100 | 20 | 98
System Time (Year) |  |  | Holding Register | [6 empty] | 3250 |  | uint16 |  |  | year | [11 empty] | /components/pcs_parameter_setting |  | Yes
System Time (Month) |  |  | Holding Register | [6 empty] | 3251 |  | uint16 |  |  | month | [11 empty] | /components/pcs_parameter_setting |  | Yes
System Time (Day) |  |  | Holding Register | [6 empty] | 3252 |  | uint16 |  |  | day | [11 empty] | /components/pcs_parameter_setting |  | Yes
System Time (Hour) |  |  | Holding Register | [6 empty] | 3253 |  | uint16 |  |  | hour | [11 empty] | /components/pcs_parameter_setting |  | Yes
System Time (Minute) |  |  | Holding Register | [6 empty] | 3254 |  | uint16 |  |  | minute | [11 empty] | /components/pcs_parameter_setting |  | Yes
System Time (Second) |  |  | Holding Register | [6 empty] | 3255 |  | uint16 |  |  | second | [11 empty] | /components/pcs_parameter_setting |  | Yes
Start/Stop/Standby |  |  | Holding Register | [6 empty] | 3256 |  | uint16 |  |  | start_stop | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xCD: Standby, 0xCE: Stop, 0xCF: Start
On/Off-Grid Mode Setting |  |  | Holding Register | [6 empty] | 3257 |  | uint16 |  |  | grid_mode_setting | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xAA: on-grid mode, 0x55: off-grid mode, 0xBB: VSG mode
Reactive Power Adjustment Switch |  |  | Holding Register | [6 empty] | 3258 |  | uint16 |  |  | reactive_power_adj_switch | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0x55: OFF, power factor automatically returns to 1 0xA1: Power factor setting is enabled 0xA2: Reactive Power percentage setting is enabled 0xA3: Reactive power operation Q(U) setting is enabled 0xA4: Reactive Power operation Q(P)
Remote/Local |  |  | Holding Register | [6 empty] | 3259 |  | uint16 |  |  | control_state | [11 empty] | /components/pcs_parameter_setting |  | Yes | 3: Remote & Local, 1: Remote, 2: Local
Active/Reactive Priority |  |  | Holding Register | [6 empty] | 3260 |  | uint16 |  |  | power_priority | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xAA: Active power takes priority 0x55: Reactive Power takes priority
Power Soft Start Enabling |  |  | Holding Register | [6 empty] | 3261 |  | uint16 |  |  | power_soft_start | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
AC Pre-charging Enabling |  |  | Holding Register | [6 empty] | 3270 |  | uint16 |  |  | ac_precharge | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Quick Dispatch |  |  | Holding Register | [6 empty] | 3271 |  | uint16 |  |  | quick_dispatch | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Zero Power Standby |  |  | Holding Register | [6 empty] | 3272 |  | uint16 |  |  | zero_power_standby | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
On-grid Charging/Discharging Mode |  |  | Holding Register | [6 empty] | 3300 |  | uint16 |  |  | on_grid_mode | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0x01: On-grid constant current 0x02: On-grid constant voltage 0x04: On-grid constant power (AC) 0x08: On-grid constant power (DC)
On-grid Constant Current Value |  |  | Holding Register | A | [5 empty] | 3301 |  | int16 |  |  | on_grid_const_current | [11 empty] | /components/pcs_parameter_setting |  | Yes
On-grid Constant Voltage Value |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3302 |  | uint16 |  |  | on_grid_const_voltage | [11 empty] | /components/pcs_parameter_setting |  | Yes
On-grid Constant Voltage Limit Current |  |  | Holding Register | A | [5 empty] | 3303 |  | uint16 |  |  | on_grid_const_volt_limit_current | [11 empty] | /components/pcs_parameter_setting |  | Yes
On-grid Constant Power (AC) |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3304 |  | int16 |  |  | on_grid_const_ac_power | [11 empty] | /components/pcs_parameter_setting |  | Yes
On-grid Constant Power (DC) |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3305 |  | int16 |  |  | on_grid_const_dc_power | [11 empty] | /components/pcs_parameter_setting |  | Yes
Independent Converter Voltage |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3306 |  | uint16 |  |  | independent_converter_voltage | [11 empty] | /components/pcs_parameter_setting |  | Yes
Independent Converter Frequency |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3307 |  | uint16 |  |  | independent_converter_frequency | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max Battery Charging Voltage |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3310 |  | uint16 |  |  | max_batt_charging_volt | [11 empty] | /components/pcs_parameter_setting |  | Yes
Min Battery Discharging Voltage |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3311 |  | uint16 |  |  | max_batt_discharging_volt | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max Battery Charging Current |  |  | Holding Register | A | [5 empty] | 3312 |  | int16 |  |  | max_batt_charging_current | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max Battery Discharging Current |  |  | Holding Register | A | [5 empty] | 3313 |  | uint16 |  |  | max_batt_discharging_current | [11 empty] | /components/pcs_parameter_setting |  | Yes
Frequency Ride Through Enabling |  |  | Holding Register | [6 empty] | 3314 |  | uint16 |  |  | frequency_ride_through_enable | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Frequency Ride Through Compensation Factor |  |  | Holding Register |  |  | 0.1 |  |  | 10 | 3315 |  | uint16 |  |  | frequency_ride_through_comp_factor | [11 empty] | /components/pcs_parameter_setting |  | Yes
Heartbeat |  |  | Holding Register | [6 empty] | 3316 |  | uint16 |  |  | heartbeat | [11 empty] | /components/pcs_parameter_setting |  | Yes | Heartbeat counts delivered by PC
Heartbeat Timeout Interval |  |  | Holding Register | s | [5 empty] | 3317 |  | uint16 |  |  | hearbeat_timeout_interval | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disable the heartbeat timeout shutdown function Other values: The converter stops when heartbeat change interval exceeds the value
Reactive Power Percentage Setting |  |  | Holding Register | % | [5 empty] | 3319 |  | int16 |  |  | reactive_power_pct_setting | [11 empty] | /components/pcs_parameter_setting |  | Yes
Power Factor Setting |  |  | Holding Register | [6 empty] | 3320 |  | int16 |  |  | power_factor_setting | [11 empty] | /components/pcs_parameter_setting |  | Yes
P(f) Frequency Regulation Control Enabling |  |  | Holding Register | [6 empty] | 3321 |  | uint16 |  |  | pf_frequency_regulation_control | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
P(f) Deadband Frequency |  |  | Holding Register | Hz | [5 empty] | 3322 |  | uint16 |  |  | pf_deadband_frequency | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max Charging Frequency Regulation Power |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3325 |  | uint16 |  |  | max_charging_frequency_regulation_power | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max Discharging Frequency Regulation Power |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3326 |  | uint16 |  |  | max_discharging_frequency_regulation_power | [11 empty] | /components/pcs_parameter_setting |  | Yes
VSG Rated Output Voltage |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3330 |  | uint16 |  |  | vsg_rated_output_voltage | [11 empty] | /components/pcs_parameter_setting |  | Yes
VSG Rated Output Frequency |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3331 |  | uint16 |  |  | vsg_rated_output_frequency | [11 empty] | /components/pcs_parameter_setting |  | Yes
VSG Frequency Droop Slope |  |  | Holding Register |  |  | 0.1 |  |  | 10 | 3332 |  | uint16 |  |  | vsg_frequency_droop_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
VSG Voltage Droop Slope |  |  | Holding Register |  |  | 0.1 |  |  | 10 | 3333 |  | uint16 |  |  | vsg_voltage_droop_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
VSG Active Setting Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3334 |  | int16 |  |  | vsg_active_setting | [11 empty] | /components/pcs_parameter_setting |  | Yes
VSG Reactive Setting Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3335 |  | int16 |  |  | vsg_reactive_setting | [11 empty] | /components/pcs_parameter_setting |  | Yes
BMS Communication Exception Switch |  |  | Holding Register | [6 empty] | 3370 |  | uint16 |  |  | bms_comms_exception_switch | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xAA: Enabled, 0x55: Disabled
BMS Communication Exception Time |  |  | Holding Register | s | [5 empty] | 3371 |  | uint16 |  |  | bms_comms_exception_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Active Power Rising Slope |  |  | Holding Register | %/s |  | 0.1 |  |  | 10 | 3387 |  | uint16 |  |  | active_power_rising_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
Active Power Droop Slope |  |  | Holding Register | %/s |  | 0.1 |  |  | 10 | 3388 |  | uint16 |  |  | active_power_droop_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
Reactive Power Rising Slope |  |  | Holding Register | %/s |  | 0.1 |  |  | 10 | 3390 |  | uint16 |  |  | reactive_power_rising_sloop | [11 empty] | /components/pcs_parameter_setting |  | Yes
Reactive Power Droop Slope |  |  | Holding Register | %/s |  | 0.1 |  |  | 10 | 3391 |  | uint16 |  |  | reactive_power_droop_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
QU Voltage Rising Start Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3392 |  | uint16 |  |  | qu_voltage_rising_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QU Voltage Rising End Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3393 |  | uint16 |  |  | qu_voltage_rising_end_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QU Voltage Droop Start Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3394 |  | uint16 |  |  | qu_voltage_droop_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QU Voltage Droop End Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3395 |  | uint16 |  |  | qu_voltage_droop_end_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QU Working Mode |  |  | Holding Register | [6 empty] | 3396 |  | uint16 |  |  | qu_working_mode | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xA1: Power Factor mode, 0xA1: Reactive Power percentage mode
Max QU Reactive Power |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3397 |  | uint16 |  |  | max_qu_reactive_power | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max QU PF |  |  | Holding Register |  |  | 0.001 |  |  | 1000 | 3398 |  | uint16 |  |  | max_qu_pf | [11 empty] | /components/pcs_parameter_setting |  | Yes
QU Enabling Power |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3399 |  | uint16 |  |  | qu_enabling_power | [11 empty] | /components/pcs_parameter_setting |  | Yes
Stop Delay Time T |  |  | Holding Register | s | [5 empty] | 3404 |  | uint16 |  |  | stop_delay_time_t | [11 empty] | /components/pcs_parameter_setting |  | Yes
Stop Slope L |  |  | Holding Register | %/s | [5 empty] | 3405 |  | uint16 |  |  | stop_slope_l | [11 empty] | /components/pcs_parameter_setting |  | Yes
DC Mode |  |  | Holding Register | [6 empty] | 3406 |  | uint16 |  |  | dc_mode | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: DC parallel, 1: DC independent
Auto Recovery Time |  |  | Holding Register | s | [5 empty] | 3407 |  | uint16 |  |  | auto_recovery_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Battery Charging SOC Upper Limit |  |  | Holding Register | % | [5 empty] | 3411 |  | uint16 |  |  | batt_charging_soc_upper_limit | [11 empty] | /components/pcs_parameter_setting |  | Yes
Battery Discharging SOC Lower Limit |  |  | Holding Register | % | [5 empty] | 3412 |  | uint16 |  |  | batt_discharging_soc_lower_limit | [11 empty] | /components/pcs_parameter_setting |  | Yes
Leakage Current Protection Value |  |  | Holding Register | A |  | 0.01 |  |  | 100 | 3415 |  | uint16 |  |  | leakage_current_protection | [11 empty] | /components/pcs_parameter_setting |  | Yes
Active Islanding Enabling |  |  | Holding Register | [6 empty] | 3416 |  | uint16 |  |  | active_islanding | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xAA: Enabled, 0x55: Disabled
LVRT Switch |  |  | Holding Register | [6 empty] | 3417 |  | uint16 |  |  | lvrt_switch | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT Voltage 1 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3418 |  | uint16 |  |  | lvrt_voltage_1 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT Voltage 2 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3419 |  | uint16 |  |  | lvrt_voltage_2 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT Voltage 3 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3420 |  | uint16 |  |  | lvrt_voltage_3 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT Voltage 4 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3421 |  | uint16 |  |  | lvrt_voltage_4 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT Voltage 5 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3422 |  | uint16 |  |  | lvrt_voltage_5 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT Dynamic Kf Factor |  |  | Holding Register |  |  | 0.1 |  |  | 10 | 3428 |  | uint16 |  |  | lvrt_dynamic_kf_factor | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT Switch |  |  | Holding Register | [6 empty] | 3429 |  | uint16 |  |  | hvrt_switch | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xAA: Enabled, 0x55: Disabled
HVRT Voltage 1 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3430 |  | uint16 |  |  | hvrt_voltage_1 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT Voltage 2 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3431 |  | uint16 |  |  | hvrt_voltage_2 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT Voltage 3 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3432 |  | uint16 |  |  | hvrt_voltage_3 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT Voltage 4 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3433 |  | uint16 |  |  | hvrt_voltage_4 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT Voltage 5 |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3434 |  | uint16 |  |  | hvrt_voltage_5 | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Voltage Unbalance Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3440 |  | uint16 |  |  | grid_voltage_unbalance_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Voltage Unbalance Protection Time |  |  | Holding Register | s |  | 0.1 |  |  | 10 | 3441 |  | uint16 |  |  | grid_voltage_unbalance_protection_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Insulation Monitoring Enabling |  |  | Holding Register | [6 empty] | 3442 |  | uint16 |  |  | insulation_monitoring_enabling | [11 empty] | /components/pcs_parameter_setting |  | Yes
Insulation Monitoring Protection Threshold |  |  | Holding Register | kΩ | [5 empty] | 3343 |  | uint16 |  |  | insulation_monitoring_protection_threshold | [11 empty] | /components/pcs_parameter_setting |  | Yes
Insulation Monitoring Measuring Time |  |  | Holding Register | s | [5 empty] | 3344 |  | uint16 |  |  | insulation_monitoring_measuring_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Fault Manual Start |  |  | Holding Register | [6 empty] | 3445 |  | uint16 |  |  | fault_manual_start | [11 empty] | /components/pcs_parameter_setting |  | Yes
Insulation Monitoring Switching Interval |  |  | Holding Register | [6 empty] | 3446 |  | uint16 |  |  | insulation_monitoring_switching_interval | [11 empty] | /components/pcs_parameter_setting |  | Yes
DC Overvoltage Value |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3449 |  | uint16 |  |  | dc_overvoltage_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
DC Undervoltage Value |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3450 |  | uint16 |  |  | dc_undervoltage_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT Dynamic Kf Factor |  |  | Holding Register |  |  | 0.1 |  |  | 10 | 3456 |  | uint16 |  |  | hvrt_dynamic_kf_factor | [11 empty] | /components/pcs_parameter_setting |  | Yes
Insulation Monitoring Alarm Threshold |  |  | Holding Register | kΩ | [5 empty] | 3457 |  | uint16 |  |  | insulation_monitoring_alarm_threshold | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-1 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3462 |  | uint16 |  |  | grid_overvoltage_level_1_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-2 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3463 |  | uint16 |  |  | grid_overvoltage_level_2_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-3 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3464 |  | uint16 |  |  | grid_overvoltage_level_3_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-4 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3465 |  | uint16 |  |  | grid_overvoltage_level_4_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-5 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3466 |  | uint16 |  |  | grid_overvoltage_level_5_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Recovery Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3472 |  | uint16 |  |  | grid_overvoltage_recovery_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-1 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3473 |  | uint16 |  |  | grid_undervoltage_level_1_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-2 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3474 |  | uint16 |  |  | grid_undervoltage_level_2_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-3 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3475 |  | uint16 |  |  | grid_undervoltage_level_3_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-4 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3476 |  | uint16 |  |  | grid_undervoltage_level_4_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-5 Protection Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3477 |  | uint16 |  |  | grid_undervoltage_level_5_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Recovery Value |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3483 |  | uint16 |  |  | grid_undervoltage_recovery_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-1 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3484 |  | uint16 |  |  | grid_overfrequency_level_1_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-2 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3485 |  | uint16 |  |  | grid_overfrequency_level_2_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-3 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3486 |  | uint16 |  |  | grid_overfrequency_level_3_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-4 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3487 |  | uint16 |  |  | grid_overfrequency_level_4_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-5 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3488 |  | uint16 |  |  | grid_overfrequency_level_5_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Recovery Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3499 |  | uint16 |  |  | grid_overfrequency_recovery_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-1 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3501 |  | uint16 |  |  | grid_underfrequency_level_1_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-2 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3502 |  | uint16 |  |  | grid_underfrequency_level_2_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-3 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3503 |  | uint16 |  |  | grid_underfrequency_level_3_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-4 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3504 |  | uint16 |  |  | grid_underfrequency_level_4_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-5 Protection Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3505 |  | uint16 |  |  | grid_underfrequency_level_5_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Recovery Value |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3516 |  | uint16 |  |  | grid_underfrequency_recovery_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
Black Start Enabling |  |  | Holding Register | [6 empty] | 3520 |  | uint16 |  |  | black_start_enabling | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Black Start Beat |  |  | Holding Register | [6 empty] | 3521 |  | uint16 |  |  | black_start_beat | [11 empty] | /components/pcs_parameter_setting |  | Yes
Overfrequency Derating Start Point |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3522 |  | uint16 |  |  | overfrequency_derate_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
Underfrequency Rising Start Point |  |  | Holding Register | Hz |  | 0.01 |  |  | 100 | 3523 |  | uint16 |  |  | underfrequency_rising_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
Frequency Rising Slope |  |  | Holding Register | %Pn/Hz |  | 0.1 |  |  | 10 | 3524 |  | uint16 |  |  | frequency_rising_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
Frequency Derating Slope |  |  | Holding Register | %Pn/Hz |  | 0.1 |  |  | 10 | 3525 |  | uint16 |  |  | frequency_derating_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
PU Characteristic Enabling |  |  | Holding Register | [6 empty] | 3526 |  | uint16 |  |  | pu_characteristic_enabling | [11 empty] | /components/pcs_parameter_setting |  | Yes
PU Voltage Rising Start Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3527 |  | uint16 |  |  | pu_voltage_rising_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
PU Voltage Rising End Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3528 |  | uint16 |  |  | pu_voltage_rising_end_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
PU Voltage Droop Start Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3529 |  | uint16 |  |  | pu_voltage_droop_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
PU Voltage Droop End Point |  |  | Holding Register | % |  | 0.1 |  |  | 10 | 3530 |  | uint16 |  |  | pu_voltage_droop_end_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QP Power Rising Start Point |  |  | Holding Register |  |  | 0.001 |  |  | 1000 | 3531 |  | int16 |  |  | qp_power_rising_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QP Power Rising End Point |  |  | Holding Register |  |  | 0.001 |  |  | 1000 | 3532 |  | int16 |  |  | qp_power_rising_end_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QP Power Droop Start Point |  |  | Holding Register |  |  | 0.001 |  |  | 1000 | 3533 |  | int16 |  |  | qp_power_droop_start_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
QP Power Droop End Point |  |  | Holding Register |  |  | 0.001 |  |  | 1000 | 3534 |  | int16 |  |  | qp_power_droop_end_point | [11 empty] | /components/pcs_parameter_setting |  | Yes
Max QP PF |  |  | Holding Register |  |  | 0.001 |  |  | 1000 | 3535 |  | uint16 |  |  | max_qp_pf | [11 empty] | /components/pcs_parameter_setting |  | Yes
Off-grid Output Slope |  |  | Holding Register | %/s |  | 0.1 |  |  | 10 | 3536 |  | uint16 |  |  | off_grid_output_slope | [11 empty] | /components/pcs_parameter_setting |  | Yes
Zero-export Mode |  |  | Holding Register | [6 empty] | 3537 |  | uint16 |  |  | zero_export_mode | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
DC Overcurrent Protection Value |  |  | Holding Register | A | [5 empty] | 3538 |  | uint16 |  |  | dc_overcurrent_protection_value | [11 empty] | /components/pcs_parameter_setting |  | Yes
DC Overcurrent Tripping Time |  |  | Holding Register | ms |  | 0.02 |  |  | 50 | 3539 |  | uint16 |  |  | dc_overcurrent_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Parallel Role |  |  | Holding Register | [6 empty] | 3540 |  | uint16 |  |  | parallel_role | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0xAA: Master, 0x55: Slave
PCC Reference Voltage |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3542 |  | uint16 |  |  | pcc_reference_voltage | [11 empty] | /components/pcs_parameter_setting |  | Yes
AC Voltage Compensation |  |  | Holding Register | V |  | 0.1 |  |  | 10 | 3543 |  | int16 |  |  | ac_voltage_compensation | [11 empty] | /components/pcs_parameter_setting |  | Yes
Parallel Address |  |  | Holding Register | [6 empty] | 3544 |  | uint16 |  |  | parallel_address | [11 empty] | /components/pcs_parameter_setting |  | Yes
Primary Frequency Modulation Control |  |  | Holding Register | [6 empty] | 3545 |  | uint16 |  |  | primary_frequency_modulation_ctrl | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
LVRT T1 |  |  | Holding Register | ms | 2 |  |  |  |  | 3546 |  | uint32 |  |  | lvrt_t1 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT T2 |  |  | Holding Register | ms | 2 |  |  |  |  | 3548 |  | uint32 |  |  | lvrt_t2 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT T3 |  |  | Holding Register | ms | 2 |  |  |  |  | 3550 |  | uint32 |  |  | lvrt_t3 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT T4 |  |  | Holding Register | ms | 2 |  |  |  |  | 3552 |  | uint32 |  |  | lvrt_t4 | [11 empty] | /components/pcs_parameter_setting |  | Yes
LVRT T5 |  |  | Holding Register | ms | 2 |  |  |  |  | 3554 |  | uint32 |  |  | lvrt_t5 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT T1 |  |  | Holding Register | ms | 2 |  |  |  |  | 3556 |  | uint32 |  |  | hvrt_1 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT T2 |  |  | Holding Register | ms | 2 |  |  |  |  | 3558 |  | uint32 |  |  | hvrt_2 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT T3 |  |  | Holding Register | ms | 2 |  |  |  |  | 3560 |  | uint32 |  |  | hvrt_3 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT T4 |  |  | Holding Register | ms | 2 |  |  |  |  | 3562 |  | uint32 |  |  | hvrt_4 | [11 empty] | /components/pcs_parameter_setting |  | Yes
HVRT T5 |  |  | Holding Register | ms | 2 |  |  |  |  | 3564 |  | uint32 |  |  | hvrt_5 | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-1 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3566 |  | uint32 |  |  | grid_overvoltage_level_1_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-2 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3568 |  | uint32 |  |  | grid_overvoltage_level_2_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-3 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3570 |  | uint32 |  |  | grid_overvoltage_level_3_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-4 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3572 |  | uint32 |  |  | grid_overvoltage_level_4_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overvoltage Level-5 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3574 |  | uint32 |  |  | grid_overvoltage_level_5_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-1 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3576 |  | uint32 |  |  | grid_undervoltage_level_1_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-2 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3578 |  | uint32 |  |  | grid_undervoltage_level_2_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-3 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3580 |  | uint32 |  |  | grid_undervoltage_level_3_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-4 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3582 |  | uint32 |  |  | grid_undervoltage_level_4_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Undervoltage Level-5 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3584 |  | uint32 |  |  | grid_undervoltage_level_5_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-1 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3586 |  | uint32 |  |  | grid_overfrequency_level_1_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-2 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3588 |  | uint32 |  |  | grid_overfrequency_level_2_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-3 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3590 |  | uint32 |  |  | grid_overfrequency_level_3_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-4 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3592 |  | uint32 |  |  | grid_overfrequency_level_4_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Overfrequency Level-5 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3594 |  | uint32 |  |  | grid_overfrequency_level_5_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-1 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3596 |  | uint32 |  |  | grid_underfrequency_level_1_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-2 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3598 |  | uint32 |  |  | grid_underfrequency_level_2_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-3 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3600 |  | uint32 |  |  | grid_underfrequency_level_3_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-4 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3602 |  | uint32 |  |  | grid_underfrequency_level_4_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Underfrequency Level-5 Tripping Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3604 |  | uint32 |  |  | grid_underfrequency_level_5_tripping_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Grid Recovery Time |  |  | Holding Register | ms | 2 | 0.02 |  |  | 50 | 3606 |  | uint32 |  |  | grid_recovery_time | [11 empty] | /components/pcs_parameter_setting |  | Yes
Parallel Operation Control |  |  | Holding Register | [6 empty] | 3608 |  | uint16 |  |  | parallel_operation_ctrl | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Weak Grid Mode |  |  | Holding Register | [6 empty] | 3609 |  | uint16 |  |  | weak_grid_mode | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Reactive Power Soft Start |  |  | Holding Register | [6 empty] | 3610 |  | uint16 |  |  | reactive_power_soft_start | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
HV Load Switch Remote Open |  |  | Holding Register | [6 empty] | 3611 |  | uint16 |  |  | hv_load_switch_remote_open | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
HV Load Switch Remote Closed |  |  | Holding Register | [6 empty] | 3612 |  | uint16 |  |  | hv_load_switch_remote_closed | [11 empty] | /components/pcs_parameter_setting |  | Yes | 0: Disabled, 1: Enabled
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A6: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A15: Tony Olivo: Do not add rows below this line, the script will break
Note on A16: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B16: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D16: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E16: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F16: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G16: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H16: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J16: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on L16: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on M16: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on N16: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on O16: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on P16: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Z16: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AA16: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AB16: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AC16: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AD16: Tony Olivo: Yes/No whether to include in the client/server config
Note on AE16: Tony Olivo: For humans
Note on AF16: Tony Olivo: For humans
Note on AG16: Tony Olivo: Ranges are for humans only