## Sheet3
Connection Name | CATL BMU
Device Name | CATL BMU
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device ID String | catl_BMU
ip_address | 192.168.112.10
port | 502
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical) | [23 empty] | OPTIONAL for web_ui configs only |  | required for modbus server configs only
Name | Type | Ref | Register Type | Unit | Words | Bus Scale | FIMS Scale | hexAddress | Scale | Address | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
MBMU Warnings | [14 empty] | catl_bms_info | TRUE | heartbeat |  | 200 | 200 | 1000 | 20 | 1
System warning (with degrees) Detailed in appendix Ⅰ |  |  | Input Register |  | 1 |  |  | 0000 |  | 0 | enum |  |  | mbmu_warning_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Register address Data quantity Description Comment
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Input Register |  | 3 |  |  | 0001 |  | 1 | enum |  |  | mbmu_warning_21 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Input Register |  | 3 |  |  | 0002 |  | 2 | enum |  |  | mbmu_warning_22 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System status |  |  | Input Register |  |  |  |  | 0010 |  | 16 | enum |  |  | mbmu_status | [11 empty] | /components/catl_mbmu_info |  | Yes | 000 Initialize; 001 Normal; 010 Full charge; 011 Full discharge; 100 Warning status; 101 Fault status
System voltage |  |  | Input Register |  | 1 |  |  | 0020 |  | 32 | uint16 |  |  | mbmu_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
System Current |  |  | Input Register |  | 1 |  |  | 0021 |  | 33 | uint16 |  |  | mbmu_current | [11 empty] | /components/catl_mbmu_info |  | Yes
SOC |  |  | Input Register |  | 1 |  |  | 0022 |  | 34 | uint16 |  |  | mbmu_soc | [11 empty] | /components/catl_mbmu_info |  | Yes
SOH |  |  | Input Register |  | 1 |  |  | 0023 |  | 35 | uint16 |  |  | mbmu_soh | [11 empty] | /components/catl_mbmu_info |  | Yes
Max cell voltage |  |  | Input Register |  | 1 |  |  | 0024 |  | 36 | int16 |  |  | mbmu_max_cell_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
Min cell voltage |  |  | Input Register |  | 1 |  |  | 0025 |  | 37 | int16 |  |  | mbmu_min_cell_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
Avg. cell voltage |  |  | Input Register |  | 1 |  |  | 0026 |  | 38 | int16 |  |  | mbmu_avg_cell_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
Max cell temperature |  |  | Input Register |  | 1 |  |  | 0027 |  | 39 | uint16 |  |  | mbmu_max_cell_temperature | [11 empty] | /components/catl_mbmu_info |  | Yes
Min cell temperature |  |  | Input Register |  | 1 |  |  | 0028 |  | 40 | uint16 |  |  | mbmu_min_cell_temperature | [11 empty] | /components/catl_mbmu_info |  | Yes
Avg. cell temperature |  |  | Input Register |  | 1 |  |  | 0029 |  | 41 | uint16 |  |  | mbmu_avg_cell_temperature | [11 empty] | /components/catl_mbmu_info |  | Yes
Max charge current allowed |  |  | Input Register |  | 1 |  |  | 002a |  | 42 | uint16 |  |  | mbmu_max_charge_current | [11 empty] | /components/catl_mbmu_info |  | Yes
Max discharge current allowed |  |  | Input Register |  | 1 |  |  | 002b |  | 43 | uint16 |  |  | mbmu_max_discharge_current | [11 empty] | /components/catl_mbmu_info |  | Yes
MBMU Liquid Cooling Messages (read) | [14 empty] | catl_bms_info | TRUE | heartbeat |  | 200 | 200 | 1000 | 20 | 1
TMS mode command by BMS 1-1 |  |  | Input Register |  | 1 |  |  | 60 |  | 96 | enum |  |  | mbmu_tms_mode_command_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 1-1 |  |  | Input Register |  | 1 |  |  | 61 |  | 97 | uint16 |  |  | mbmu_tms_temp_setting_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 1-1 |  |  | Input Register |  | 1 |  |  | 62 |  | 98 | enum |  |  | mbmu_tms_real_mode_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 1-1 |  |  | Input Register |  | 1 |  |  | 63 |  | 99 | uint16 |  |  | mbmu_rack_inlet_temperature_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 1-1 |  |  | Input Register |  | 1 |  |  | 64 |  | 100 | uint16 |  |  | mbmu_rack_outlet_temperature_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 1-1 |  |  | Input Register |  | 1 |  |  | 65 |  | 101 | uint16 |  |  | mbmu_ambient_temp_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 1-1 |  |  | Input Register |  | 1 |  |  | 66 |  | 102 | uint16 |  |  | mbmu_tms_fault_code_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 1-1 |  |  | Input Register |  | 1 |  |  | 67 |  | 103 | enum |  |  | mbmu_tms_fault_level_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS communication fault 1-1 |  |  | Input Register |  | 1 |  |  | 68 |  | 104 | enum |  |  | mbmu_tms_communication_fault_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode conflict 1-1 |  |  | Input Register |  | 1 |  |  | 69 |  | 105 | enum |  |  | mbmu_tms_mode_conflict_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS Make BMS Stop 1-1 |  |  | Input Register |  | 1 |  |  | 006a |  | 106 | enum |  |  | mbmu_tms_make_bms_stop_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode command by BMS 2-1 |  |  | Input Register |  | 1 |  |  | 006b |  | 107 | enum |  |  | mbmu_tms_mode_command_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 2-1 |  |  | Input Register |  | 1 |  |  | 006c |  | 108 | uint16 |  |  | mbmu_tms_temp_setting_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 2-1 |  |  | Input Register |  | 1 |  |  | 006d |  | 109 | enum |  |  | mbmu_tms_real_mode_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 2-1 |  |  | Input Register |  | 1 |  |  | 006e |  | 110 | uint16 |  |  | mbmu_rack_inlet_temperature_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 2-1 |  |  | Input Register |  | 1 |  |  | 006f |  | 111 | uint16 |  |  | mbmu_rack_outlet_temperature_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 2-1 |  |  | Input Register |  | 1 |  |  | 70 |  | 112 | uint16 |  |  | mbmu_ambient_temp_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 2-1 |  |  | Input Register |  | 1 |  |  | 71 |  | 113 | uint16 |  |  | mbmu_tms_fault_code_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 2-1 |  |  | Input Register |  | 1 |  |  | 72 |  | 114 | enum |  |  | mbmu_tms_fault_level_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS communication fault 2-1 |  |  | Input Register |  | 1 |  |  | 73 |  | 115 | enum |  |  | mbmu_tms_communication_fault_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode conflict 2-1 |  |  | Input Register |  | 1 |  |  | 74 |  | 116 | enum |  |  | mbmu_tms_mode_conflict_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS Make BMS Stop 2-1 |  |  | Input Register |  | 1 |  |  | 75 |  | 117 | enum |  |  | mbmu_tms_make_bms_stop_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode command by BMS 1-2 |  |  | Input Register |  | 1 |  |  | 76 |  | 118 | enum |  |  | mbmu_tms_mode_command_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 1-2 |  |  | Input Register |  | 1 |  |  | 77 |  | 119 | uint16 |  |  | mbmu_tms_temp_setting_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 1-2 |  |  | Input Register |  | 1 |  |  | 78 |  | 120 | enum |  |  | mbmu_tms_real_mode_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 1-2 |  |  | Input Register |  | 1 |  |  | 79 |  | 121 | uint16 |  |  | mbmu_rack_inlet_temperature_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 1-2 |  |  | Input Register |  | 1 |  |  | 007a |  | 122 | uint16 |  |  | mbmu_rack_outlet_temperature_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 1-2 |  |  | Input Register |  | 1 |  |  | 007b |  | 123 | uint16 |  |  | mbmu_ambient_temp_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 1-2 |  |  | Input Register |  | 1 |  |  | 007c |  | 124 | uint16 |  |  | mbmu_tms_fault_code_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 1-2 |  |  | Input Register |  | 1 |  |  | 007d |  | 125 | enum |  |  | mbmu_tms_fault_level_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS communication fault 1-2 |  |  | Input Register |  | 1 |  |  | 007e |  | 126 | enum |  |  | mbmu_tms_communication_fault_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode conflict 1-2 |  |  | Input Register |  | 1 |  |  | 007f |  | 127 | enum |  |  | mbmu_tms_mode_conflict_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS Make BMS Stop 1-2 |  |  | Input Register |  | 1 |  |  | 0080 |  | 128 | enum |  |  | mbmu_tms_make_bms_stop_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode command by BMS 2-2 |  |  | Input Register |  | 1 |  |  | 81 |  | 129 | enum |  |  | mbmu_tms_mode_command_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 2-2 |  |  | Input Register |  | 1 |  |  | 0082 |  | 130 | uint16 |  |  | mbmu_tms_temp_setting_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 2-2 |  |  | Input Register |  | 1 |  |  | 83 |  | 131 | enum |  |  | mbmu_tms_real_mode_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 2-2 |  |  | Input Register |  | 1 |  |  | 0084 |  | 132 | uint16 |  |  | mbmu_rack_inlet_temperature_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 2-2 |  |  | Input Register |  | 1 |  |  | 85 |  | 133 | uint16 |  |  | mbmu_rack_outlet_temperature_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 2-2 |  |  | Input Register |  | 1 |  |  | 0086 |  | 134 | uint16 |  |  | mbmu_ambient_temp_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 2-2 |  |  | Input Register |  | 1 |  |  | 87 |  | 135 | uint16 |  |  | mbmu_tms_fault_code_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 2-2 |  |  | Input Register |  | 1 |  |  | 0088 |  | 136 | enum |  |  | mbmu_tms_fault_level_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS communication fault 2-2 |  |  | Input Register |  | 1 |  |  | 89 |  | 137 | enum |  |  | mbmu_tms_communication_fault_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS mode conflict 2-2 |  |  | Input Register |  | 1 |  |  | 008a |  | 138 | enum |  |  | mbmu_tms_mode_conflict_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
TMS Make BMS Stop 2-2 |  |  | Input Register |  | 1 |  |  | 008b |  | 139 | enum |  |  | mbmu_tms_make_bms_stop_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: fault
BMS to EMS (read) | [14 empty] | catl_bms_info | TRUE | heartbeat |  | 200 | 200 | 1000 | 20 | 1
BMS heartbeat |  |  | Input Register |  | 1 |  |  | 0300 |  | 768 | uint16 |  |  | bms_heartbeat | [11 empty] | /components/catl_mbmu_info |  | Yes | BMS heartbeats 0-255 updated every 1s
BMS_poweron |  |  | Input Register |  | 1 |  |  | 0301 |  | 769 | enum |  |  | bms_poweron | [11 empty] | /components/catl_mbmu_info |  | Yes | BMS high voltage status - 0: Power off ready; 1: Power on ready; 3: Power off fault; 2: Power on fault
BMS_status |  |  | Input Register |  | 1 |  |  | 0302 |  | 770 | enum |  |  | bms_status | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: Initial status; 1: Normal status; 2: Full charge status; 3: Full discharge status; 4: Warning status; 5: Fault status
Number of HV connected subsystem |  |  | Input Register |  | 1 |  |  | 0304 |  | 772 | uint16 |  |  | num_hv_subsystem | [11 empty] | /components/catl_mbmu_info |  | Yes | Number of HV connected subsystem
System remain charge energy |  |  | Input Register |  | 1 |  |  | 0307 |  | 775 | uint16 |  |  | bms_remain_charge_energy | [11 empty] | /components/catl_mbmu_info |  | Yes | Charge remaining energy
System remain discharge energy |  |  | Input Register |  | 1 |  |  | 0308 |  | 776 | uint16 |  |  | bms_remain_discharge_energy | [11 empty] | /components/catl_mbmu_info |  | Yes | Discharge remaining energy
EMS to BMS (read/write) | [14 empty] | catl_bms_controls | TRUE | heartbeat |  | 200 | 200 | 1000 | 20 | 1
EMS heartbeat |  |  | Holding Register |  | 1 |  |  | 0380 |  | 896 | uint16 |  |  | ems_heartbeat | [11 empty] | /components/catl_ems_bms_rw |  | Yes | Pcs heartbeats 0-255 updated every 1s
EMS_cmd |  |  | Holding Register |  | 1 |  |  | 0381 |  | 897 | enum |  |  | ems_cmd | [11 empty] | /components/catl_ems_bms_rw |  | Yes | 0: Initial; 1: Stay Status; 2: Power on cmd; 3: Power off cmd
EMS_status |  |  | Holding Register |  | 1 |  |  | 0382 |  | 898 | enum |  |  | ems_status | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS system status (reserve)
EMS_RTC_year |  |  | Holding Register |  | 1 |  |  | 0384 |  | 900 | uint16 |  |  | ems_rtc_year | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-year
EMS_RTC_month |  |  | Holding Register |  | 1 |  |  | 0385 |  | 901 | uint16 |  |  | ems_rtc_month | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-month
EMS_RTC_date |  |  | Holding Register |  | 1 |  |  | 0386 |  | 902 | uint16 |  |  | ems_rtc_date | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-day
EMS_RTC_hour |  |  | Holding Register |  | 1 |  |  | 0387 |  | 903 | uint16 |  |  | ems_rtc_hour | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-hour
EMS_RTC_minute |  |  | Holding Register |  | 1 |  |  | 0388 |  | 904 | uint16 |  |  | ems_rtc_minute | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-minute
EMS_RTC_second |  |  | Holding Register |  | 1 |  |  | 0389 |  | 905 | uint16 |  |  | ems_rtc_second | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-second
Fault_Clear_cmd |  |  | Holding Register |  | 1 |  |  | 038c |  | 908 | uint16 |  |  | fault_clear_cmd | [11 empty] | /components/catl_ems_bms_rw |  | Yes | Fault clear command
SBMU Info | [14 empty] | catl_bms_info | TRUE | heartbeat |  | 200 | 200 | 1000 | 20 | 1
System warning (with degrees) |  |  | Input Register |  | 1 |  |  | 0400 |  | 1024 | enum |  |  | sbmu_1_warning_1 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅲ
System warning (without degrees) 1 |  |  | Input Register |  | 2 |  |  | 0401 |  | 1025 | enum |  |  | sbmu_1_warning_21 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅳ
System warning (without degrees) 2 |  |  | Input Register |  | 2 |  |  | 0402 |  | 1026 | enum |  |  | sbmu_1_warning_22 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅳ
System warning (without degrees) 3 |  |  | Input Register |  | 2 |  |  | 0403 |  | 1027 | enum |  |  | sbmu_1_warning_23 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅳ
Precharge Relay Status |  |  | Input Register |  | 1 |  |  | 0410 |  | 1040 | enum |  |  | sbmu_1_precharge_status | [11 empty] | /components/catl_rack_info |  | Yes | relay status - 0: Open; 1: Close
Master positive relay status |  |  | Input Register |  | 1 |  |  | 0411 |  | 1041 | enum |  |  | sbmu_1_master_positive | [11 empty] | /components/catl_rack_info |  | Yes | relay status - 0: Open; 1: Close
Master negative relay status |  |  | Input Register |  | 1 |  |  | 0412 |  | 1042 | enum |  |  | sbmu_1_master_negative | [11 empty] | /components/catl_rack_info |  | Yes | relay status - 0: Open; 1: Close
Balance status |  |  | Input Register |  | 1 |  |  | 0414 |  | 1044 | enum |  |  | sbmu_1_balance_status | [11 empty] | /components/catl_rack_info |  | Yes | 0: Not Run; 1: Run
Battery Subsystem Voltage |  |  | Input Register |  | 1 |  |  | 0420 |  | 1056 | uint16 |  |  | sbmu_1_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery subsystem dc outer side voltage
Battery Subsystem Current |  |  | Input Register |  | 1 |  |  | 0422 |  | 1058 | uint16 |  |  | sbmu_1_current | [11 empty] | /components/catl_rack_info |  | Yes | Battery subsystem current charge/discharge current
SOC Battery system |  |  | Input Register |  | 1 |  |  | 0423 |  | 1059 | uint16 |  |  | sbmu_1_soc | [11 empty] | /components/catl_rack_info |  | Yes | current SOC
SOH Battery system |  |  | Input Register |  | 1 |  |  | 0424 |  | 1060 | uint16 |  |  | sbmu_1_soh | [11 empty] | /components/catl_rack_info |  | Yes | current SOH
Max single cell voltage |  |  | Input Register |  | 1 |  |  | 0425 |  | 1061 | uint16 |  |  | sbmu_1_max_cell_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum single cell voltage
Min single cell voltage |  |  | Input Register |  | 1 |  |  | 0426 |  | 1062 | uint16 |  |  | sbmu_1_min_cell_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current minimum single cell voltage
Avg. cell voltage |  |  | Input Register |  | 1 |  |  | 0427 |  | 1063 | uint16 |  |  | sbmu_1_avg_cell_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current average cell voltage
Max single cell temperature |  |  | Input Register |  | 1 |  |  | 0428 |  | 1064 | uint16 |  |  | sbmu_1_max_cell_temp | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum temperature
Min single cell temperature |  |  | Input Register |  | 1 |  |  | 0429 |  | 1065 | uint16 |  |  | sbmu_1_min_cell_temp | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current minimum temperature
Avg. single cell temperature |  |  | Input Register |  | 1 |  |  | 042a |  | 1066 | uint16 |  |  | sbmu_1_avg_cell_temp | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current average temperature
Max allowed charge current |  |  | Input Register |  | 1 |  |  | 042b |  | 1067 | uint16 |  |  | sbmu_1_max_charge_current | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum allowed charge current
Max allowed discharge current |  |  | Input Register |  | 1 |  |  | 042c |  | 1068 | uint16 |  |  | sbmu_1_max_discharge_current | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum allowed discharge current
Max single cell voltage position |  |  | Input Register |  | 1 |  |  | 0430 |  | 1072 | uint16 |  |  | sbmu_1_max_cell_voltage_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Min single cell voltage position |  |  | Input Register |  | 1 |  |  | 0431 |  | 1073 | uint16 |  |  | sbmu_1_min_cell_voltage_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Max single cell temperature position |  |  | Input Register |  | 1 |  |  | 0432 |  | 1074 | uint16 |  |  | sbmu_1_max_cell_temp_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Min single cell temperature position |  |  | Input Register |  | 1 |  |  | 0433 |  | 1075 | uint16 |  |  | sbmu_1_min_cell_temp_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Sum of cell voltage |  |  | Input Register |  | 1 |  |  | 0437 |  | 1079 | uint16 |  |  | sbmu_1_sum_cells | [11 empty] | /components/catl_rack_info |  | Yes | Sum of cell voltage
Door state |  |  | Input Register |  | 1 |  |  | 450 |  | 1104 | enum |  |  | sbmu_1_door_state | [11 empty] | /components/catl_rack_info |  | Yes | 0: Close; 1: Open
Fan state in control box |  |  | Input Register |  | 1 |  |  | 451 |  | 1105 | enum |  |  | sbmu_1_fan_in_boxs | [11 empty] | /components/catl_rack_info |  | Yes | 0: Stop; 1: Run
Detail message-single cell voltage |  |  | Input Register |  | 576 |  |  | 0480 |  | 1152 | uint16 |  |  | sbmu_1_det_single_voltages | [11 empty] | /components/catl_rack_info |  | No | M#CSC cells voltage: (0x480+(M-1) *N) ~ (0x480+M*N-1)
Detail message-single cell temperature |  |  | Input Register |  | 192 |  |  | 06c0 |  | 1728 | uint16 |  |  | sbmu_1_det_single_temperatures | [11 empty] | /components/catl_rack_info |  | No | M#CSC temperatures: (0x6c0+(M-1) *P) ~ (0x6c0+M*P)
Detail message-balance information |  |  | Input Register |  | 48 |  |  | 0780 |  | 1920 | uint16 |  |  | sbmu_1_detail_information | [11 empty] | /components/catl_rack_info |  | No | M# CSC cells balance status: (0x780+(M-1)*ceil(N/16))~ (0x780+M*ceil(N/16) -1)
sbmu_1 |  |  | Input Register |  | 81 |  |  | 800 |  | 2048 | repeat |  | 1024 | sbmu_2 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 0c00 |  | 3072 | repeat |  | 1024 | sbmu_3 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 1000 |  | 4096 | repeat |  | 1024 | sbmu_4 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 1400 |  | 5120 | repeat |  | 1024 | sbmu_5 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 1800 |  | 6144 | repeat |  | 1024 | sbmu_6 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 1c00 |  | 7168 | repeat |  | 1024 | sbmu_7 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 2000 |  | 8192 | repeat |  | 1024 | sbmu_8 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 2400 |  | 9216 | repeat |  | 1024 | sbmu_9 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Input Register |  | 81 |  |  | 2800 |  | 10240 | repeat |  | 1024 | sbmu_10 | [11 empty] | /components/catl_rack_info |  | Yes
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A13: Tony Olivo: Do not add rows below this line, the script will break
Note on A14: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B14: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D14: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E14: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F14: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G14: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H14: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J14: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on K14: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on L14: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on M14: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on N14: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on O14: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Y14: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on Z14: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AA14: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AB14: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AC14: Tony Olivo: Yes/No whether to include in the client/server config
Note on AD14: Tony Olivo: For humans
Note on AE14: Tony Olivo: For humans
Note on AF14: Tony Olivo: Ranges are for humans only

## 04_26_2022
Connection Name | CATL BMU
Device Name | CATL BMU
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device ID String | catl_BMU
ip_address | 192.168.112.10
port | 502
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical) | [23 empty] | OPTIONAL for web_ui configs only |  | required for modbus server configs only
Name | Type | Ref | Register Type | Unit | Words | Bus Scale | FIMS Scale | hexAddress | Scale | Address | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
BMS Controls | [14 empty] | catl_bms_controls | [5 empty] | 1000 | 20 | 1
EMS to BMS (read/write)
EMS heartbeat |  |  | Holding Register |  | 1 |  |  | 0380 |  | 896 | uint16 |  |  | ems_heartbeat | [11 empty] | /components/catl_ems_bms_rw |  | Yes | Pcs heartbeats 0-255 updated every 1s
EMS_cmd |  |  | Holding Register |  | 1 |  |  | 0381 |  | 897 | uint16 |  |  | ems_cmd | [11 empty] | /components/catl_ems_bms_rw |  | Yes | 0: Initial; 1: Stay Status; 2: Power on cmd; 3: Power off cmd
EMS_status |  |  | Holding Register |  | 1 |  |  | 0382 |  | 898 | uint16 |  |  | ems_status | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS system status (reserve)
EMS_RTC_year |  |  | Holding Register |  | 1 |  |  | 0384 |  | 900 | uint16 |  |  | ems_rtc_year | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-year
EMS_RTC_month |  |  | Holding Register |  | 1 |  |  | 0385 |  | 901 | uint16 |  |  | ems_rtc_month | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-month
EMS_RTC_date |  |  | Holding Register |  | 1 |  |  | 0386 |  | 902 | uint16 |  |  | ems_rtc_date | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-day
EMS_RTC_hour |  |  | Holding Register |  | 1 |  |  | 0387 |  | 903 | uint16 |  |  | ems_rtc_hour | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-hour
EMS_RTC_minute |  |  | Holding Register |  | 1 |  |  | 0388 |  | 904 | uint16 |  |  | ems_rtc_minute | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-minute
EMS_RTC_second |  |  | Holding Register |  | 1 |  |  | 0389 |  | 905 | uint16 |  |  | ems_rtc_second | [11 empty] | /components/catl_ems_bms_rw |  | Yes | EMS time-second
EMS_insulation switch control_cmd |  |  | Holding Register |  | 1 |  |  | 038b |  | 907 | uint16 |  |  | ems_insulation_switch_control_cmd | [11 empty] | /components/catl_ems_bms_rw |  | Yes | 0=bms insulation close, 1=bms insulation open
Fault_Clear_cmd |  |  | Holding Register |  | 1 |  |  | 038c |  | 908 | uint16 |  |  | fault_clear_cmd | [11 empty] | /components/catl_ems_bms_rw |  | Yes | Fault clear command
BMS Info (read) | [14 empty] | catl_bms_info | [5 empty] | 1000 | 20 | 1
MBMU Warnings
System warning (with degrees) Detailed in appendix Ⅰ |  |  | Holding Register |  | 1 |  |  | 0000 |  | 0 | uint16 |  |  | mbmu_warning_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Register address Data quantity Description Comment
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Holding Register |  | 1 |  |  | 0001 |  | 1 | uint16 |  |  | mbmu_warning_21 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Holding Register |  | 1 |  |  | 0002 |  | 2 | uint16 |  |  | mbmu_warning_22 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Holding Register |  | 1 |  |  | 0003 |  | 3 | uint16 |  |  | mbmu_warning_23 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Holding Register |  | 1 |  |  | 0004 |  | 4 | uint16 |  |  | mbmu_warning_24 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Holding Register |  | 1 |  |  | 0005 |  | 5 | uint16 |  |  | mbmu_warning_25 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (without degrees) Detailed in appendix Ⅱ |  |  | Holding Register |  | 1 |  |  | 0006 |  | 6 | uint16 |  |  | mbmu_warning_26 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (with degrees) Detailed in appendix Ⅰ |  |  | Holding Register |  | 1 |  |  | 000e |  | 14 | uint16 |  |  | mbmu_warning_12 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System warning (with degrees) Detailed in appendix Ⅰ |  |  | Holding Register |  | 1 |  |  | 000f |  | 15 | uint16 |  |  | mbmu_warning_13 | [11 empty] | /components/catl_mbmu_info |  | Yes | System warning
System status |  |  | Holding Register |  | 1 |  |  | 0010 |  | 16 | uint16 |  |  | mbmu_status | [11 empty] | /components/catl_mbmu_info |  | Yes | 000 Initialize; 001 Normal; 010 Full charge; 011 Full discharge; 100 Warning status; 101 Fault status
System voltage |  |  | Holding Register |  | 1 |  |  | 0020 | 10 | 32 | uint16 |  |  | mbmu_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
System Current |  |  | Holding Register |  | 1 |  |  | 0021 |  | 33 | int16 |  |  | mbmu_current | [11 empty] | /components/catl_mbmu_info |  | Yes
SOC |  |  | Holding Register |  | 1 |  |  | 0022 | 10 | 34 | uint16 |  |  | mbmu_soc | [11 empty] | /components/catl_mbmu_info |  | Yes
SOH |  |  | Holding Register |  | 1 |  |  | 0023 | 10 | 35 | uint16 |  |  | mbmu_soh | [11 empty] | /components/catl_mbmu_info |  | Yes
Max cell voltage |  |  | Holding Register |  | 1 |  |  | 0024 | 1000 | 36 | int16 |  |  | mbmu_max_cell_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
Min cell voltage |  |  | Holding Register |  | 1 |  |  | 0025 | 1000 | 37 | int16 |  |  | mbmu_min_cell_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
Avg. cell voltage |  |  | Holding Register |  | 1 |  |  | 0026 | 1000 | 38 | int16 |  |  | mbmu_avg_cell_voltage | [11 empty] | /components/catl_mbmu_info |  | Yes
Max cell temperature |  |  | Holding Register |  | 1 |  |  | 0027 |  | 39 | uint16 |  |  | mbmu_max_cell_temperature | [11 empty] | /components/catl_mbmu_info |  | Yes
Min cell temperature |  |  | Holding Register |  | 1 |  |  | 0028 |  | 40 | uint16 |  |  | mbmu_min_cell_temperature | [11 empty] | /components/catl_mbmu_info |  | Yes
Avg. cell temperature |  |  | Holding Register |  | 1 |  |  | 0029 |  | 41 | uint16 |  |  | mbmu_avg_cell_temperature | [11 empty] | /components/catl_mbmu_info |  | Yes
Max charge current allowed |  |  | Holding Register |  | 1 |  |  | 002a | -1 | 42 | uint16 |  |  | mbmu_max_charge_current | [11 empty] | /components/catl_mbmu_info |  | Yes
Max discharge current allowed |  |  | Holding Register |  | 1 |  |  | 002b |  | 43 | uint16 |  |  | mbmu_max_discharge_current | [11 empty] | /components/catl_mbmu_info |  | Yes
High voltage command on battery |  |  | Holding Register |  | 1 |  |  | 003a |  | 58 | uint16 |  |  | mbmu_high_voltage_comm_on_battery | [11 empty] | /components/catl_mbmu_info |  | Yes | 1=on the battery, 2=under battery
MBMU software version |  |  | Holding Register |  | 1 |  |  | 100 |  | 256 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 101 |  | 257 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 102 |  | 258 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 103 |  | 259 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 104 |  | 260 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 105 |  | 261 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 106 |  | 262 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 107 |  | 263 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 108 |  | 264 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 109 |  | 265 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 010a |  | 266 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 010b |  | 267 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 010c |  | 268 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 010d |  | 269 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 010e |  | 270 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU software version |  |  | Holding Register |  | 1 |  |  | 010f |  | 271 | uint16 |  |  | mbmu_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 110 |  | 272 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 111 |  | 273 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 112 |  | 274 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 113 |  | 275 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 114 |  | 276 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 115 |  | 277 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 116 |  | 278 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 117 |  | 279 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 118 |  | 280 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 119 |  | 281 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 011a |  | 282 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 011b |  | 283 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 011c |  | 284 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 011d |  | 285 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 011e |  | 286 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU hardware version |  |  | Holding Register |  | 1 |  |  | 011f |  | 287 | uint16 |  |  | mbmu_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 120 |  | 288 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 121 |  | 289 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 122 |  | 290 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 123 |  | 291 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 124 |  | 292 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 125 |  | 293 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 126 |  | 294 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 127 |  | 295 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 128 |  | 296 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 129 |  | 297 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 012a |  | 298 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 012b |  | 299 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 012c |  | 300 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 012d |  | 301 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 012e |  | 302 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH software version |  |  | Holding Register |  | 1 |  |  | 012f |  | 303 | uint16 |  |  | eth_software_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 130 |  | 304 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 131 |  | 305 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 132 |  | 306 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 133 |  | 307 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 134 |  | 308 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 135 |  | 309 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 136 |  | 310 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 137 |  | 311 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 138 |  | 312 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 139 |  | 313 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 013a |  | 314 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 013b |  | 315 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 013c |  | 316 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 013d |  | 317 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 013e |  | 318 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
ETH hardware version |  |  | Holding Register |  | 1 |  |  | 013f |  | 319 | uint16 |  |  | eth_hardware_version | [11 empty] | /components/catl_mbmu_info |  | Yes | show in ASCII
MBMU Liquid Cooling Messages (read)
TMS mode command by BMS 1-1 |  |  | Holding Register |  | 1 |  |  | 60 |  | 96 | uint16 |  |  | mbmu_tms_mode_command_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 1-1 |  |  | Holding Register |  | 1 |  |  | 61 |  | 97 | uint16 |  |  | mbmu_tms_temp_setting_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 1-1 |  |  | Holding Register |  | 1 |  |  | 62 |  | 98 | uint16 |  |  | mbmu_tms_real_mode_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 1-1 |  |  | Holding Register |  | 1 |  |  | 63 |  | 99 | uint16 |  |  | mbmu_rack_inlet_temperature_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 1-1 |  |  | Holding Register |  | 1 |  |  | 64 |  | 100 | uint16 |  |  | mbmu_rack_outlet_temperature_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 1-1 |  |  | Holding Register |  | 1 |  |  | 65 |  | 101 | uint16 |  |  | mbmu_ambient_temp_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 1-1 |  |  | Holding Register |  | 1 |  |  | 66 |  | 102 | uint16 |  |  | mbmu_tms_fault_code_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 1-1 |  |  | Holding Register |  | 1 |  |  | 67 |  | 103 | uint16 |  |  | mbmu_tms_fault_level_1_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS mode command by BMS 2-1 |  |  | Holding Register |  | 1 |  |  | 68 |  | 104 | uint16 |  |  | mbmu_tms_mode_command_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 2-1 |  |  | Holding Register |  | 1 |  |  | 69 |  | 105 | uint16 |  |  | mbmu_tms_temp_setting_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 2-1 |  |  | Holding Register |  | 1 |  |  | 006a |  | 106 | uint16 |  |  | mbmu_tms_real_mode_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 2-1 |  |  | Holding Register |  | 1 |  |  | 006b |  | 107 | uint16 |  |  | mbmu_rack_inlet_temperature_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 2-1 |  |  | Holding Register |  | 1 |  |  | 006c |  | 108 | uint16 |  |  | mbmu_rack_outlet_temperature_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 2-1 |  |  | Holding Register |  | 1 |  |  | 006d |  | 109 | uint16 |  |  | mbmu_ambient_temp_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 2-1 |  |  | Holding Register |  | 1 |  |  | 006e |  | 110 | uint16 |  |  | mbmu_tms_fault_code_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 2-1 |  |  | Holding Register |  | 1 |  |  | 006f |  | 111 | uint16 |  |  | mbmu_tms_fault_level_2_1 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS mode command by BMS 1-2 |  |  | Holding Register |  | 1 |  |  | 70 |  | 112 | uint16 |  |  | mbmu_tms_mode_command_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 1-2 |  |  | Holding Register |  | 1 |  |  | 71 |  | 113 | uint16 |  |  | mbmu_tms_temp_setting_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 1-2 |  |  | Holding Register |  | 1 |  |  | 72 |  | 114 | uint16 |  |  | mbmu_tms_real_mode_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 1-2 |  |  | Holding Register |  | 1 |  |  | 73 |  | 115 | uint16 |  |  | mbmu_rack_inlet_temperature_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 1-2 |  |  | Holding Register |  | 1 |  |  | 74 |  | 116 | uint16 |  |  | mbmu_rack_outlet_temperature_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 1-2 |  |  | Holding Register |  | 1 |  |  | 75 |  | 117 | uint16 |  |  | mbmu_ambient_temp_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 1-2 |  |  | Holding Register |  | 1 |  |  | 76 |  | 118 | uint16 |  |  | mbmu_tms_fault_code_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 1-2 |  |  | Holding Register |  | 1 |  |  | 77 |  | 119 | uint16 |  |  | mbmu_tms_fault_level_1_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
TMS mode command by BMS 2-2 |  |  | Holding Register |  | 1 |  |  | 78 |  | 120 | uint16 |  |  | mbmu_tms_mode_command_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
TMS temperature value set by BMS 2-2 |  |  | Holding Register |  | 1 |  |  | 79 |  | 121 | uint16 |  |  | mbmu_tms_temp_setting_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS temperature value set by BMS
TMS real mode 2-2 |  |  | Holding Register |  | 1 |  |  | 007a |  | 122 | uint16 |  |  | mbmu_tms_real_mode_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: power off; 1: cooling mode; 2: heating mode; 3: self-circulation mode
Rack inlet temperature 2-2 |  |  | Holding Register |  | 1 |  |  | 007b |  | 123 | uint16 |  |  | mbmu_rack_inlet_temperature_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack inlet temperature
Rack outlet temperature 2-2 |  |  | Holding Register |  | 1 |  |  | 007c |  | 124 | uint16 |  |  | mbmu_rack_outlet_temperature_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Rack outlet temperature
TMS Environment temperature 2-2 |  |  | Holding Register |  | 1 |  |  | 007d |  | 125 | uint16 |  |  | mbmu_ambient_temp_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | Environment temperature
TMS fault code 2-2 |  |  | Holding Register |  | 1 |  |  | 007e |  | 126 | uint16 |  |  | mbmu_tms_fault_code_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | TMS fault code
TMS fault level 2-2 |  |  | Holding Register |  | 1 |  |  | 007f |  | 127 | uint16 |  |  | mbmu_tms_fault_level_2_2 | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: normal; 1: tms fault level 1; 2: tms fault level 2; 3: tms fault level 3
BMS to EMS (read)
BMS heartbeat |  |  | Holding Register |  | 1 |  |  | 0300 |  | 768 | uint16 |  |  | bms_heartbeat | [11 empty] | /components/catl_mbmu_info |  | Yes | BMS heartbeats 0-255 updated every 1s
BMS_poweron |  |  | Holding Register |  | 1 |  |  | 0301 |  | 769 | uint16 |  |  | bms_poweron | [11 empty] | /components/catl_mbmu_info |  | Yes | BMS high voltage status - 0: Power off ready; 1: Power on ready; 3: Power off fault; 2: Power on fault
BMS_status |  |  | Holding Register |  | 1 |  |  | 0302 |  | 770 | uint16 |  |  | bms_status | [11 empty] | /components/catl_mbmu_info |  | Yes | 0: Initial status; 1: Normal status; 2: Full charge status; 3: Full discharge status; 4: Warning status; 5: Fault status
Number of HV connected subsystem |  |  | Holding Register |  | 1 |  |  | 0304 |  | 772 | uint16 |  |  | num_hv_subsystem | [11 empty] | /components/catl_mbmu_info |  | Yes | Number of HV connected subsystem
System remain charge energy |  |  | Holding Register |  | 1 |  |  | 0307 | 10 | 775 | uint16 |  |  | bms_remain_charge_energy | [11 empty] | /components/catl_mbmu_info |  | Yes | Charge remaining energy
System remain discharge energy |  |  | Holding Register |  | 1 |  |  | 0308 | 10 | 776 | uint16 |  |  | bms_remain_discharge_energy | [11 empty] | /components/catl_mbmu_info |  | Yes | Discharge remaining energy
System power |  |  | Holding Register |  | 1 |  |  | 313 |  | 787 | uint16 |  |  | bms_system_power | [11 empty] | /components/catl_mbmu_info |  | Yes | System power
SBMU Info
System warning (with degrees) Detailed in appendix III |  |  | Holding Register |  | 1 |  |  | 0400 |  | 1024 | uint16 |  |  | sbmu_1_warning_1 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅲ
System warning (without degrees) 1 Detailed in appendix IV |  |  | Holding Register |  | 1 |  |  | 0401 |  | 1025 | uint16 |  |  | sbmu_1_warning_21 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅳ
System warning (without degrees) 2 Detailed in appendix IV |  |  | Holding Register |  | 1 |  |  | 0402 |  | 1026 | uint16 |  |  | sbmu_1_warning_22 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅳ
System warning (without degrees) 3 Detailed in appendix IV |  |  | Holding Register |  | 1 |  |  | 0403 |  | 1027 | uint16 |  |  | sbmu_1_warning_23 | [11 empty] | /components/catl_rack_info |  | Yes | Details in appendix Ⅳ
Precharge Relay Status |  |  | Holding Register |  | 1 |  |  | 0410 |  | 1040 | uint16 |  |  | sbmu_1_precharge_status | [11 empty] | /components/catl_rack_info |  | Yes | relay status - 0: Open; 1: Close
Master positive relay status |  |  | Holding Register |  | 1 |  |  | 0411 |  | 1041 | uint16 |  |  | sbmu_1_master_positive | [11 empty] | /components/catl_rack_info |  | Yes | relay status - 0: Open; 1: Close
Master negative relay status |  |  | Holding Register |  | 1 |  |  | 0412 |  | 1042 | uint16 |  |  | sbmu_1_master_negative | [11 empty] | /components/catl_rack_info |  | Yes | relay status - 0: Open; 1: Close
Fan status |  |  | Holding Register |  | 1 |  |  | 413 |  | 1043 | uint16 |  |  | sbmu_1_fan_status | [11 empty] | /components/catl_rack_info |  | Yes | 0: not run, 1:run
Balance status |  |  | Holding Register |  | 1 |  |  | 0414 |  | 1044 | uint16 |  |  | sbmu_1_balance_status | [11 empty] | /components/catl_rack_info |  | Yes | 0: Not Run; 1: Run
Battery Subsystem Voltage |  |  | Holding Register |  | 1 |  |  | 0420 | 10 | 1056 | uint16 |  |  | sbmu_1_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery subsystem dc outer side voltage
Battery Subsystem Current |  |  | Holding Register |  | 1 |  |  | 0422 | 10 | 1058 | int16 |  |  | sbmu_1_current | [11 empty] | /components/catl_rack_info |  | Yes | Battery subsystem current charge/discharge current
SOC Battery system |  |  | Holding Register |  | 1 |  |  | 0423 | 10 | 1059 | uint16 |  |  | sbmu_1_soc | [11 empty] | /components/catl_rack_info |  | Yes | current SOC
SOH Battery system |  |  | Holding Register |  | 1 |  |  | 0424 | 10 | 1060 | uint16 |  |  | sbmu_1_soh | [11 empty] | /components/catl_rack_info |  | Yes | current SOH
Max single cell voltage |  |  | Holding Register |  | 1 |  |  | 0425 | 1000 | 1061 | uint16 |  |  | sbmu_1_max_cell_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum single cell voltage
Min single cell voltage |  |  | Holding Register |  | 1 |  |  | 0426 | 1000 | 1062 | uint16 |  |  | sbmu_1_min_cell_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current minimum single cell voltage
Avg. cell voltage |  |  | Holding Register |  | 1 |  |  | 0427 | 1000 | 1063 | uint16 |  |  | sbmu_1_avg_cell_voltage | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current average cell voltage
Max single cell temperature |  |  | Holding Register |  | 1 |  |  | 0428 |  | 1064 | uint16 |  |  | sbmu_1_max_cell_temp | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum temperature
Min single cell temperature |  |  | Holding Register |  | 1 |  |  | 0429 |  | 1065 | uint16 |  |  | sbmu_1_min_cell_temp | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current minimum temperature
Avg. single cell temperature |  |  | Holding Register |  | 1 |  |  | 042a |  | 1066 | uint16 |  |  | sbmu_1_avg_cell_temp | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current average temperature
Max allowed charge current |  |  | Holding Register |  | 1 |  |  | 042b | -10 | 1067 | uint16 |  |  | sbmu_1_max_charge_current | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum allowed charge current
Max allowed discharge current |  |  | Holding Register |  | 1 |  |  | 042c | 10 | 1068 | uint16 |  |  | sbmu_1_max_discharge_current | [11 empty] | /components/catl_rack_info |  | Yes | Battery system current maximum allowed discharge current
Max single cell voltage position |  |  | Holding Register |  | 1 |  |  | 0430 |  | 1072 | uint16 |  |  | sbmu_1_max_cell_voltage_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Min single cell voltage position |  |  | Holding Register |  | 1 |  |  | 0431 |  | 1073 | uint16 |  |  | sbmu_1_min_cell_voltage_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Max single cell temperature position |  |  | Holding Register |  | 1 |  |  | 0432 |  | 1074 | uint16 |  |  | sbmu_1_max_cell_temp_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Min single cell temperature position |  |  | Holding Register |  | 1 |  |  | 0433 |  | 1075 | uint16 |  |  | sbmu_1_min_cell_temp_position | [11 empty] | /components/catl_rack_info |  | Yes | Low byte: cell number; high byte: tank number
Sum of cell voltage |  |  | Holding Register |  | 1 |  |  | 0437 |  | 1079 | uint16 |  |  | sbmu_1_sum_cells | [11 empty] | /components/catl_rack_info |  | Yes | Sum of cell voltage
Door state |  |  | Holding Register |  | 1 |  |  | 450 |  | 1104 | uint16 |  |  | sbmu_1_door_state | [11 empty] | /components/catl_rack_info |  | Yes | 0: Close; 1: Open
Fan state in control box |  |  | Holding Register |  | 1 |  |  | 451 |  | 1105 | uint16 |  |  | sbmu_1_fan_in_boxs | [11 empty] | /components/catl_rack_info |  | Yes | 0: Stop; 1: Run
Historical accumulated charging energy |  |  | Holding Register |  | 2 |  |  | 454 |  | 1108 | uint16 |  |  | sbmu_1_historical_accumulated_charg_energy | [11 empty] | /components/catl_rack_info |  | Yes
Historical accumulated charging energy |  |  | Holding Register |  | 2 |  |  | 455 |  | 1109 | uint16 |  |  | sbmu_1_historical_accumulated_charg_energy | [11 empty] | /components/catl_rack_info |  | Yes
Historical cumulative discharge energy |  |  | Holding Register |  | 2 |  |  | 456 |  | 1110 | uint16 |  |  | sbmu_1_historical_cumulative_discharg_energy | [11 empty] | /components/catl_rack_info |  | Yes
Historical cumulative discharge energy |  |  | Holding Register |  | 2 |  |  | 457 |  | 1111 | uint16 |  |  | sbmu_1_historical_cumulative_discharg_energy | [11 empty] | /components/catl_rack_info |  | Yes
Detail message-single cell voltage |  |  | Holding Register |  | 576 |  |  | 0480 |  | 1152 | uint16 |  |  | sbmu_1_det_single_voltages | [11 empty] | /components/catl_rack_info |  | No | M#CSC cells voltage: (0x480+(M-1) *N) ~ (0x480+M*N-1)
Detail message-single cell temperature |  |  | Holding Register |  | 192 |  |  | 06c0 |  | 1728 | uint16 |  |  | sbmu_1_det_single_temperatures | [11 empty] | /components/catl_rack_info |  | No | M#CSC temperatures: (0x6c0+(M-1) *P) ~ (0x6c0+M*P)
Detail message-balance information |  |  | Holding Register |  | 48 |  |  | 0780 |  | 1920 | uint16 |  |  | sbmu_1_detail_information | [11 empty] | /components/catl_rack_info |  | No | M# CSC cells balance status: (0x780+(M-1)*ceil(N/16))~ (0x780+M*ceil(N/16) -1)
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 800 |  | 2048 | repeat |  | 1024 | sbmu_2 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 0c00 |  | 3072 | repeat |  | 1024 | sbmu_3 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 1000 |  | 4096 | repeat |  | 1024 | sbmu_4 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 1400 |  | 5120 | repeat |  | 1024 | sbmu_5 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 1800 |  | 6144 | repeat |  | 1024 | sbmu_6 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 1c00 |  | 7168 | repeat |  | 1024 | sbmu_7 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 2000 |  | 8192 | repeat |  | 1024 | sbmu_8 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 2400 |  | 9216 | repeat |  | 1024 | sbmu_9 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 2800 |  | 10240 | repeat |  | 1024 | sbmu_10 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 2C00 |  | 11264 | repeat |  | 1024 | sbmu_11 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 3000 |  | 12288 | repeat |  | 1024 | sbmu_12 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 3400 |  | 13312 | repeat |  | 1024 | sbmu_13 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 3800 |  | 14336 | repeat |  | 1024 | sbmu_14 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 3C00 |  | 15360 | repeat |  | 1024 | sbmu_15 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 4000 |  | 16384 | repeat |  | 1024 | sbmu_16 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 4400 |  | 17408 | repeat |  | 1024 | sbmu_17 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 4800 |  | 18432 | repeat |  | 1024 | sbmu_18 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 4C00 |  | 19456 | repeat |  | 1024 | sbmu_19 | [11 empty] | /components/catl_rack_info |  | Yes
sbmu_1 |  |  | Holding Register |  | 81 |  |  | 5000 |  | 20480 | repeat |  | 1024 | sbmu_20 | [11 empty] | /components/catl_rack_info |  | Yes
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A13: Tony Olivo: Do not add rows below this line, the script will break
Note on A14: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B14: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D14: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E14: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F14: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G14: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H14: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J14: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on K14: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on L14: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on M14: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on N14: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on O14: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Y14: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on Z14: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AA14: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AB14: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AC14: Tony Olivo: Yes/No whether to include in the client/server config
Note on AD14: Tony Olivo: For humans
Note on AE14: Tony Olivo: For humans
Note on AF14: Tony Olivo: Ranges are for humans only