## HEMSW01L1
Connection Name | PCMS
Connection Name | PCMS
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device Name | pe_pcs_1
Device ID String | pe_pcs_1
ip_address | 192.168.112.13
Device Port (502 typical)
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address | Address Original | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
Remote Control Functions | [15 empty] | pcs_controls | [5 empty] | 200 | 0 | 98
Start | Control | G0.1 | Holding Register |  | 1 |  |  |  |  | 3009 | 43010 | uint16 |  |  | start | [9 empty] | enum | 1 = Start | /components/pcs_controls | pcs_start | Yes | G0: Remote Control
Stop | Control | G0.2 | Holding Register |  | 1 |  |  |  |  | 3010 | 43011 | uint16 |  |  | stop | [10 empty] | 1 = Stop | /components/pcs_controls | pcs_stop | Yes
Reset | Control | G0.3 | Holding Register |  | 1 |  |  |  |  | 3011 | 43012 | uint16 |  |  | reset | [10 empty] | 1 = Reset | /components/pcs_controls | pcs_reset | Yes
E-Stop | Control | G0.4 | Holding Register |  | 1 |  |  |  |  | 3199 | 43200 | uint16 |  |  | e_stop | [10 empty] | 1 = Estop | /components/pcs_controls | pcs_e_stop | Yes
General | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
Access Code | Control | G1.2 | Input Register |  | 1 |  |  |  |  | 2 | 40003 | uint16 |  |  | access | [11 empty] | /components/pcs_controls | pcs_access | Yes | G1: General
User | Control | G1.3 | Input Register |  | 1 |  |  |  |  | 3 | 40004 | uint16 |  |  | user | [11 empty] | /components/pcs_controls | pcs_user | Yes
User Password | Control | G1.4 | Holding Register |  | 1 |  |  |  |  | 4 | 40005 | uint16 |  |  | user_pw | [11 empty] | /components/pcs_controls | pcs_user_pw | Yes
seconds | Control | G1.5.1 | Holding Register | Sec | 1 |  |  |  |  | 5 | 40006 | uint16 |  |  | seconds | [11 empty] | /components/pcs_controls | pcs_seconds | Yes
Minutes | Control | G1.5.2 | Holding Register | Min | 1 |  |  |  |  | 6 | 40007 | uint16 |  |  | minutes | [11 empty] | /components/pcs_controls | pcs_minutes | Yes
Hours | Control | G1.5.3 | Holding Register | Hrs | 1 |  |  |  |  | 7 | 40008 | uint16 |  |  | hours | [11 empty] | /components/pcs_controls | pcs_hours | Yes
Day | Control | G1.5.4 | Holding Register | Day | 1 |  |  |  |  | 8 | 40009 | uint16 |  |  | day | [11 empty] | /components/pcs_controls | pcs_day | Yes
Month | Control | G1.5.5 | Holding Register | Month | 1 |  |  |  |  | 9 | 40010 | uint16 |  |  | month | [11 empty] | /components/pcs_controls | pcs_month | Yes
Year | Control | G1.5.6 | Holding Register | Year | 1 |  |  |  |  | 10 | 40011 | uint16 |  |  | year | [11 empty] | /components/pcs_controls | pcs_year | Yes
UTC offset | Control | G1.6 | Holding Register | UTC | 1 |  |  |  |  | 11 | 40012 | int16 |  |  | utc | [11 empty] | /components/pcs_controls | pcs_utc | Yes | -720 to 840
Running Conditions | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
Vdc Low | Control | G2.1.1 | Holding Register | V | 1 |  |  |  |  | 30 | 40031 | uint16 |  |  | vdc_low | [11 empty] | /components/pcs_controls | pcs_vdc_low | Yes | G2: Running conditions. 0 to 1500 Volts
Vac Low | Control | G2.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 31 | 40032 | uint16 |  |  | vac_low | [11 empty] | /components/pcs_controls | pcs_vac_low | Yes | 80.0 to 100.0
Vac High | Control | G2.1.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 32 | 40033 | uint16 |  |  | vac_high | [11 empty] | /components/pcs_controls | pcs_vac_high | Yes | 100.0 to 120
Start Delay | Control | G2.1.6 | Holding Register | Sec | 1 |  |  |  |  | 35 | 40036 | uint16 |  |  | start_delay | [11 empty] | /components/pcs_controls | pcs_start_delay | Yes | 0 to 600 Seconds
Limits | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
P Limit | Control | G3.1.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 100 | 40101 | uint16 |  |  | p_limit | [11 empty] | /components/pcs_controls | pcs_p_limit | Yes | G3: Limits. 100 = 10000
Q Limit | Control | G3.1.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 101 | 40102 | uint16 |  |  | q_limit | [11 empty] | /components/pcs_controls | pcs_q_limit | Yes | 0 to 150 % 100=10000
P / Q Priority | Control | G3.1.3 | Holding Register |  | 1 |  |  |  |  | 102 | 40103 | uint16 |  |  | p_q_priority | [9 empty] | enum | 0=P, 1= Q | /components/pcs_controls | pcs_p_q_priority | Yes
S limit | Control | G3.1.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 103 | 40104 | unt16 |  |  | s_limit | [11 empty] | /components/pcs_controls | pcs_s_limit | Yes | 0-200% 0, to 20000
P algorithm priority | Control | G3.1.5 | Holding Register |  | 1 |  |  |  |  | 104 | 40105 | uint16 |  |  | p_algo_pri | [9 empty] | enum | 0=min, 1=P(f) priority, 2=P(v)piority | /components/pcs_controls | pcs_p_algo_pri | Yes
Gradients | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
LVRT Reference | Control | G4.2.1.8 | Holding Register | % | 1 |  |  |  |  | 192 | 40193 | uint16 |  |  | lvrt_ref | [11 empty] | /components/pcs_controls | pcs_lvrt_ref | Yes | G4: Algorithms
OVRT Reference | Control | G4.3.1.8 | Holding Register | % | 1 |  |  |  |  | 193 | 40194 | uint16 |  |  | ovrt_ref | [11 empty] | /components/pcs_controls | pcs_ovrt_ref | Yes
Night Mode Enable | Control | G4.7.1 | Holding Register |  | 1 |  |  |  |  | 260 | 40261 | uint16 |  |  | night_mode_enable | [9 empty] | enum | 0=No, 1=Yes | /components/pcs_controls | pcs_night_mode_enable | Yes
Night Mode Q ref | Control | G4.7.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 261 | 40262 | int16 |  |  | night_mode_q_ref | [11 empty] | /components/pcs_controls | pcs_night_mode_q_ref | Yes | -100 to 100 ,100 = 10000
Night Mode Vbus Ref | Control | G4.7.3 | Holding Register | V | 1 | 1 |  |  | 1 | 262 | 40263 | uint16 |  |  | night_mode_vbus_ref | [11 empty] | /components/pcs_controls | pcs_night_mode_vbus_ref | Yes | 961 to 1250
Night Mode Activate | Control | G4.7.4 | Holding Register |  | 1 |  |  |  |  | 263 | 40264 | uint16 |  |  | night_mode_activate | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_night_mode_activate | Yes
P Start Gradient Enable | Control | G4.8.1.1 | Holding Register |  | 1 |  |  |  |  | 276 | 40277 | uint16 |  |  | start_grad_p_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_start_grad_p_enable | Yes
P Start Gradient | Control | G4.8.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 277 | 40278 | uint16 |  |  | start_grad_p | [11 empty] | /components/pcs_controls | pcs_start_grad_p | Yes | 0.1 to 30000.0 % , 0 to 30000
Q Start Gradient Enable | Control | G4.8.1.3 | Holding Register |  | 1 |  |  |  |  | 278 | 40279 | uint16 |  |  | start_grad_q_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_start_grad_q_enable | Yes
Q Start Gradient | Control | G4.8.1.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 279 | 40280 | uint16 |  |  | start_grad_q | [11 empty] | /components/pcs_controls | pcs_start_grad_q | Yes | 0.1 to 30000.0 % , 0 to 30000
P Rise Gradient Enable | Control | G4.8.2.1 | Holding Register |  | 1 |  |  |  |  | 280 | 40281 | uint16 |  |  | rise_grad_p_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_rise_grad_p_enable | Yes
P Rise Gradient | Control | G4.8.2.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 281 | 40282 | uint16 |  |  | rise_grad_p | [11 empty] | /components/pcs_controls | pcs_rise_grad_p | Yes
Q Rise Gradient Enable | Control | G4.8.2.3 | Holding Register |  | 1 |  |  |  |  | 282 | 40283 | uint16 |  |  | rise_grad_q_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_rise_grad_q_enable | Yes
Q Rise Gradient | Control | G4.8.2.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 283 | 40284 | uint16 |  |  | rise_grad_q | [11 empty] | /components/pcs_controls | pcs_rise_grad_q | Yes
P Drop Gradient Enable | Control | G4.8.3.1 | Holding Register |  | 1 |  |  |  |  | 284 | 40285 | uint16 |  |  | drop_grad_p_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_drop_grad_p_enable | Yes
P Drop Gradient | Control | G4.8.3.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 285 | 40286 | uint16 |  |  | drop_grad_p | [11 empty] | /components/pcs_controls | pcs_drop_grad_p | Yes
Q Drop Gradient Enable | Control | G4.8.3.3 | Holding Register |  | 1 |  |  |  |  | 286 | 40287 | uint16 |  |  | drop_grad_q_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_drop_grad_q_enable | Yes
Q Drop Gradient | Control | G4.8.3.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 287 | 40288 | uint16 |  |  | drop_grad_q | [11 empty] | /components/pcs_controls | pcs_drop_grad_q | Yes
P Stop Gradient Enable | Control | G4.8.4.1 | Holding Register |  | 1 |  |  |  |  | 288 | 40289 | uint16 |  |  | stop_grad_p_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_stop_grad_p_enable | Yes
P Stop Gradient | Control | G4.8.4.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 289 | 40290 | uint16 |  |  | stop_grad_p | [11 empty] | /components/pcs_controls | pcs_stop_grad_p | Yes
Q Stop Gradient Enable | Control | G4.8.4.3 | Holding Register |  | 1 |  |  |  |  | 290 | 40291 | uint16 |  |  | stop_grad_q_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_stop_grad_q_enable | Yes
Q Stop Gradient | Control | G4.8.4.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 291 | 40292 | uint16 |  |  | stop_grad_q | [11 empty] | /components/pcs_controls | pcs_stop_grad_q | Yes
Trackers Enable | Control | G4.9.1 | Holding Register |  | 1 |  |  |  |  | 292 | 40293 | uint16 |  |  | tracker_enable | [9 empty] | enum | 0=No, 1= Yes | /components/pcs_controls | pcs_tracker_enable | Yes
Trackers Vac Out | Control | G4.9.2 | Holding Register | V | 1 |  |  |  |  | 293 | 40294 | uint16 |  |  | tracker_vac_out | [11 empty] | /components/pcs_controls | pcs_tracker_vac_out | Yes
Trackers Vac min | Control | G4.9.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 294 | 40295 | uint16 |  |  | tracker_vac_min | [11 empty] | /components/pcs_controls | pcs_tracker_vac_min | Yes | 00 to 100, 0 to 1000
Trackers Time Start | Control | G4.9.4 | Holding Register | Sec | 1 | 10 |  |  | 0.1 | 295 | 40296 | uint16 |  |  | tracker_time_start | [11 empty] | /components/pcs_controls | pcs_tracker_time_start | Yes | 0.1 to 15 s , 0 to 150
V/P Enable | Control | G4.10.1 | Holding Register |  | 1 |  |  |  |  | 820 | 40821 | uint16 |  |  | vp_enable | [11 empty] | /components/pcs_controls | pcs_vp_enable | Yes
V/P V1 | Control | G4.10.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 821 | 40822 | uint16 |  |  | vp_v1 | [10 empty] | 100 to g4_10_3% | /components/pcs_controls | pcs_vp_v1 | Yes
V/P V2 | Control | G4.10.3 | Holding Register | % | 1 | 100 |  |  | 0.01 | 822 | 40823 | uint16 |  |  | vp_v2 | [10 empty] | G4.10.2% to 140%, G4.10.2 to 14000 | /components/pcs_controls | pcs_vp_v2 | Yes
V/P P1 | Control | G4.10.4 | Holding Register | % | 1 | 100 |  |  | 0.01 | 823 | 40824 | uint16 |  |  | vp_p1 | [10 empty] | G4.10.5% to 100%, G4.10.5 to 10000 | /components/pcs_controls | pcs_vp_p1 | Yes
V/P P2 | Control | G4.10.5 | Holding Register | % | 1 | 100 |  |  | 0.01 | 824 | 40825 | uint16 |  |  | vp_p2 | [10 empty] | 0 to G4.10.4% , 0 to G4.10.4 | /components/pcs_controls | pcs_vp_p2 | Yes
V/P Hysteresis | Control | G4.10.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 825 | 40826 | uint16 |  |  | vp_hysteresis | [10 empty] | 0 to 10%, 0 to 100 | /components/pcs_controls | pcs_vp_hysteresis | Yes
V/P Delay Hysterisis | Control | G4.10.8 | Holding Register | S | 1 | 10 |  |  | 0.1 | 827 | 40828 | uint16 |  |  | vp_delay_hysteresis | [10 empty] | 0.0 to 90 Sec, 0 to 900 | /components/pcs_controls | pcs_vp_delay_hysteresis | Yes
V/P Response Time | Control | G4.10.9 | Holding Register | S | 1 | 10 |  |  | 0.1 | 828 | 40829 | uint16 |  |  | vp_response_tiime | [10 empty] | 0.0 to 90.0s, 0 to 900 | /components/pcs_controls | pcs_vp_response_tiime | Yes
V/P Ref Power Rel | Control | G4.10.10 | Holding Register |  | 1 |  |  |  |  | 818 | 40819 | uint16 |  |  | vp_ref_power | [10 empty] | 0=rel, 1= abs | /components/pcs_controls | pcs_vp_ref_power | Yes
V/P Recover Mode | Control | G4.10.11 | Holding Register |  | 1 |  |  |  |  | 819 | 40820 | uint16 |  |  | vp_rec_mode | [10 empty] | 0=Abs, 1= Rel | /components/pcs_controls | pcs_vp_rec_mode | Yes
SVR Enable | Control | G4.11.1 | Holding Register |  | 1 |  |  |  |  | 540 | 40541 | uint16 |  |  | svr_enable | [10 empty] | 0=No, 1= Yes | /components/pcs_controls | pcs_svr_enable | Yes | Suppression of Voltage Rise
SVR V1 Threshold | Control | G4.11.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 541 | 40542 | uint16 |  |  | svr_v1_threshold | [10 empty] | 100.0% to G4.11.7%, 1000 to G4.11.7 | /components/pcs_controls | pcs_svr_v1_threshold | Yes
SVR V1 Hysteresis | Control | G4.11.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 543 | 40544 | uint16 |  |  | svr_v1_hysteresis | [10 empty] | 0.5 to 10%, 5 to 100 | /components/pcs_controls | pcs_svr_v1_hysteresis | Yes
SVR Grad Inj Q | Control | G4.11.4 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 545 | 40546 | uint16 |  |  | svr_grad_inject | [10 empty] | 0.1 to 200.0 %/S, 1 to 2000 | /components/pcs_controls | pcs_svr_grad_inject | Yes
SVR Grad Recover Q | Control | G4.11.5 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 546 | 40547 | uint16 |  |  | svr_grad_recover_q | [10 empty] | 0.1% to 200.0%, 1 to 2000 | /components/pcs_controls | pcs_svr_grad_recover_q | Yes
SVR CosFi limit | Control | G4.11.6 | Holding Register |  | 1 | 100 |  |  | 0.01 | 549 | 40550 | uint16 |  |  | svr_cosfi_limit | [10 empty] | 0.80 to 1.00. 80 to 100 | /components/pcs_controls | pcs_svr_cosfi_limit | Yes
SVR V2 Threshold | Control | G4.11.7 | Holding Register | % | 1 | 10 |  |  | 0.1 | 542 | 40543 | uint16 |  |  | svr_v2_threshold | [10 empty] | G4.11.2% to 120%, G4.11.2 to 1200 | /components/pcs_controls | pcs_svr_v2_threshold | Yes
SVR V2 Hysteresis | Control | G4.11.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 544 | 40545 | uint16 |  |  | svr_v2_hysetresis | [10 empty] | 0.5 to 10%, 5 to 100 | /components/pcs_controls | pcs_svr_v2_hysetresis | Yes
SVR Grad Reduction P | Control | G4.11.9 | Holding Register |  | 1 | 10 |  |  | 0.1 | 547 | 40548 | uint16 |  |  | svr_grad_reduction_p | [10 empty] | 0.1 to 200 %/S, 1 to 2000 | /components/pcs_controls | pcs_svr_grad_reduction_p | Yes
SVR Grad Recover P | Control | G4.11.10 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 548 | 40549 | uint16 |  |  | svr_grad_recover_p | [10 empty] | 0.1% to 200.0%, 1 to 2000 | /components/pcs_controls | pcs_svr_grad_recover_p | Yes
Active Balancing Activate | Control | G4.12.1.2 | Holding Register |  | 1 |  |  |  |  | 7021 | 47022 | uint16 |  |  | active_bal_activate | [10 empty] | 0=No, 1= Yes | /components/pcs_controls | pcs_active_bal_activate | Yes
Bank Balancing Activate | Control | G4.12.2.2 | Holding Register |  | 1 |  |  |  |  | 7024 | 47025 | uint16 |  |  | bank_bal_activate | [10 empty] | 0=No, 1= Yes | /components/pcs_controls | pcs_bank_bal_activate | Yes
Bank Balancing Reconnect Gradient | Control | G4.12.2.5 | Holding Register |  | 1 |  |  |  |  | 7027 | 47028 | uint16 |  |  | bank_bal_reconnect_grad | [10 empty] | 0.1 to 3000.0 %/s | /components/pcs_controls | pcs_bank_bal_reconnect_grad | Yes
Constant Voltage Standby Activate | Control | G4.12.3.2 | Holding Register |  | 1 |  |  |  |  | 7029 | 47030 | uint16 |  |  | cvsb_activate | [10 empty] | 0=No, 1= Yes | /components/pcs_controls | pcs_cvsb_activate | Yes
Constant Voltage Standby Time to Enter | Control | G4.12.3.3 | Holding Register |  | 1 |  |  |  |  | 7030 | 47031 | uint16 |  |  | cvsb_time_to_enter | [10 empty] | 60 to 3600 s | /components/pcs_controls | pcs_cvsb_time_to_enter | Yes | 60 to 3600s
Protections | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
LV Protections Enable | Control | G5.1.1 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | bit_field |  |  | lv_enable | [11 empty] | /components/pcs_controls | pcs_lv_enable | Yes | G5: Protections
LV Slow Protection | Control | G5.1.1.0 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | bit | 0 |  | lv_slow | [11 empty] | /components/pcs_controls | pcs_lv_slow | Yes
LV Fast Protection | Control | G5.1.1.1 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | bit | 1 |  | lv_fast | [11 empty] | /components/pcs_controls | pcs_lv_fast | Yes
LV Fast 2 Protection | Control | G5.1.1.2 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | bit | 2 |  | lv_fast_2 | [11 empty] | /components/pcs_controls | pcs_lv_fast_2 | Yes
LV Very Fast Protection | Control | G5.1.1.3 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | bit | 3 |  | lv_very_fast | [11 empty] | /components/pcs_controls | pcs_lv_very_fast | Yes
LV Very Fast 2 Protection | Control | G5.1.1.4 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | bit | 4 |  | lv_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lv_very_fast_2 | Yes
LV Interpolation | Control | G5.1.1b | Holding Register |  | 1 |  |  |  |  | 308 | 40309 | uint16 |  |  | lv_interpolation | [10 empty] | 0=No, 1= Yes | /components/pcs_controls | pcs_lv_interpolation | Yes
LV Slow Protection | Control | G5.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 301 | 40302 | uint16 |  |  | lv_slow | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_lv_slow | Yes
LV Delay Slow Protection | Control | G5.1.3 | Holding Register | S | 1 | 100 |  |  | 0.01 | 302 | 40303 | uint16 |  |  | lv_delay_slow | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_lv_delay_slow | Yes
LV Fast Protection | Control | G5.1.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 303 | 40304 | uint16 |  |  | lv_fast | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_lv_fast | Yes
LV Delay Fast Protection | Control | G5.1.5 | Holding Register | S | 1 | 100 |  |  | 0.01 | 304 | 40305 | uint16 |  |  | lv_delay_fast | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_lv_delay_fast | Yes
LV Fast Protection 2 | Control | G5.1.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 375 | 40376 | uint16 |  |  | lv_fast_2 | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_lv_fast_2 | Yes
LV Delay Fast Protection 2 | Control | G5.1.7 | Holding Register | S | 1 | 100 |  |  | 0.01 | 376 | 40377 | uint16 |  |  | lv_delay_fast_2 | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_lv_delay_fast_2 | Yes
LV Very Fast Protection | Control | G5.1.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 305 | 40306 | uint16 |  |  | lv_very_fast | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_lv_very_fast | Yes
LV Delay Very Fast Protection | Control | G5.1.9 | Holding Register | S | 1 | 100 |  |  | 0.01 | 306 | 40307 | uint16 |  |  | lv_delay_very_fast | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_lv_delay_very_fast | Yes
LV Very Fast Protection 2 | Control | G5.1.10 | Holding Register | % | 1 | 10 |  |  | 0.1 | 377 | 40378 | uint16 |  |  | lv_very_fast_2 | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_lv_very_fast_2 | Yes
LV Delay Very Fast Protection 2 | Control | G5.1.11 | Holding Register | S | 1 | 100 |  |  | 0.01 | 378 | 40379 | uint16 |  |  | lv_delay_very_fast_2 | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_lv_delay_very_fast_2 | Yes
HV Protections Enable | Control | G5.2.1 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | bit_field |  |  | hv_enable | [11 empty] | /components/pcs_controls | pcs_hv_enable | Yes
HV Slow Protection | Control | G5.2.1.0 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | bit | 0 |  | hv_slow | [11 empty] | /components/pcs_controls | pcs_hv_slow | Yes
HV Fast Protection | Control | G5.2.1.1 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | bit | 1 |  | hv_fast | [11 empty] | /components/pcs_controls | pcs_hv_fast | Yes
HV Fast 2 Protection | Control | G5.2.1.2 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | bit | 2 |  | hv_fast_2 | [11 empty] | /components/pcs_controls | pcs_hv_fast_2 | Yes
HV Very Fast Protection | Control | G5.2.1.3 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | bit | 3 |  | hv_very_fast | [11 empty] | /components/pcs_controls | pcs_hv_very_fast | Yes
HV Very Fast 2 Protection | Control | G5.2.1.4 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | bit | 4 |  | hv_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hv_very_fast_2 | Yes
HV Interpolation | Control | G5.2.1b | Holding Register |  | 1 |  |  |  |  | 317 | 40318 | uint16 |  |  | hv_interpolation | [10 empty] | 0=No, 1= Yes | /components/pcs_controls | pcs_hv_interpolation | Yes
HV Slow Protection | Control | G5.2.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 311 | 40312 | uint16 |  |  | hv_slow | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_hv_slow | Yes
HV Delay Slow Protection | Control | G5.2.3 | Holding Register | S | 1 | 100 |  |  | 0.01 | 312 | 40313 | uint16 |  |  | hv_delay_slow | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_hv_delay_slow | Yes
HV Fast Protection | Control | G5.2.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 313 | 40314 | uint16 |  |  | hv_fast | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_hv_fast | Yes
HV Delay Fast Protection | Control | G5.2.5 | Holding Register | S | 1 | 100 |  |  | 0.01 | 314 | 40315 | uint16 |  |  | hv_delay_fast | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_hv_delay_fast | Yes
HV Fast Protection 2 | Control | G5.2.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 379 | 40380 | uint16 |  |  | hv_fast_2 | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_hv_fast_2 | Yes
HV Delay Fast Protection 2 | Control | G5.2.7 | Holding Register | S | 1 | 100 |  |  | 0.01 | 380 | 40381 | uint16 |  |  | hv_delay_fast_2 | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_hv_delay_fast_2 | Yes
HV Very Fast Protection | Control | G5.2.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 315 | 40316 | uint16 |  |  | hv_very_fast | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_hv_very_fast | Yes
HV Delay Very Fast Protection | Control | G5.2.9 | Holding Register | S | 1 | 100 |  |  | 0.01 | 316 | 40317 | uint16 |  |  | hv_delay_very_fast | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_hv_delay_very_fast | Yes
HV Very Fast Protection 2 | Control | G5.2.10 | Holding Register | % | 1 | 10 |  |  | 0.1 | 381 | 40382 | uint16 |  |  | hv_very_fast_2 | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_hv_very_fast_2 | Yes
HV Delay Very Fast Protection 2 | Control | G5.2.11 | Holding Register | S | 1 | 100 |  |  | 0.01 | 382 | 40383 | uint16 |  |  | hv_delay_very_fast_2 | [10 empty] | 0.0 to 6550.0S , 0 to 65500 | /components/pcs_controls | pcs_hv_delay_very_fast_2 | Yes
LF Protections Enable | Control | G5.3.1 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | bit_field |  |  | lf_enable | [11 empty] | /components/pcs_controls | pcs_lf_enable | Yes
LF Slow Protection | Control | G5.3.1.0 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | bit | 0 |  | lf_slow | [11 empty] | /components/pcs_controls | pcs_lf_slow | Yes
LF Slow 2 Protection | Control | G5.3.1.1 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | bit | 1 |  | lf_slow_2 | [11 empty] | /components/pcs_controls | pcs_lf_slow_2 | Yes
LF Fast Protection | Control | G5.3.1.2 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | bit | 2 |  | lf_fast | [11 empty] | /components/pcs_controls | pcs_lf_fast | Yes
LF Very Fast Protection | Control | G5.3.1.3 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | bit | 3 |  | lf_very_fast | [11 empty] | /components/pcs_controls | pcs_lf_very_fast | Yes
LF Very Fast 2 Protection | Control | G5.3.1.4 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | bit | 4 |  | lf_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lf_very_fast_2 | Yes
LF Slow Protection | Control | G5.3.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 321 | 40322 | uint16 |  |  | lf_slow | [10 empty] | 0 to 100%, 10 to 1000 | /components/pcs_controls | pcs_lf_slow | Yes
LF Delay Slow Protection | Control | G5.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 322 | 40323 | uint16 |  |  | lf_delay_slow | [11 empty] | /components/pcs_controls | pcs_lf_delay_slow | Yes
LF Slow 2 Protection | Control | G5.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 383 | 40384 | uint16 |  |  | lf_slow_2 | [11 empty] | /components/pcs_controls | pcs_lf_slow_2 | Yes
LF Delay Slow 2 Protection | Control | G5.3.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 384 | 40385 | uint16 |  |  | lf_delay_slow_2 | [11 empty] | /components/pcs_controls | pcs_lf_delay_slow_2 | Yes
LF Fast Protection | Control | G5.3.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 323 | 40324 | uint16 |  |  | lf_fast | [11 empty] | /components/pcs_controls | pcs_lf_fast | Yes
LF Delay Fast Protection | Control | G5.3.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 324 | 40325 | uint16 |  |  | lf_delay_fast | [11 empty] | /components/pcs_controls | pcs_lf_delay_fast | Yes
LF Very Fast Protection | Control | G5.3.8 | Holding Register |  | 1 | 100 |  |  | 0.01 | 325 | 40326 | uint16 |  |  | lf_very_fast | [11 empty] | /components/pcs_controls | pcs_lf_very_fast | Yes
LF Delay Very Fast Protection | Control | G5.3.9 | Holding Register |  | 1 | 10 |  |  | 0.1 | 326 | 40327 | uint16 |  |  | lf_delay_very_fast | [11 empty] | /components/pcs_controls | pcs_lf_delay_very_fast | Yes
LF Very Fast 2 Protection | Control | G5.3.10 | Holding Register |  | 1 | 10 |  |  | 0.1 | 385 | 40386 | uint16 |  |  | lf_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lf_very_fast_2 | Yes
LF Delay Very Fast 2 Protection | Control | G5.3.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 386 | 40387 | uint16 |  |  | lf_delay_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lf_delay_very_fast_2 | Yes
HF Protections Enable | Control | G5.4.1 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | bit_field |  |  | hf_enable | [11 empty] | /components/pcs_controls | pcs_hf_enable | Yes
HF Slow Protection | Control | G5.4.1.0 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | bit | 0 |  | hf_slow | [11 empty] | /components/pcs_controls | pcs_hf_slow | Yes
HF Slow 2 Protection | Control | G5.4.1.1 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | bit | 1 |  | hf_slow_2 | [11 empty] | /components/pcs_controls | pcs_hf_slow_2 | Yes
HF Fast Protection | Control | G5.4.1.2 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | bit | 2 |  | hf_fast | [11 empty] | /components/pcs_controls | pcs_hf_fast | Yes
HF Very Fast Protection | Control | G5.4.1.3 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | bit | 3 |  | hf_very_fast | [11 empty] | /components/pcs_controls | pcs_hf_very_fast | Yes
HF Very Fast 2 Protection | Control | G5.4.1.4 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | bit | 4 |  | hf_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hf_very_fast_2 | Yes
HF Slow Protection |  | G5.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 331 | 40332 | uint16 |  |  | hf_slow | [11 empty] | /components/pcs_controls | pcs_hf_slow | Yes
HF Delay Slow Protection |  | G5.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 332 | 40333 | uint16 |  |  | hf_delay_slow | [11 empty] | /components/pcs_controls | pcs_hf_delay_slow | Yes
HF Slow 2 Protection |  | G5.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 387 | 40388 | uint16 |  |  | hf_slow_2 | [11 empty] | /components/pcs_controls | pcs_hf_slow_2 | Yes
HF Delay Slow 2 Protection |  | G5.4.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 388 | 40389 | uint16 |  |  | hf_delay_slow_2 | [11 empty] | /components/pcs_controls | pcs_hf_delay_slow_2 | Yes
HF Fast Protection |  | G5.4.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 333 | 40334 | uint16 |  |  | hf_fast | [11 empty] | /components/pcs_controls | pcs_hf_fast | Yes
HF Delay Fast Protection |  | G5.4.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 334 | 40335 | uint16 |  |  | hf_delay_fast | [11 empty] | /components/pcs_controls | pcs_hf_delay_fast | Yes
HF Very Fast Protection |  | G5.4.8 | Holding Register |  | 1 | 10 |  |  | 0.1 | 335 | 40336 | uint16 |  |  | hf_very_fast | [11 empty] | /components/pcs_controls | pcs_hf_very_fast | Yes
HF Delay Very Fast Protection |  | G5.4.9 | Holding Register |  | 1 | 100 |  |  | 0.01 | 336 | 40337 | uint16 |  |  | hf_delay_very_fast | [11 empty] | /components/pcs_controls | pcs_hf_delay_very_fast | Yes
HF Very Fast 2 Protection |  | G5.4.10 | Holding Register |  | 1 | 10 |  |  | 0.1 | 389 | 40390 | uint16 |  |  | hf_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hf_very_fast_2 | Yes
HF Delay Very Fast 2 Protection |  | G5.4.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 390 | 40391 | uint16 |  |  | hf_delay_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hf_delay_very_fast_2 | Yes
Enable 5.4b.1.1 |  | G5.4b.1.1 | Holding Register |  | 1 |  |  |  |  | 730 | 40731 | uint16 |  |  | hv_hf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_1 | Yes
V1 = 120% |  | G5.4b.1.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 731 | 40732 | uint16 |  |  | hv_hf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_1_V1 | Yes
f1 = 62.00 Hz |  | G5.4b.1.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 732 | 40733 | uint16 |  |  | hv_hf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_1_f1 | Yes
t1 = 1.0 s |  | G5.4b.1.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 733 | 40734 | uint16 |  |  | hv_hf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_1_t1 | Yes
Enable 5.4b.2.1 |  | G5.4b.2.1 | Holding Register |  | 1 |  |  |  |  | 734 | 40735 | uint16 |  |  | lv_hf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_2 | Yes
V2 = 80% |  | G5.4b.2.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 735 | 40736 | uint16 |  |  | lv_hf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_2_V2 | Yes
f2 = 62.00 Hz |  | G5.4b.2.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 736 | 40737 | uint16 |  |  | lv_hf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_2_f2 | Yes
t2 = 1.0 s |  | G5.4b.2.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 737 | 40738 | uint16 |  |  | lv_hf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_2_t2 | Yes
Enable 5.4b.3.1 |  | G5.4b.3.1 | Holding Register |  | 1 |  |  |  |  | 738 | 40739 | uint16 |  |  | hv_lf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_3 | Yes
V3 = 120% |  | G5.4b.3.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 739 | 40740 | uint16 |  |  | hv_lf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_3_V3 | Yes
f3 = 58.00 Hz |  | G5.4b.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 740 | 40741 | uint16 |  |  | hv_lf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_3_f3 | Yes
t3 = 1.0 s |  | G5.4b.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 741 | 40742 | uint16 |  |  | hv_lf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_3_t3 | Yes
Enable 5.4b.4.1 |  | G5.4b.4.1 | Holding Register |  | 1 |  |  |  |  | 472 | 40473 | uint16 |  |  | lv_lf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_4 | Yes
V4 = 80% |  | G5.4b.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 473 | 40474 | uint16 |  |  | lv_lf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_4_V4 | Yes
f4 = 58.00 Hz |  | G5.4b.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 474 | 40475 | uint16 |  |  | lv_lf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_4_f4 | Yes
t4 = 1.0 s |  | G5.4b.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 475 | 40476 | uint16 |  |  | lv_lf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_4_t4 | Yes
Unbalance Protections |  | G5.5.1 | Holding Register |  | 1 |  |  |  |  | 340 | 40341 | bit_field |  |  | unbalance_enable | [11 empty] | /components/pcs_controls | pcs_unbalance_enable | Yes
I unbalance |  | G5.5.1.0 | Holding Register |  | 1 |  |  |  |  | 340 | 40341 | bit | 0 |  | unbalance_i | [11 empty] | /components/pcs_controls | pcs_unbalance_i | Yes
v unbalance |  | G5.5.1.1 | Holding Register |  | 1 |  |  |  |  | 340 | 40341 | bit | 1 |  | unbalance_v | [11 empty] | /components/pcs_controls | pcs_unbalance_v | Yes
I unbalance |  | G5.5.2 | Holding Register |  | 1 | 1 |  |  | 1 | 341 | 40342 | uint16 |  |  | unbalance_i_threshold | [11 empty] | /components/pcs_controls | pcs_unbalance_i_threshold | Yes
I unbalance min |  | G5.5.2b | Holding Register |  | 1 | 1 |  |  | 1 | 347 | 40348 | uint16 |  |  | unbalance_i_min | [11 empty] | /components/pcs_controls | pcs_unbalance_i_min | Yes
Delay I unbalance |  | G5.5.3 | Holding Register |  | 1 | 1 |  |  | 1 | 342 | 40343 | uint16 |  |  | unbalance_i_delay | [11 empty] | /components/pcs_controls | pcs_unbalance_i_delay | Yes
Unbalance V |  | G5.5.4 | Holding Register |  | 1 | 1 |  |  | 1 | 343 | 40344 | uint16 |  |  | unbalance_v_threshold | [11 empty] | /components/pcs_controls | pcs_unbalance_v_threshold | Yes
Delay Unbalance V |  | G5.5.5 | Holding Register |  | 1 | 1 |  |  | 1 | 344 | 40345 | uint16 |  |  | unbalance_v_delay | [11 empty] | /components/pcs_controls | pcs_unbalance_v_delay | Yes
Anti Islanding Enable |  | G5.6.1 | Holding Register |  | 1 |  |  |  |  | 350 | 40351 | bit_field |  |  | antiislanding_enable | [11 empty] | /components/pcs_controls | pcs_antiislanding_enable | Yes
Anti Islanding off |  | G5.6.1.0 | Holding Register |  | 1 |  |  |  |  | 350 | 40351 | bit | 0 |  | antiislanding_off | [11 empty] | /components/pcs_controls | pcs_antiislanding_off | Yes
Anti Islanding Active |  | G5.6.1.1 | Holding Register |  | 1 |  |  |  |  | 350 | 40351 | bit | 1 |  | antiislanding_active | [11 empty] | /components/pcs_controls | pcs_antiislanding_active | Yes
Anti Islanding Passive |  | G5.6.1.2 | Holding Register |  | 1 |  |  |  |  | 350 | 40351 | bit | 2 |  | antiislanding_passive | [11 empty] | /components/pcs_controls | pcs_antiislanding_passive | Yes
Anti Islanding Simultaneous |  | G5.6.1.3 | Holding Register |  | 1 |  |  |  |  | 350 | 40351 | bit | 3 |  | antiislanding_simultaneous | [11 empty] | /components/pcs_controls | pcs_antiislanding_simultaneous | Yes
IGBTs temp thres fit=125 C |  | G5.7.1 | Holding Register |  | 1 | 1 |  |  | 1 | 360 | 40361 | uint16 |  |  | igbt_temp_thres_fit | [11 empty] | /components/pcs_controls | pcs_igbt_temp_thres_fit | Yes
IGBTs temp hist =10 C |  | G5.7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 361 | 40362 | uint16 |  |  | igbt_temp_hist | [11 empty] | /components/pcs_controls | pcs_igbt_temp_hist | Yes
Module temp thres fit=85 C |  | G5.7.3 | Holding Register |  | 1 | 1 |  |  | 1 | 362 | 40363 | uint16 |  |  | module_temp_thres_fit | [11 empty] | /components/pcs_controls | pcs_module_temp_thres_fit | Yes
Module temp thist=10 C |  | G5.7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 363 | 40364 | uint16 |  |  | module_temp_hist | [11 empty] | /components/pcs_controls | pcs_module_temp_hist | Yes
Internal temp thres fit=85 C |  | G5.7.5 | Holding Register |  | 1 | 1 |  |  | 1 | 364 | 40365 | uint16 |  |  | internal_temp_thres_fit | [11 empty] | /components/pcs_controls | pcs_internal_temp_thres_fit | Yes
HVPL Enable 5.9.1 |  | G5.9.1 | Holding Register |  | 1 |  |  |  |  | 391 | 40392 | bit_field |  |  | hvpl_enable | [11 empty] | /components/pcs_controls | pcs_hvpl_enable | Yes
HVPL Enable 5.9.1 No |  | G5.9.1.0 | Holding Register |  | 1 |  |  |  |  | 391 | 40392 | bit | 0 |  | bit_hvpl_no | [11 empty] | /components/pcs_controls | pcs_bit_hvpl_no | Yes
HVPL Enable 5.9.1 Yes |  | G5.9.1.1 | Holding Register |  | 1 | 1 |  |  | 1 | 391 | 40392 | bit | 1 |  | bit_hvpl_yes | [11 empty] | /components/pcs_controls | pcs_bit_hvpl_yes | Yes
HVPL Activation Level = 5% |  | G5.9.2 | Holding Register |  | 1 | 1 |  |  | 1 | 392 | 40393 | uint16 |  |  | hvpl_activation_level_5 | [11 empty] | /components/pcs_controls | pcs_hvpl_activation_level_5 | Yes
HVPL Scale = 1000 |  | G5.9.3 | Holding Register |  | 1 | 1 |  |  | 1 | 393 | 40394 | uint16 |  |  | hvpl_scale_1000 | [11 empty] | /components/pcs_controls | pcs_hvpl_scale_1000 | Yes
HVPL Fault Level = 0 |  | G5.9.4 | Holding Register |  | 1 | 1 |  |  | 1 | 394 | 40395 | uint16 |  |  | hvpl_fault_level_0 | [11 empty] | /components/pcs_controls | pcs_hvpl_fault_level_0 | Yes
HVPL filter = 0.100 Hz |  | G5.9.5 | Holding Register |  | 1 | 1000 |  |  | 0.001 | 395 | 40396 | uint16 |  |  | hvpl_filter_hz_100_hz | [11 empty] | /components/pcs_controls | pcs_hvpl_filter_hz_100_hz | Yes
HVPL delay fault = 2.0 s |  | G5.9.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 396 | 40397 | uint16 |  |  | hvpl_delay_fault_s_0_s | [11 empty] | /components/pcs_controls | pcs_hvpl_delay_fault_s_0_s | Yes
HVPL Start Test |  | G5.9.7 | Holding Register |  | 1 |  |  |  |  | 397 | 40398 | bit_field |  |  | hvpl_start_test | [11 empty] | /components/pcs_controls | pcs_hvpl_start_test | Yes
HVPL Start Test no |  | G5.9.7.0 | Holding Register |  | 1 |  |  |  |  | 397 | 40398 | bit | 0 |  | bit_hvpl_test_no | [11 empty] | /components/pcs_controls | pcs_bit_hvpl_test_no | Yes
HVPL Start Test yes |  | G5.9.7.1 | Holding Register |  | 1 |  |  |  |  | 397 | 40398 | bit | 1 |  | bit_hvpl_test_yes | [11 empty] | /components/pcs_controls | pcs_bit_hvpl_test_yes | Yes
HVPL Test Level = -20% |  | G5.9.8 | Holding Register |  | 1 | 1 |  |  | 1 | 398 | 40399 | int16 |  |  | hvpl_test_level_20 | [11 empty] | /components/pcs_controls | pcs_hvpl_test_level_20 | Yes
Earth Current |  | G5.11.1 | Holding Register | % | 1 | 10 |  |  | 0.1 | 370 | 40371 | uint16 |  |  | earth_current | [11 empty] | /components/pcs_controls | pcs_earth_current | Yes
Delay High Vdc = 1 s |  | G5.11.2 | Holding Register | s | 1 | 1 |  |  | 1 | 371 | 40372 | uint16 |  |  | high_vdc_delay | [11 empty] | /components/pcs_controls | pcs_high_vdc_delay | Yes
DU Overcurrent = 400.0 A |  | G5.11.3 | Holding Register | A | 1 | 10 |  |  | 0.1 | 372 | 40373 | uint16 |  |  | du_overcurrent | [11 empty] | /components/pcs_controls | pcs_du_overcurrent | Yes
MV manometer fault = off |  | G5.11.4 | Holding Register |  | 1 | 1 |  |  | 1 | 480 | 40481 | uint16 |  |  | mv_manometer_fault | [11 empty] | /components/pcs_controls | pcs_mv_manometer_fault | Yes
MV manometer delay = 10 s |  | G5.11.5 | Holding Register | s | 1 | 1 |  |  | 1 | 481 | 40482 | uint16 |  |  | mv_manometer_delay | [11 empty] | /components/pcs_controls | pcs_mv_manometer_delay | Yes
LV manometer fault = off |  | G5.11.6 | Holding Register |  | 1 | 1 |  |  | 1 | 482 | 40483 | uint16 |  |  | lv_manometer_fault | [11 empty] | /components/pcs_controls | pcs_lv_manometer_fault | Yes
LV manometer delay = 10 s |  | G5.11.7 | Holding Register | s | 1 | 1 |  |  | 1 | 483 | 40484 | uint16 |  |  | lv_manometer_delay | [11 empty] | /components/pcs_controls | pcs_lv_manometer_delay | Yes
Communications | [15 empty] | pcs_controls | [5 empty] | 2000 | 20 | 98
Display Baudrate = 115200 |  | G6.1.1 | Holding Register | bps | 1 |  |  |  |  | 400 | 40401 | uint16 |  |  | display_baudrate | [11 empty] | /components/pcs_controls | pcs_display_baudrate | Yes
Modbus Address=150 |  | G6.1.2 | Holding Register |  | 1 |  |  |  |  | 401 | 40402 | uint16 |  |  | modbus_address | [11 empty] | /components/pcs_controls | pcs_modbus_address | Yes
Modbus Baudrate=19200 bps |  | G6.1.3 | Holding Register | bps | 1 |  |  |  |  | 402 | 40403 | uint16 |  |  | modbus_baudrate | [11 empty] | /components/pcs_controls | pcs_modbus_baudrate | Yes
Modbus Parity |  | G6.1.4 | Holding Register |  | 1 |  |  |  |  | 403 | 40404 | uint16 |  |  | modbus_parity | [11 empty] | /components/pcs_controls | pcs_modbus_parity | Yes
Modbus Stop bits |  | G6.1.5 | Holding Register |  | 1 |  |  |  |  | 404 | 40405 | uint16 |  |  | modbus_stop_bits | [11 empty] | /components/pcs_controls | pcs_modbus_stop_bits | Yes
Modbus Master |  | G6.1.6 | Holding Register |  | 1 |  |  |  |  | 405 | 40406 | uint16 |  |  | modbus_master | [11 empty] | /components/pcs_controls | pcs_modbus_master | Yes
Automatic IP |  | G6.2.1 | Holding Register |  | 1 |  |  |  |  | 410 | 40411 | uint16 |  |  | automatic_ip | [11 empty] | /components/pcs_controls | pcs_automatic_ip | Yes
Assigned IP A |  | G6.2.1.1a | Holding Register |  | 1 |  |  |  |  | 411 | 40412 | uint16 |  |  | assigned_ip_a | [11 empty] | /components/pcs_controls | pcs_assigned_ip_a | Yes
Assigned IP B |  | G6.2.1.1b | Holding Register |  | 1 |  |  |  |  | 412 | 40413 | uint16 |  |  | assigned_ip_b | [11 empty] | /components/pcs_controls | pcs_assigned_ip_b | Yes
Assigned IP C |  | G6.2.1.1c | Holding Register |  | 1 |  |  |  |  | 413 | 40414 | uint16 |  |  | assigned_ip_c | [11 empty] | /components/pcs_controls | pcs_assigned_ip_c | Yes
Assigned IP D |  | G6.2.1.1d | Holding Register |  | 1 |  |  |  |  | 414 | 40415 | uint16 |  |  | assigned_ip_d | [11 empty] | /components/pcs_controls | pcs_assigned_ip_d | Yes
Assigned Subnet A |  | G6.2.1.2a | Holding Register |  | 1 |  |  |  |  | 415 | 40416 | uint16 |  |  | assigned_subnet_a | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_a | Yes
Assigned Subnet B |  | G6.2.1.2b | Holding Register |  | 1 |  |  |  |  | 416 | 40417 | uint16 |  |  | assigned_subnet_b | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_b | Yes
Assigned Subnet C |  | G6.2.1.2c | Holding Register |  | 1 |  |  |  |  | 417 | 40418 | uint16 |  |  | assigned_subnet_c | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_c | Yes
Assigned Subnet D |  | G6.2.1.2d | Holding Register |  | 1 |  |  |  |  | 418 | 40419 | uint16 |  |  | assigned_subnet_d | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_d | Yes
Assigned Gateway A |  | G6.2.1.3a | Holding Register |  | 1 |  |  |  |  | 419 | 40420 | uint16 |  |  | assigned_gateway_a | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_a | Yes
Assigned Gateway B |  | G6.2.1.3b | Holding Register |  | 1 |  |  |  |  | 420 | 40421 | uint16 |  |  | assigned_gateway_b | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_b | Yes
Assigned Gateway C |  | G6.2.1.3c | Holding Register |  | 1 |  |  |  |  | 421 | 40422 | uint16 |  |  | assigned_gateway_c | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_c | Yes
Assigned Gateway D |  | G6.2.1.3d | Holding Register |  | 1 |  |  |  |  | 422 | 40423 | uint16 |  |  | assigned_gateway_d | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_d | Yes
IP address A |  | G6.2.2a | Holding Register |  | 1 |  |  |  |  | 423 | 40424 | uint16 |  |  | ip_address_a | [11 empty] | /components/pcs_controls | pcs_ip_address_a | Yes
IP address B |  | G6.2.2b | Holding Register |  | 1 |  |  |  |  | 424 | 40425 | uint16 |  |  | ip_address_b | [11 empty] | /components/pcs_controls | pcs_ip_address_b | Yes
IP address C |  | G6.2.2c | Holding Register |  | 1 |  |  |  |  | 425 | 40426 | uint16 |  |  | ip_address_c | [11 empty] | /components/pcs_controls | pcs_ip_address_c | Yes
IP address D |  | G6.2.2d | Holding Register |  | 1 |  |  |  |  | 426 | 40427 | uint16 |  |  | ip_address_d | [11 empty] | /components/pcs_controls | pcs_ip_address_d | Yes
Subnet A |  | G6.2.3a | Holding Register |  | 1 |  |  |  |  | 427 | 40428 | uint16 |  |  | subnet_a | [11 empty] | /components/pcs_controls | pcs_subnet_a | Yes
Subnet B |  | G6.2.3b | Holding Register |  | 1 |  |  |  |  | 428 | 40429 | uint16 |  |  | subnet_b | [11 empty] | /components/pcs_controls | pcs_subnet_b | Yes
Subnet C |  | G6.2.3c | Holding Register |  | 1 |  |  |  |  | 429 | 40430 | uint16 |  |  | subnet_c | [11 empty] | /components/pcs_controls | pcs_subnet_c | Yes
Subnet D |  | G6.2.3d | Holding Register |  | 1 |  |  |  |  | 430 | 40431 | uint16 |  |  | subnet_d | [11 empty] | /components/pcs_controls | pcs_subnet_d | Yes
Gateway A |  | G6.2.4a | Holding Register |  | 1 |  |  |  |  | 431 | 40432 | uint16 |  |  | gateway_a | [11 empty] | /components/pcs_controls | pcs_gateway_a | Yes
Gateway B |  | G6.2.4b | Holding Register |  | 1 |  |  |  |  | 432 | 40433 | uint16 |  |  | gateway_b | [11 empty] | /components/pcs_controls | pcs_gateway_b | Yes
Gateway C |  | G6.2.4c | Holding Register |  | 1 |  |  |  |  | 433 | 40434 | uint16 |  |  | gateway_c | [11 empty] | /components/pcs_controls | pcs_gateway_c | Yes
Gateway D |  | G6.2.4d | Holding Register |  | 1 |  |  |  |  | 434 | 40435 | uint16 |  |  | gateway_d | [11 empty] | /components/pcs_controls | pcs_gateway_d | Yes
Mac A |  | G6.2.5a | Holding Register |  | 1 |  |  |  |  | 435 | 40436 | uint16 |  |  | mac_a | [11 empty] | /components/pcs_controls | pcs_mac_a | Yes
Mac B |  | G6.2.5b | Holding Register |  | 1 |  |  |  |  | 436 | 40437 | uint16 |  |  | mac_b | [11 empty] | /components/pcs_controls | pcs_mac_b | Yes
Mac C |  | G6.2.5c | Holding Register |  | 1 |  |  |  |  | 437 | 40438 | uint16 |  |  | mac_c | [11 empty] | /components/pcs_controls | pcs_mac_c | Yes
Mac D |  | G6.2.5d | Holding Register |  | 1 |  |  |  |  | 438 | 40439 | uint16 |  |  | mac_d | [11 empty] | /components/pcs_controls | pcs_mac_d | Yes
Mac E |  | G6.2.5e | Holding Register |  | 1 |  |  |  |  | 439 | 40440 | uint16 |  |  | mac_e | [11 empty] | /components/pcs_controls | pcs_mac_e | Yes
Mac F |  | G6.2.5e | Holding Register |  | 1 |  |  |  |  | 440 | 40441 | uint16 |  |  | mac_f | [11 empty] | /components/pcs_controls | pcs_mac_f | Yes
Watchdog timer input |  | G6.3 | Holding Register |  | 1 | 1 |  |  | 1 | 4251 | 44252 | uint16 |  |  | ppc_watchdog_ref | [11 empty] | /components/pcs_controls | pcs_ppc_watchdog_ref | Yes
Reset refs time = 4s |  | G6.3.1 | Holding Register |  | 1 | 1 |  |  | 1 | 4252 | 44253 | uint16 |  |  | reset_refs_time_s | [11 empty] | /components/pcs_controls | pcs_reset_refs_time_s | Yes
Comms Fault time = 60 s |  | G6.3.2 | Holding Register |  | 1 | 1 |  |  | 1 | 4253 | 44254 | uint16 |  |  | comms_fault_time_s_s | [11 empty] | /components/pcs_controls | pcs_comms_fault_time_s_s | Yes
Home P ref = 0.0% |  | G6.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 4254 | 44255 | uint16 |  |  | home_p_ref_0_0 | [11 empty] | /components/pcs_controls | pcs_home_p_ref_0_0 | Yes
Home Q ref = 0.0% |  | G6.3.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 4255 | 44256 | int16 |  |  | home_q_ref_0_0 | [11 empty] | /components/pcs_controls | pcs_home_q_ref_0_0 | Yes
Auto Reset | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
Auto Reset Enable |  | G7.1 | Holding Register |  | 1 |  |  |  |  | 500 | 40501 | uint16 |  |  | auto_reset_enable | [11 empty] | /components/pcs_controls | pcs_enable_g_1 | Yes
Number of Retries |  | G7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 501 | 40502 | uint16 |  |  | number_of_retries | [11 empty] | /components/pcs_controls | pcs_number_of_retries | Yes
Delay between retries = 30 s |  | G7.3 | Holding Register |  | 1 | 10 |  |  | 0.1 | 502 | 40503 | uint16 |  |  | delay_between_retries_s_s | [11 empty] | /components/pcs_controls | pcs_delay_between_retries_s_s | Yes
Reset Retries timeout |  | G7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 503 | 40504 | uint16 |  |  | reset_retries_timeout | [11 empty] | /components/pcs_controls | pcs_reset_retries_timeout | Yes
All Faults enabled |  | G7.5 | Holding Register |  | 1 |  |  |  |  | 504 | 40505 | uint16 |  |  | all_faults_enabled | [11 empty] | /components/pcs_controls | pcs_all_faults_enabled | Yes
Faults allowed number = 0 |  | G7.6 | Holding Register |  | 1 |  |  |  |  | 505 | 40506 | uint16 |  |  | faults_allowed_number | [11 empty] | /components/pcs_controls | pcs_faults_allowed_number | Yes
Faults allowed 1 = No Faults |  | G7.6.1 | Holding Register |  | 1 |  |  |  |  | 506 | 40507 | uint16 |  |  | faults_allowed_1 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_1 | Yes
Faults allowed 2 = No Faults |  | G7.6.2 | Holding Register |  | 1 |  |  |  |  | 507 | 40508 | uint16 |  |  | faults_allowed_2 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_2 | Yes
Faults allowed 3 = No Faults |  | G7.6.3 | Holding Register |  | 1 |  |  |  |  | 508 | 40509 | uint16 |  |  | faults_allowed_3 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_3 | Yes
Faults allowed 4 = No Faults |  | G7.6.4 | Holding Register |  | 1 |  |  |  |  | 509 | 40510 | uint16 |  |  | faults_allowed_4 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_4 | Yes
Faults allowed 5 = No Faults |  | G7.6.5 | Holding Register |  | 1 |  |  |  |  | 510 | 40511 | uint16 |  |  | faults_allowed_5 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_5 | Yes
Faults allowed 6 = No Faults |  | G7.6.6 | Holding Register |  | 1 |  |  |  |  | 511 | 40512 | uint16 |  |  | faults_allowed_6 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_6 | Yes
Faults allowed 7 = No Faults |  | G7.6.7 | Holding Register |  | 1 |  |  |  |  | 512 | 40513 | uint16 |  |  | faults_allowed_7 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_7 | Yes
Faults allowed 8 = No Faults |  | G7.6.8 | Holding Register |  | 1 |  |  |  |  | 513 | 40514 | uint16 |  |  | faults_allowed_8 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_8 | Yes
Faults allowed 9 = No Faults |  | G7.6.9 | Holding Register |  | 1 |  |  |  |  | 514 | 40515 | uint16 |  |  | faults_allowed_9 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_9 | Yes
Faults allowed 10 = No Faults |  | G7.6.10 | Holding Register |  | 1 |  |  |  |  | 515 | 40516 | uint16 |  |  | faults_allowed_10 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_10 | Yes
Faults exception number = 0 |  | G7.7 | Holding Register |  | 1 |  |  |  |  | 516 | 40517 | uint16 |  |  | faults_exception_number | [11 empty] | /components/pcs_controls | pcs_faults_exception_number | Yes
Faults exception 1 = No faults |  | G7.7.1 | Holding Register |  | 1 |  |  |  |  | 517 | 40518 | uint16 |  |  | faults_exception_1 | [11 empty] | /components/pcs_controls | pcs_faults_exception_1 | Yes
Faults exception 2 = No faults |  | G.7.2 | Holding Register |  | 1 |  |  |  |  | 518 | 40519 | uint16 |  |  | faults_exception_2 | [11 empty] | /components/pcs_controls | pcs_faults_exception_2 | Yes
Faults exception 3 = No faults |  | G7.7.3 | Holding Register |  | 1 |  |  |  |  | 519 | 40520 | uint16 |  |  | faults_exception_3 | [11 empty] | /components/pcs_controls | pcs_faults_exception_3 | Yes
Faults exception 4 = No faults |  | G7.7.4 | Holding Register |  | 1 |  |  |  |  | 520 | 40521 | uint16 |  |  | faults_exception_4 | [11 empty] | /components/pcs_controls | pcs_faults_exception_4 | Yes
Faults exception 5 = No faults |  | G7.7.5 | Holding Register |  | 1 |  |  |  |  | 521 | 40522 | uint16 |  |  | faults_exception_5 | [11 empty] | /components/pcs_controls | pcs_faults_exception_5 | Yes
Faults exception 6 = No faults |  | G7.7.6 | Holding Register |  | 1 |  |  |  |  | 522 | 40523 | uint16 |  |  | faults_exception_6 | [11 empty] | /components/pcs_controls | pcs_faults_exception_6 | Yes
Faults exception 7 = No faults |  | G7.7.7 | Holding Register |  | 1 |  |  |  |  | 523 | 40524 | uint16 |  |  | faults_exception_7 | [11 empty] | /components/pcs_controls | pcs_faults_exception_7 | Yes
Faults exception 8 = No faults |  | G7.7.8 | Holding Register |  | 1 |  |  |  |  | 524 | 40525 | uint16 |  |  | faults_exception_8 | [11 empty] | /components/pcs_controls | pcs_faults_exception_8 | Yes
Faults exception 9 = No faults |  | G7.7.9 | Holding Register |  | 1 |  |  |  |  | 525 | 40526 | uint16 |  |  | faults_exception_9 | [11 empty] | /components/pcs_controls | pcs_faults_exception_9 | Yes
Faults exception 10 = No faults |  | G7.7.10 | Holding Register |  | 1 |  |  |  |  | 526 | 40527 | uint16 |  |  | faults_exception_10 | [11 empty] | /components/pcs_controls | pcs_faults_exception_10 | Yes
Control | [15 empty] | pcs_controls | [5 empty] | 200 | 20 | 98
P control Mode |  | G8.1.1 | Holding Register |  | 1 |  |  |  |  | 550 | 40551 | bit_field |  |  | p_control_mode | [11 empty] | /components/pcs_controls | pcs_p_control_mode | Yes
P control Mode = I |  | G8.1.1.0 | Holding Register |  | 1 |  |  |  |  | 550 | 40551 | bit | 0 |  | bit_p_mode_i | [11 empty] | /components/pcs_controls | pcs_bit_p_mode_i | Yes
P control mode = P |  | G8.1.1.1 | Holding Register |  | 1 |  |  |  |  | 550 | 40551 | bit | 1 |  | bit_p_mode_p | [11 empty] | /components/pcs_controls | pcs_bit_p_mode_p | Yes
Q control Mode = Q |  | G8.1.2 | Holding Register |  | 1 |  |  |  |  | 551 | 40552 | bit_field |  |  | q_control_mode | [11 empty] | /components/pcs_controls | pcs_q_control_mode | Yes
Q control Mode = Cos phi |  | G8.1.2.0 | Holding Register |  | 1 |  |  |  |  | 551 | 40552 | bit | 0 |  | bit_q_mode_cosphi | [11 empty] | /components/pcs_controls | pcs_bit_q_mode_cosphi | Yes
Q control Mode = Q |  | G8.1.2.1 | Holding Register |  | 1 |  |  |  |  | 551 | 40552 | bit | 1 |  | bit_q_mode_q | [11 empty] | /components/pcs_controls | pcs_bit_q_mode_q | Yes
Q control Mode = I |  | G8.1.2.2 | Holding Register |  | 1 |  |  |  |  | 551 | 40552 | bit | 2 |  | bit_q_mode_i | [11 empty] | /components/pcs_controls | pcs_bit_q_mode_i | Yes
Q control mode = V/Q |  | G8.1.2.3 | Holding Register |  | 1 |  |  |  |  | 551 | 40552 | bit | 3 |  | bit_q_mode_vq | [11 empty] | /components/pcs_controls | pcs_bit_q_mode_vq | Yes
P reference = 100% |  | G8.1.3.0.0 | Holding Register | % | 1 | 100 |  |  | 0.01 | 552 | 40553 | int16 |  |  | p_p_reference | [11 empty] | /components/pcs_controls | pcs_p_p_reference | Yes
Id reference = 100% |  | G8.1.3.0.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 553 | 40554 | int16 |  |  | p_id_reference | [11 empty] | /components/pcs_controls | pcs_p_id_reference | Yes
Cos phi reference = 1.000 |  | G8.1.4.0 | Holding Register | % | 1 | 1000 |  |  | 0.001 | 555 | 40556 | int16 |  |  | q_cosphi_reference | [11 empty] | /components/pcs_controls | pcs_q_cosphi_reference | Yes
Iq reference = 0 |  | G8.1.4.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 556 | 40557 | int16 |  |  | q_iq_reference | [11 empty] | /components/pcs_controls | pcs_q_iq_reference | Yes
Q reference = 0.0% |  | G8.1.4.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 557 | 40558 | int16 |  |  | q_q_reference | [11 empty] | /components/pcs_controls | pcs_q_q_reference | Yes
Vref = 100.00% |  | G8.1.4.3 | Holding Register | % | 1 | 100 |  |  | 0.01 | 575 | 40576 | int16 |  |  | q_v_reference | [11 empty] | /components/pcs_controls | pcs_q_v_reference | Yes
Excitation |  | G8.1.5.0 | Holding Register |  | 1 |  |  |  |  | 558 | 40559 | bit_field |  |  | excitation | [10 empty] | 0 = cap, 1 = ind | /components/pcs_controls | pcs_excitation | Yes
Excitation = Capacitive |  | G8.1.5.0 | Holding Register |  | 1 |  |  |  |  | 558 | 40559 | bit | 0 |  | bit_excitation_cap | [11 empty] | /components/pcs_controls | pcs_bit_excitation_cap | Yes
Excitation = Inductive |  | G8.1.5.0 | Holding Register |  | 1 |  |  |  |  | 558 | 40559 | bit | 1 |  | bit_excitation_ind | [11 empty] | /components/pcs_controls | pcs_bit_excitation_ind | Yes
V1=90% |  | G8.1.5.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 576 | 40577 | uint16 |  |  | vq_v1 | [11 empty] | /components/pcs_controls | pcs_vq_v1 | Yes
V2 = 92.00% |  | G8.1.6 | Holding Register | % | 1 | 100 |  |  | 0.01 | 577 | 40578 | uint16 |  |  | vq_v2 | [11 empty] | /components/pcs_controls | pcs_vq_v2 | Yes
V3 = 108.00% |  | G8.1.7 | Holding Register | % | 1 | 100 |  |  | 0.01 | 578 | 40579 | uint16 |  |  | vq_v3 | [11 empty] | /components/pcs_controls | pcs_vq_v3 | Yes
V4 = 110.00% |  | G8.1.8 | Holding Register | % | 1 | 100 |  |  | 0.01 | 579 | 40580 | uint16 |  |  | vq_v4 | [11 empty] | /components/pcs_controls | pcs_vq_v4 | Yes
Q1 = 48.43% |  | G8.1.9 | Holding Register | % | 1 | 100 |  |  | 0.01 | 580 | 40581 | uint16 |  |  | vq_q1 | [11 empty] | /components/pcs_controls | pcs_vq_q1 | Yes
Q2 = 0.00% |  | G8.1.10 | Holding Register | % | 1 | 100 |  |  | 0.01 | 581 | 40582 | uint16 |  |  | vq_q2 | [11 empty] | /components/pcs_controls | pcs_vq_q2 | Yes
Q3 = 0.00% |  | G8.1.11 | Holding Register | % | 1 | 100 |  |  | 0.01 | 582 | 40583 | uint16 |  |  | vq_q3 | [11 empty] | /components/pcs_controls | pcs_vq_q3 | Yes
Q4 = 48.43% |  | G8.1.12 | Holding Register | % | 1 | 100 |  |  | 0.01 | 583 | 40584 | uint16 |  |  | vq_q4 | [11 empty] | /components/pcs_controls | pcs_vq_q4 | Yes
V hysterisis = 1.0% |  | G8.1.13 | Holding Register | % | 1 | 10 |  |  | 0.1 | 584 | 40585 | uint16 |  |  | vq_hysterisis | [11 empty] | /components/pcs_controls | pcs_vq_hysterisis | Yes
P activation = 20% |  | G8.1.14 | Holding Register | % | 1 | 10 |  |  | 0.1 | 585 | 40586 | uint16 |  |  | vq_p_activation | [11 empty] | /components/pcs_controls | pcs_vq_p_activation | Yes
P deactivation = 5.0% |  | G8.1.15 | Holding Register | % | 1 | 10 |  |  | 0.1 | 586 | 40587 | uint16 |  |  | vq_p_deactivation | [11 empty] | /components/pcs_controls | pcs_vq_p_deactivation | Yes
Response Tdelay = 0.3 s |  | G8.1.16 | Holding Register | s | 1 | 10 |  |  | 0.1 | 587 | 40588 | uint16 |  |  | vq_response_delay | [11 empty] | /components/pcs_controls | pcs_vq_response_delay | Yes
Response Time = 5.0 s |  | G8.1.17 | Holding Register | s | 1 | 10 |  |  | 0.1 | 588 | 40589 | uint16 |  |  | vq_response_time | [11 empty] | /components/pcs_controls | pcs_vq_response_time | Yes
Q reference 1 = 0.00% |  | G8.1.4a | Holding Register | % | 1 | 100 |  |  | 0.01 | 597 | 40598 | int16 |  |  | q_reference_1 | [11 empty] | /components/pcs_controls | q_reference_1 | Yes
Q reference 2 = 0.00% |  | G8.1.4b | Holding Register | % | 1 | 100 |  |  | 0.01 | 598 | 40599 | int16 |  |  | q_reference_2 | [11 empty] | /components/pcs_controls | q_reference_2 | Yes
Q reference 3 = 0.00% |  | G8.1.4a | Holding Register | % | 1 | 100 |  |  | 0.01 | 599 | 40600 | int16 |  |  | q_reference_3 | [11 empty] | /components/pcs_controls | q_reference_3 | Yes
Control | [15 empty] | pcs_controls | [5 empty] | 200 | 20 | 98
P DC reference 1 = 100% |  | G8.1.3a | Holding Register | % | 1 | 100 |  |  | 0.01 | 7141 | 47142 | int16 |  |  | p_dc_reference_1 | [11 empty] | /components/pcs_controls | pcs_p_dc_reference_1 | Yes
P DC reference 2 = 100% |  | G8.1.3b | Holding Register | % | 1 | 100 |  |  | 0.01 | 7142 | 47143 | int16 |  |  | p_dc_reference_2 | [11 empty] | /components/pcs_controls | pcs_p_dc_reference_2 | Yes
P DC reference 3 = 100% |  | G8.1.3c | Holding Register | % | 1 | 100 |  |  | 0.01 | 7143 | 47144 | int16 |  |  | p_dc_reference_3 | [11 empty] | /components/pcs_controls | pcs_p_dc_reference_3 | Yes
P AC reference 1 = 100% |  | G8.1.3a | Holding Register | % | 1 | 100 |  |  | 0.01 | 7144 | 47145 | int16 |  |  | p_ac_reference_1 | [11 empty] | /components/pcs_controls | pcs_p_ac_reference_1 | Yes
P AC reference 2 = 100% |  | G8.1.3b | Holding Register | % | 1 | 100 |  |  | 0.01 | 7145 | 47146 | int16 |  |  | p_ac_reference_2 | [11 empty] | /components/pcs_controls | pcs_p_ac_reference_2 | Yes
P AC reference 3 = 100% |  | G8.1.3c | Holding Register | % | 1 | 100 |  |  | 0.01 | 7146 | 47147 | int16 |  |  | p_ac_reference_3 | [11 empty] | /components/pcs_controls | pcs_p_ac_reference_3 | Yes
Leak Protection | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
Leak Protection Type |  | G9.2.1 | Holding Register |  | 1 |  |  |  |  | 7150 | 47151 | uint16 |  |  | leak_protection_type_1 | [11 empty] | /components/pcs_controls | pcs_leak_protection_type_1 | Yes
IMI Activation |  | G9.2.1a | Holding Register |  | 1 |  |  |  |  | 7151 | 47152 | uint16 |  |  | leak_imi_activation_1 | [11 empty] | /components/pcs_controls | pcs_leak_imi_activation_1 | Yes
Fault Threshold = 5.0kOhms |  | G9.2.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7152 | 47153 | uint16 |  |  | leak_fault_threshold_1 | [11 empty] | /components/pcs_controls | pcs_leak_fault_threshold_1 | Yes
Fault Recover Threshold = 115% |  | G9.2.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 7153 | 47154 | uint16 |  |  | leak_fault_recover_threshold_1 | [11 empty] | /components/pcs_controls | pcs_leak_fault_recover_threshold_1 | Yes
Warning Theshold=50.0kOhms |  | G9.2.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7154 | 47155 | uint16 |  |  | leak_warning_theshold_1 | [11 empty] | /components/pcs_controls | pcs_leak_warning_theshold_1 | Yes
Self Test exec per = 1440 |  | G9.2.7 | Holding Register |  | 1 | 1 |  |  | 1 | 7157 | 47158 | uint16 |  |  | leak_self_test_exec_period_1 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_exec_period_1 | Yes
Self Test Manual Command |  | G9.2.8 | Holding Register |  | 1 | 1 |  |  | 1 | 7158 | 47159 | uint16 |  |  | leak_self_test_manual_command_1 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_manual_command_1 | Yes
Leak Protection Type |  | G9.3.1 | Holding Register |  | 1 |  |  |  |  | 7160 | 47161 | uint16 |  |  | leak_protection_type_2 | [11 empty] | /components/pcs_controls | pcs_leak_protection_type_2 | Yes
IMI Activation |  | G9.3.1a | Holding Register |  | 1 |  |  |  |  | 7161 | 47162 | uint16 |  |  | leak_imi_activation_2 | [11 empty] | /components/pcs_controls | pcs_leak_imi_activation_2 | Yes
Fault Threshold = 5.0kOhms |  | G9.3.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7162 | 47163 | uint16 |  |  | leak_fault_threshold_2 | [11 empty] | /components/pcs_controls | pcs_leak_fault_threshold_2 | Yes
Fault Recover Threshold = 115% |  | G9.3.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 7163 | 47164 | uint16 |  |  | leak_fault_recover_threshold_2 | [11 empty] | /components/pcs_controls | pcs_leak_fault_recover_threshold_2 | Yes
Warning Theshold=50.0kOhms |  | G9.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7164 | 47165 | uint16 |  |  | leak_warning_theshold_2 | [11 empty] | /components/pcs_controls | pcs_leak_warning_theshold_2 | Yes
Self Test exec per = 1440 |  | G9.3.7 | Holding Register |  | 1 | 1 |  |  | 1 | 7167 | 47168 | uint16 |  |  | leak_self_test_exec_period_2 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_exec_period_2 | Yes
Self Test Manual Command |  | G9.3.8 | Holding Register |  | 1 | 1 |  |  | 1 | 7168 | 47169 | uint16 |  |  | leak_self_test_manual_command_2 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_manual_command_2 | Yes
Leak Protection Type |  | G9.4.1 | Holding Register |  | 1 |  |  |  |  | 7170 | 47171 | uint16 |  |  | leak_protection_type_3 | [11 empty] | /components/pcs_controls | pcs_leak_protection_type_3 | Yes
IMI Activation |  | G9.4.1a | Holding Register |  | 1 |  |  |  |  | 7171 | 47172 | uint16 |  |  | leak_imi_activation_3 | [11 empty] | /components/pcs_controls | pcs_leak_imi_activation_3 | Yes
Fault Threshold = 5.0kOhms |  | G9.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7172 | 47173 | uint16 |  |  | leak_fault_threshold_3 | [11 empty] | /components/pcs_controls | pcs_leak_fault_threshold_3 | Yes
Fault Recover Threshold = 115% |  | G9.4.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 7173 | 47174 | uint16 |  |  | leak_fault_recover_threshold_3 | [11 empty] | /components/pcs_controls | pcs_leak_fault_recover_threshold_3 | Yes
Warning Theshold=50.0kOhms |  | G9.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7174 | 47175 | uint16 |  |  | leak_warning_theshold_3 | [11 empty] | /components/pcs_controls | pcs_leak_warning_theshold_3 | Yes
Self Test exec per = 1440 |  | G9.4.7 | Holding Register |  | 1 | 1 |  |  | 1 | 7177 | 47178 | uint16 |  |  | leak_self_test_exec_period_3 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_exec_period_3 | Yes
Self Test Manual Command |  | G9.4.8 | Holding Register |  | 1 | 1 |  |  | 1 | 7178 | 47179 | uint16 |  |  | leak_self_test_manual_command_3 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_manual_command_3 | Yes
DU Configuration | [15 empty] | pcs_controls | [5 empty] | 200 | 20 | 98
Du Type = HEM |  | G10.1 | Holding Register |  | 1 | 1 |  |  | 1 | 649 | 40650 | uint16 |  |  | du_type | [11 empty] | /components/pcs_controls | pcs_du_type | Yes
Working Mode = GFDI + IMI |  | G10.2 | Holding Register |  | 1 | 1 |  |  | 1 | 650 | 40651 | uint16 |  |  | working_mode | [11 empty] | /components/pcs_controls | pcs_working_mode | Yes
Enabled NEC = NEC 2017 |  | G10.2b | Holding Register |  | 1 | 1 |  |  | 1 | 648 | 40649 | uint16 |  |  | enabled_nec | [11 empty] | /components/pcs_controls | pcs_enabled_nec | Yes
Battery Configuration | [15 empty] | pcs_controls | [5 empty] | 500 | 20 | 98
Battery Module Model |  | G15.1.1 | Holding Register |  | 1 | 1 |  |  | 1 | 7050 | 47051 | uint16 |  |  | battery_module_model | [11 empty] | /components/pcs_controls | pcs_battery_module_model | Yes
BMS Banks Enabled |  | G15.1.2 | Holding Register |  | 1 | 1 |  |  | 1 | 7051 | 47052 | uint16 |  |  | bms_banks_enabled | [11 empty] | /components/pcs_controls | pcs_bms_banks_enabled | Yes
Grid Visualization | [15 empty] | pcs_info | [5 empty] | 200 | 20 | 98
Grid voltage RS |  | SV1.1 | Input Register |  | 1 | 1 |  |  | 1 | 1000 | 41001 | uint16 |  |  | grid_voltage_rs | [11 empty] | /components/pcs_info | pcs_grid_voltage_rs | Yes | Real value = (Modbus value / 10)
Grid voltage ST |  | SV1.2 | Input Register |  | 1 | 1 |  |  | 1 | 1001 | 41002 | uint16 |  |  | grid_voltage_st | [11 empty] | /components/pcs_info | pcs_grid_voltage_st | Yes | Real value = (Modbus value / 10)
Grid voltage TR |  | SV1.3 | Input Register |  | 1 | 1 |  |  | 1 | 1002 | 41003 | uint16 |  |  | grid_voltage_tr | [11 empty] | /components/pcs_info | pcs_grid_voltage_tr | Yes | Real value = (Modbus value / 10)
Grid current I1 |  | SV1.4 | Input Register |  | 1 | 1 |  |  | 1 | 1003 | 41004 | int16 |  |  | grid_current_1 | [11 empty] | /components/pcs_info | pcs_grid_current_1 | Yes | Real value = (Modbus value / 10)
Grid current I2 |  | SV1.5 | Input Register |  | 1 | 1 |  |  | 1 | 1004 | 41005 | int16 |  |  | grid_current_2 | [11 empty] | /components/pcs_info | pcs_grid_current_2 | Yes | Real value = (Modbus value / 10)
Grid current I3 |  | SV1.6 | Input Register |  | 1 | 1 |  |  | 1 | 1005 | 41006 | int16 |  |  | grid_current_3 | [11 empty] | /components/pcs_info | pcs_grid_current_3 | Yes | Real value = (Modbus value / 10)
P |  | SV1.7 | Input Register |  | 1 |  |  |  |  | 1007 | 41008 | int16 |  |  | active_power | [11 empty] | /components/pcs_info | pcs_active_power | Yes | Real value = Modbus value
Q |  | SV1.8 | Input Register |  | 1 |  |  |  |  | 1008 | 41009 | int16 |  |  | reactive_power | [11 empty] | /components/pcs_info | pcs_reactive_power | Yes | Real value = Modbus value
S |  | SV1.9 | Input Register |  | 1 |  |  |  |  | 1009 | 41010 | int16 |  |  | apparent_power | [11 empty] | /components/pcs_info | pcs_apparent_power | Yes | Real value = Modbus value
Cos phi |  | SV1.10 | Input Register |  | 1 | 1000 |  |  | 0.001 | 1010 | 41011 | int16 |  |  | cosphi | [11 empty] | /components/pcs_info | pcs_cosphi | Yes | Real value = (Modbus value / 1000)
Grid frequency |  | SV1.11 | Input Register |  | 1 | 1000 |  |  | 0.001 | 1011 | 41012 | uint16 |  |  | grid_frequency | [11 empty] | /components/pcs_info | pcs_grid_frequency | Yes | Real value = (Modbus value / 100)
POI V estimated |  | SV1.13 | Input Register |  | 1 |  |  |  |  | 1013 | 41014 | uint16 |  |  | poi_v_est | [11 empty] | /components/pcs_info | pcs_poi_v_est | Yes | Real value = Modbus value
DC Inputs | [15 empty] | pcs_info | [5 empty] | 200 | 20 | 98
DC Voltage Bus 1 |  | SV2.1.1 | Input Register |  | 1 |  |  |  |  | 7400 | 47401 | uint16 |  |  | vdc_bus_1 | [11 empty] | /components/pcs_info | pcs_vdc_bus_1 | Yes | Real value = Modbus value
DC Voltage Bus 2 |  | SV2.1.2 | Input Register |  | 1 |  |  |  |  | 7401 | 47402 | uint16 |  |  | vdc_bus_2 | [11 empty] | /components/pcs_info | pcs_vdc_bus_2 | Yes | Real value = Modbus value
DC Voltage Bus 3 |  | SV2.1.3 | Input Register |  | 1 |  |  |  |  | 7402 | 47403 | uint16 |  |  | vdc_bus_3 | [11 empty] | /components/pcs_info | pcs_vdc_bus_3 | Yes | Real value = Modbus value
DC voltage last linp |  | SV2.3 | Input Register |  | 1 |  |  |  |  | 1052 | 41053 | uint16 |  |  | vdc_last_linp | [11 empty] | /components/pcs_info | pcs_vdc_last_linp | Yes | Real value = Modbus value
BESS 1 voltage bus |  | SV2.4.1 | Input Register |  | 1 | 10 |  |  | 0.1 | 7403 | 47404 | uint16 |  |  | bess_1_v | [11 empty] | /components/pcs_info | pcs_bess_1_v | Yes | Real value = (Modbus value / 10)
BESS 2 voltage bus |  | SV2.4.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 7404 | 47405 | uint16 |  |  | bess_2_v | [11 empty] | /components/pcs_info | pcs_bess_2_v | Yes | Real value = (Modbus value / 10)
BESS 3 voltage bus |  | SV2.4.3 | Input Register |  | 1 | 10 |  |  | 0.1 | 7405 | 47406 | uint16 |  |  | bess_3_v | [11 empty] | /components/pcs_info | pcs_bess_3_v | Yes | Real value = (Modbus value / 10)
DC input power |  | SV2.5 | Input Register |  | 1 |  |  |  |  | 1060 | 41061 | int16 |  |  | dc_p_input | [11 empty] | /components/pcs_info | pcs_dc_p_input | Yes | Real value = Modbus value
BESS1 DC input power |  | SV2.5a | Input Register |  | 1 |  |  |  |  | 7406 | 47407 | uint16 |  |  | bess_1_p_input | [11 empty] | /components/pcs_info | pcs_bess_1_p_input | Yes | Real value = Modbus value
BESS2 DC input power |  | SV2.5b | Input Register |  | 1 |  |  |  |  | 7407 | 47408 | uint16 |  |  | bess_2_p_input | [11 empty] | /components/pcs_info | pcs_bess_2_p_input | Yes | Real value = Modbus value
BESS3 DC input power |  | SV2.5c | Input Register |  | 1 |  |  |  |  | 7408 | 47409 | uint16 |  |  | bess_3_p_input | [11 empty] | /components/pcs_info | pcs_bess_3_p_input | Yes | Real value = Modbus value
DC input current total |  | SV2.6 | Input Register |  | 1 |  |  |  |  | 1061 | 41062 | int16 |  |  | dc_total_i_input | [11 empty] | /components/pcs_info | pcs_dc_total_i_input | Yes | Real value = Modbus value
DC input current 1 |  | SV2.6a | Input Register |  | 1 |  |  |  |  | 7409 | 47410 | uint16 |  |  | dc_1_i_input | [11 empty] | /components/pcs_info | pcs_dc_1_i_input | Yes | Real value = Modbus value
DC input current 2 |  | SV2.6b | Input Register |  | 1 |  |  |  |  | 7410 | 47411 | uint16 |  |  | dc_2_i_input | [11 empty] | /components/pcs_info | pcs_dc_2_i_input | Yes | Real value = Modbus value
DC input current 3 |  | SV2.6c | Input Register |  | 1 |  |  |  |  | 7411 | 47412 | uint16 |  |  | dc_3_i_input | [11 empty] | /components/pcs_info | pcs_dc_3_i_input | Yes | Real value = Modbus value
Ref current DC BESS1 |  | SV2.8 | Input Register |  | 1 |  |  |  |  | 7412 | 47413 | uint16 |  |  | bess_1_idcref | [11 empty] | /components/pcs_info | pcs_bess_1_idcref | Yes | Real value = Modbus value
Ref current DC BESS2 |  | SV2.9 | Input Register |  | 1 |  |  |  |  | 7413 | 47414 | uint16 |  |  | bess_2_idcref | [11 empty] | /components/pcs_info | pcs_bess_2_idcref | Yes | Real value = Modbus value
Ref current DC BESS3 |  | SV2.10 | Input Register |  | 1 |  |  |  |  | 7414 | 47415 | uint16 |  |  | bess_3_idcref | [11 empty] | /components/pcs_info | pcs_bess_3_idcref | Yes | Real value = Modbus value
Insulation Monitoring | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
Insulation Status |  | SV3.2.1 | Input Register |  | 1 |  |  |  |  | 1102 | 41103 | uint16 |  |  | insulation_status_1 | [11 empty] | /components/pcs_info | pcs_insulation_status_1 | Yes | Real value = Modbus value
Insulation Resistor MSB |  | SV3.2.2a | Input Register |  | 1 |  |  |  |  | 1103 | 41104 | uint16 |  |  | insulation_resistor_msb_1 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_msb_1 | Yes | – MSB
Resistor LSB |  | SV3.2.2b | Input Register |  | 1 |  |  |  |  | 1104 | 41105 | uint16 |  |  | insulation_resistor_lsb_1 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_lsb_1 | Yes | – MSB
Insulation Measurement started time |  | SV3.2.3 | Input Register |  | 1 |  |  |  |  | 1105 | 41106 | uint16 |  |  | insulation_measurement_started_time_1 | [11 empty] | /components/pcs_info | pcs_insulation_measurement_started_time_1 | Yes | Real value = Modbus value
Insulation Self-test started time |  | SV3.2.4 | Input Register |  | 1 |  |  |  |  | 1106 | 41107 | uint16 |  |  | insulation_self_test_started_time_1 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_started_time_1 | Yes | Real value = Modbus value
Insulation Self-test exec countdown |  | SV3.2.5 | Input Register |  | 1 |  |  |  |  | 1107 | 41108 | uint16 |  |  | insulation_self_test_exec_countdown_1 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_exec_countdown_1 | Yes | Real value = Modbus value
Insulation Status update |  | SV3.2.6 | Input Register |  | 1 |  |  |  |  | 1108 | 41109 | uint16 |  |  | insulation_status_update_1 | [11 empty] | /components/pcs_info | pcs_insulation_status_update_1 | Yes | Real value = Modbus value
Insulation Status |  | SV3.3.1 | Input Register |  | 1 |  |  |  |  | 7482 | 47483 | uint16 |  |  | insulation_status_2 | [11 empty] | /components/pcs_info | pcs_insulation_status_2 | Yes | Real value = Modbus value
Insulation Resistor MSB |  | SV3.3.2a | Input Register |  | 1 |  |  |  |  | 7483 | 47484 | uint16 |  |  | insulation_resistor_msb_2 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_msb_2 | Yes
Resistor LSB |  | SV3.3.2b | Input Register |  | 1 |  |  |  |  | 7484 | 47485 | uint16 |  |  | insulation_resistor_lsb_2 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_lsb_2 | Yes | Real value = Modbus value
Insulation Measurement started time |  | SV3.3.3 | Input Register |  | 1 |  |  |  |  | 7485 | 47486 | uint16 |  |  | insulation_measurement_started_time_2 | [11 empty] | /components/pcs_info | pcs_insulation_measurement_started_time_2 | Yes | Real value = Modbus value
Insulation Self-test started time |  | SV3.3.4 | Input Register |  | 1 |  |  |  |  | 7486 | 47487 | uint16 |  |  | insulation_self_test_started_time_2 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_started_time_2 | Yes | Real value = Modbus value
Insulation Self-test exec countdown |  | SV3.3.5 | Input Register |  | 1 |  |  |  |  | 7487 | 47488 | uint16 |  |  | insulation_self_test_exec_countdown_2 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_exec_countdown_2 | Yes | Real value = Modbus value
Insulation Status update |  | SV3.3.6 | Input Register |  | 1 |  |  |  |  | 7488 | 47489 | uint16 |  |  | insulation_status_update_2 | [11 empty] | /components/pcs_info | pcs_insulation_status_update_2 | Yes | Real value = Modbus value
Insulation Status |  | SV3.4.1 | Input Register |  | 1 |  |  |  |  | 7491 | 47492 | uint16 |  |  | insulation_status_3 | [11 empty] | /components/pcs_info | pcs_insulation_status_3 | Yes | Real value = Modbus value
Insulation Resistor MSB |  | SV3.4.2a | Input Register |  | 1 |  |  |  |  | 7492 | 47493 | uint16 |  |  | insulation_resistor_msb_3 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_msb_3 | Yes
Resistor LSB |  | SV3.4.2b | Input Register |  | 1 |  |  |  |  | 7493 | 47494 | uint16 |  |  | insulation_resistor_lsb_3 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_lsb_3 | Yes | Real value = Modbus value
Insulation Measurement started time |  | SV3.4.3 | Input Register |  | 1 |  |  |  |  | 7494 | 47495 | uint16 |  |  | insulation_measurement_started_time_3 | [11 empty] | /components/pcs_info | pcs_insulation_measurement_started_time_3 | Yes | Real value = Modbus value
Insulation Self-test started time |  | SV3.4.4 | Input Register |  | 1 |  |  |  |  | 7495 | 47496 | uint16 |  |  | insulation_self_test_started_time_3 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_started_time_3 | Yes | Real value = Modbus value
Insulation Self-test exec countdown |  | SV3.4.5 | Input Register |  | 1 |  |  |  |  | 7496 | 47497 | uint16 |  |  | insulation_self_test_exec_countdown_3 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_exec_countdown_3 | Yes | Real value = Modbus value
Insulation Status update |  | SV3.4.6 | Input Register |  | 1 |  |  |  |  | 7497 | 47498 | uint16 |  |  | insulation_status_update_3 | [11 empty] | /components/pcs_info | pcs_insulation_status_update_3 | Yes | Real value = Modbus value
Internal Visualization | [15 empty] | pcs_info | [5 empty] | 200 | 20 | 98
Current fault |  | SV4.1.1 | Input Register |  | 1 |  |  |  |  | 1120 | 41121 | uint16 |  |  | current_fault | [11 empty] | /components/pcs_info | pcs_current_fault | Yes | Real value = Modbus value
Current fault module |  | SV4.1.1b | Input Register |  | 1 |  |  |  |  | 1130 | 41131 | uint16 |  |  | current_fault_module | [11 empty] | /components/pcs_info | pcs_current_fault_module | Yes | Real value = Modbus value
Current warning |  | SV4.1.2 | Input Register |  | 1 |  |  |  |  | 1121 | 41122 | uint16 |  |  | current_warning | [11 empty] | /components/pcs_info | pcs_current_warning | Yes | Real value = Modbus value
Current status |  | SV4.1.3 | Input Register |  | 1 |  |  |  |  | 1122 | 41123 | uint16 |  |  | current_status | [11 empty] | /components/pcs_info | pcs_current_status | Yes | Real value = Modbus value
Internal temperature |  | SV4.1.4 | Input Register |  | 1 |  |  |  |  | 1123 | 41124 | uint16 |  |  | internal_temperature | [11 empty] | /components/pcs_info | pcs_internal_temperature | Yes | Real value = Modbus value
Max IGBTs temperature |  | SV4.1.5 | Input Register |  | 1 |  |  |  |  | 1124 | 41125 | uint16 |  |  | max_igbts_temperature | [11 empty] | /components/pcs_info | pcs_max_igbts_temperature | Yes | Real value = Modbus value
Max modules temperature |  | SV4.1.6 | Input Register |  | 1 |  |  |  |  | 1125 | 41126 | uint16 |  |  | max_modules_temperature | [11 empty] | /components/pcs_info | pcs_max_modules_temperature | Yes | Real value = Modbus value
Internal input status |  | SV4.1.7 | Input Register |  | 1 |  |  |  |  | 1126 | 41127 | uint16 |  |  | internal_input_status | [11 empty] | /components/pcs_info | pcs_internal_input_status | Yes | Real value = Modbus value
Internal output status |  | SV4.1.8 | Input Register |  | 1 |  |  |  |  | 1127 | 41128 | uint16 |  |  | internal_output_status | [11 empty] | /components/pcs_info | pcs_internal_output_status | Yes | Real value = Modbus value
AC module admission temperature |  | SV4.1.9 | Input Register |  | 1 | 10 |  |  | 0.1 | 1128 | 41129 | uint16 |  |  | ac_module_admission_temperature | [11 empty] | /components/pcs_info | pcs_ac_module_admission_temperature | Yes | Real value = (Modbus value / 10)
Current normative |  | SV4.1.10 | Input Register |  | 1 |  |  |  |  | 1129 | 41130 | uint16 |  |  | current_normative | [11 empty] | /components/pcs_info | pcs_current_normative | Yes | Real value = Modbus value
Internal humidity |  | SV4.1.11 | Input Register |  | 1 |  |  |  |  | 1131 | 41132 | uint16 |  |  | internal_humidity | [11 empty] | /components/pcs_info | pcs_internal_humidity | Yes | Real value = Modbus value
LV manometer |  | SV4.1.12 | Input Register |  | 1 |  |  |  |  | 1132 | 41133 | uint16 |  |  | lv_manometer | [11 empty] | /components/pcs_info | pcs_lv_manometer | Yes | Real value = Modbus value
Power source 1 |  | SV4.1.14 | Input Register |  | 1 | 100 |  |  | 0.01 | 1134 | 41135 | uint16 |  |  | power_source_1 | [11 empty] | /components/pcs_info | pcs_power_source_1 | Yes | Real value = (Modbus value / 100)
Power source 2 |  | SV4.1.15 | Input Register |  | 1 | 100 |  |  | 0.01 | 1135 | 41136 | uint16 |  |  | power_source_2 | [11 empty] | /components/pcs_info | pcs_power_source_2 | Yes | Real value = (Modbus value / 100)
P limit inst |  | SV4.2.1 | Input Register |  | 1 | 10000 |  |  | 0.0001 | 1140 | 41141 | uint16 |  |  | p_limit_inst | [11 empty] | /components/pcs_info | pcs_p_limit_inst | Yes | Real value = (Modbus value / 10000)
Q limit inst |  | SV4.2.2 | Input Register |  | 1 | 10000 |  |  | 0.0001 | 1141 | 41142 | uint16 |  |  | q_limit_inst | [11 empty] | /components/pcs_info | pcs_q_limit_inst | Yes | Real value = (Modbus value / 10000)
Start conditions all |  | SV4.3.1 | Input Register |  | 1 |  |  |  |  | 1150 | 41151 | uint16 |  |  | start_conditions_all | [11 empty] | /components/pcs_info | pcs_start_conditions_all | Yes | Real value = Modbus value
Start conditions V |  | SV4.3.2 | Input Register |  | 1 |  |  |  |  | 1151 | 41152 | uint16 |  |  | start_conditions_v | [11 empty] | /components/pcs_info | pcs_start_conditions_v | Yes | Real value = Modbus value
Start conditions f |  | SV4.3.3 | Input Register |  | 1 |  |  |  |  | 1152 | 41153 | uint16 |  |  | start_conditions_f | [11 empty] | /components/pcs_info | pcs_start_conditions_f | Yes | Real value = Modbus value
Start conditions Vdc |  | SV4.3.4 | Input Register |  | 1 |  |  |  |  | 1153 | 41154 | uint16 |  |  | start_conditions_vdc | [11 empty] | /components/pcs_info | pcs_start_conditions_vdc | Yes | Real value = Modbus value
Start conditions P |  | SV4.3.6 | Input Register |  | 1 |  |  |  |  | 1155 | 41156 | uint16 |  |  | start_conditions_p | [11 empty] | /components/pcs_info | pcs_start_conditions_p | Yes | Real value = Modbus value
Start conditions SOC = No |  | SV4.3.7 | Input Register |  | 1 |  |  |  |  | 1156 | 41157 | uint16 |  |  | start_conditions_soc_no | [11 empty] | /components/pcs_info | pcs_start_conditions_soc_no | Yes | Real value = Modbus value
Inverter type |  | SV4.4.1.1 | Input Register |  | 1 |  |  |  |  | 1182 | 41183 | uint16 |  |  | inverter_type | [11 empty] | /components/pcs_info | pcs_inverter_type | Yes | Real value = Modbus value
Nominal AC voltage |  | SV4.4.1.2 | Input Register |  | 1 |  |  |  |  | 1160 | 41161 | uint16 |  |  | nominal_ac_voltage | [11 empty] | /components/pcs_info | pcs_nominal_ac_voltage | Yes | Real value = Modbus value
Nominal S |  | SV4.4.1.3 | Input Register |  | 1 | 100 |  |  | 0.01 | 1164 | 41165 | uint16 |  |  | nominal_s | [11 empty] | /components/pcs_info | pcs_nominal_s | Yes | Real value = (Modbus value / 100)
Number of modules |  | SV4.4.1.4 | Input Register |  | 1 |  |  |  |  | 1165 | 41166 | uint16 |  |  | number_of_modules | [11 empty] | /components/pcs_info | pcs_number_of_modules | Yes | Real value = Modbus value
Number of BUS = 2 |  | SV4.4.1.4a | Input Register |  | 1 |  |  |  |  | 1169 | 41170 | uint16 |  |  | number_of_bus | [11 empty] | /components/pcs_info | pcs_number_of_bus | Yes | Real value = Modbus value
Number of MPPs |  | SV4.4.1.5 | Input Register |  | 1 |  |  |  |  | 1166 | 41167 | uint16 |  |  | number_of_mpps | [11 empty] | /components/pcs_info | pcs_number_of_mpps | Yes | Real value = Modbus value
Nominal bus voltage |  | SV4.4.1.6 | Input Register |  | 1 |  |  |  |  | 1162 | 41163 | uint16 |  |  | nominal_bus_voltage | [11 empty] | /components/pcs_info | pcs_nominal_bus_voltage | Yes | Real value = Modbus value
Max AC current |  | SV4.4.1.7 | Input Register |  | 1 |  |  |  |  | 1161 | 41162 | uint16 |  |  | max_ac_current | [11 empty] | /components/pcs_info | pcs_max_ac_current | Yes | Real value = Modbus value
Max DC current |  | SV4.4.1.8 | Input Register |  | 1 |  |  |  |  | 1163 | 41164 | uint16 |  |  | max_dc_current | [11 empty] | /components/pcs_info | pcs_max_dc_current | Yes | Real value = Modbus value
Inductive I limit |  | SV4.4.3.1 | Input Register |  | 1 |  |  |  |  | 1183 | 41184 | uint16 |  |  | inductive_i_limit | [11 empty] | /components/pcs_info | pcs_inductive_i_limit | Yes | Real value = Modbus value
Capacitive I limit |  | SV4.4.3.2 | Input Register |  | 1 |  |  |  |  | 1184 | 41185 | uint16 |  |  | capacitive_i_limit | [11 empty] | /components/pcs_info | pcs_capacitive_i_limit | Yes | Real value = Modbus value
Max P limit |  | SV4.4.3.3 | Input Register |  | 1 | 100 |  |  | 0.01 | 1185 | 41186 | uint16 |  |  | max_p_limit | [11 empty] | /components/pcs_info | pcs_max_p_limit | Yes | Real value = (Modbus value / 100)
Max Q limit |  | SV4.4.3.4 | Input Register |  | 1 | 100 |  |  | 0.01 | 1186 | 41187 | uint16 |  |  | max_q_limit | [11 empty] | /components/pcs_info | pcs_max_q_limit | Yes | Real value = (Modbus value / 100)
Max S limit |  | SV4.4.3.5 | Input Register |  | 1 | 100 |  |  | 0.01 | 1187 | 41188 | uint16 |  |  | max_s_limit | [11 empty] | /components/pcs_info | pcs_max_s_limit | Yes | Real value = (Modbus value / 100)
R (mOhm) |  | SV4.4.5.1 | Input Register |  | 1 | 100 |  |  | 0.01 | 1145 | 41146 | uint16 |  |  | r_mohm | [11 empty] | /components/pcs_info | pcs_r_mohm | Yes | Real value = (Modbus value / 100)
L (uH) |  | SV4.4.5.2 | Input Register |  | 1 |  |  |  |  | 1146 | 41147 | uint16 |  |  | l_uh | [11 empty] | /components/pcs_info | pcs_l_uh | Yes | Real value = Modbus value
C (uF) |  | SV4.4.5.3 | Input Register |  | 1 | 100 |  |  | 0.01 | 1147 | 41148 | uint16 |  |  | c_uf | [11 empty] | /components/pcs_info | pcs_c_uf | Yes | Real value = (Modbus value / 100)
Lc (uH) |  | SV4.4.5.4 | Input Register |  | 1 | 100 |  |  | 0.01 | 1148 | 41149 | uint16 |  |  | lc_uh | [11 empty] | /components/pcs_info | pcs_lc_uh | Yes | Real value = (Modbus value / 100)
Counters | [15 empty] | pcs_info | [5 empty] | 2000 | 20 | 98
Select module |  | SV5.1.1 | Input Register |  | 1 |  |  |  |  | 1200 | 41201 | uint16 |  |  | select_module | [11 empty] | /components/pcs_info | pcs_select_module | Yes | Real value = Modbus value
Daily energy MSB |  | SV5.1.2 | Input Register |  | 1 |  |  |  |  | 1201 | 41202 | uint16 |  |  | daily_energy_msb | [11 empty] | /components/pcs_info | pcs_daily_energy_msb | Yes | – MSB
Daily energy LSB |  | SV5.1.2 | Input Register |  | 1 |  |  |  |  | 1202 | 41203 | uint16 |  |  | daily_energy_lsb | [11 empty] | /components/pcs_info | pcs_daily_energy_lsb | Yes | – LSB Real value = Modbus value
Yesterday energy MSB |  | SV5.1.3 | Input Register |  | 1 |  |  |  |  | 1203 | 41204 | uint16 |  |  | yesterday_energy_msb | [11 empty] | /components/pcs_info | pcs_yesterday_energy_msb | Yes | – MSB
Yesterday energy LSB |  | SV5.1.3 | Input Register |  | 1 |  |  |  |  | 1204 | 41205 | uint16 |  |  | yesterday_energy_lsb | [11 empty] | /components/pcs_info | pcs_yesterday_energy_lsb | Yes | – LSB Real value = Modbus value
Current month energy MSB |  | SV5.1.4 | Input Register |  | 1 |  |  |  |  | 1205 | 41206 | uint16 |  |  | current_month_energy_msb | [11 empty] | /components/pcs_info | pcs_current_month_energy_msb | Yes | – MSB
Current month energy LSB |  | SV5.1.4 | Input Register |  | 1 |  |  |  |  | 1206 | 41207 | uint16 |  |  | current_month_energy_lsb | [11 empty] | /components/pcs_info | pcs_current_month_energy_lsb | Yes | – LSB Real value = Modbus value
Last month energy MSB |  | SV5.1.5 | Input Register |  | 1 |  |  |  |  | 1207 | 41208 | uint16 |  |  | last_month_energy_msb | [11 empty] | /components/pcs_info | pcs_last_month_energy_msb | Yes | – MSB
Last month energy LSB |  | SV5.1.5 | Input Register |  | 1 |  |  |  |  | 1208 | 41209 | uint16 |  |  | last_month_energy_lsb | [11 empty] | /components/pcs_info | pcs_last_month_energy_lsb | Yes | – LSB Real value = Modbus value
Total energy MSB |  | SV5.1.6 | Input Register |  | 1 |  |  |  |  | 1209 | 41210 | uint16 |  |  | total_energy_msb | [11 empty] | /components/pcs_info | pcs_total_energy_msb | Yes | – MSB
Total energy LSB |  | SV5.1.6 | Input Register |  | 1 |  |  |  |  | 1210 | 41211 | uint16 |  |  | total_energy_lsb | [11 empty] | /components/pcs_info | pcs_total_energy_lsb | Yes | – LSB Real value = Modbus value
Consum. daily energy MSB |  | SV5.1.7 | Input Register |  | 1 |  |  |  |  | 1230 | 41231 | uint16 |  |  | consum_daily_energy_msb | [11 empty] | /components/pcs_info | pcs_consum_daily_energy_msb | Yes | – MSB
Consum. daily energy LSB |  | SV5.1.7 | Input Register |  | 1 |  |  |  |  | 1231 | 41232 | uint16 |  |  | consum_daily_energy_lsb | [11 empty] | /components/pcs_info | pcs_consum_daily_energy_lsb | Yes | – LSB Real value = Modbus value
Consum. total energy MSB |  | SV5.1.8 | Input Register |  | 1 |  |  |  |  | 1232 | 41233 | uint16 |  |  | consum_total_energy_msb | [11 empty] | /components/pcs_info | pcs_consum_total_energy_msb | Yes | – MSB
Consum. total energy LSB |  | SV5.1.8 | Input Register |  | 1 |  |  |  |  | 1233 | 41234 | uint16 |  |  | consum_total_energy_lsb | [11 empty] | /components/pcs_info | pcs_consum_total_energy_lsb | Yes | – LSB Real value = Modbus value
Select module reactive energy |  | SV5.2.1 | Input Register |  | 1 |  |  |  |  | 1211 | 41212 | uint16 |  |  | select_module_reactive_energy | [11 empty] | /components/pcs_info | pcs_select_module_reactive_energy | Yes | Real value = Modbus value
Daily reactive energy MSB |  | SV5.2.2 | Input Register |  | 1 |  |  |  |  | 1212 | 41213 | uint16 |  |  | daily_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_daily_reactive_energy_msb | Yes | – MSB
Daily reactive energy LSB |  | SV5.2.2 | Input Register |  | 1 |  |  |  |  | 1213 | 41214 | uint16 |  |  | daily_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_daily_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Yesterday reactive energy MSB |  | SV5.2.3 | Input Register |  | 1 |  |  |  |  | 1214 | 41215 | uint16 |  |  | yesterday_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_yesterday_reactive_energy_msb | Yes | – MSB
Yesterday reactive energy LSB |  | SV5.2.3 | Input Register |  | 1 |  |  |  |  | 1215 | 41216 | uint16 |  |  | yesterday_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_yesterday_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Current month reactive energy MSB |  | SV5.2.4 | Input Register |  | 1 |  |  |  |  | 1216 | 41217 | uint16 |  |  | current_month_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_current_month_reactive_energy_msb | Yes | – MSB
Current month reactive energy LSB |  | SV5.2.4 | Input Register |  | 1 |  |  |  |  | 1217 | 41218 | uint16 |  |  | current_month_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_current_month_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Last month reactive energy MSB |  | SV5.2.5 | Input Register |  | 1 |  |  |  |  | 1218 | 41219 | uint16 |  |  | last_month_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_last_month_reactive_energy_msb | Yes | – MSB
Last month reactive energy LSB |  | SV5.2.5 | Input Register |  | 1 |  |  |  |  | 1219 | 41220 | uint16 |  |  | last_month_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_last_month_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Total reactive energy MSB |  | SV5.2.6 | Input Register |  | 1 |  |  |  |  | 1220 | 41221 | uint16 |  |  | total_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_total_reactive_energy_msb | Yes | – MSB
Total reactive energy LSB |  | SV5.2.6 | Input Register |  | 1 |  |  |  |  | 1221 | 41222 | uint16 |  |  | total_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_total_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Total run time years |  | SV5.3.1 | Input Register |  | 1 |  |  |  |  | 1222 | 41223 | uint16 |  |  | total_run_time_years | [11 empty] | /components/pcs_info | pcs_total_run_time_years | Yes | Real value = Modbus value
Total run time days |  | SV5.3.2 | Input Register |  | 1 |  |  |  |  | 1223 | 41224 | uint16 |  |  | total_run_time_days | [11 empty] | /components/pcs_info | pcs_total_run_time_days | Yes | Real value = Modbus value
Total run time hours |  | SV5.3.3 | Input Register |  | 1 |  |  |  |  | 1224 | 41225 | uint16 |  |  | total_run_time_hours | [11 empty] | /components/pcs_info | pcs_total_run_time_hours | Yes | Real value = Modbus value
Partial run time years |  | SV5.3.4 | Input Register |  | 1 |  |  |  |  | 1225 | 41226 | uint16 |  |  | partial_run_time_years | [11 empty] | /components/pcs_info | pcs_partial_run_time_years | Yes | Real value = Modbus value
Partial run time days |  | SV5.3.5 | Input Register |  | 1 |  |  |  |  | 1226 | 41227 | uint16 |  |  | partial_run_time_days | [11 empty] | /components/pcs_info | pcs_partial_run_time_days | Yes | Real value = Modbus value
Partial run time hours |  | SV5.3.6 | Input Register |  | 1 |  |  |  |  | 1227 | 41228 | uint16 |  |  | partial_run_time_hours | [11 empty] | /components/pcs_info | pcs_partial_run_time_hours | Yes | Real value = Modbus value
Total number of grid connections |  | SV5.4.1 | Input Register |  | 1 |  |  |  |  | 1228 | 41229 | uint16 |  |  | total_grid_connections | [11 empty] | /components/pcs_info | pcs_total_grid_connections | Yes | Real value = Modbus value
Partial number of grid connections |  | SV5.4.2 | Input Register |  | 1 |  |  |  |  | 1229 | 41230 | uint16 |  |  | partial_grid_connections | [11 empty] | /components/pcs_info | pcs_partial_grid_connections | Yes | Real value = Modbus value
Fault History | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
Last fault |  | SV6.1 | Input Register |  | 1 |  |  |  |  | 1250 | 41251 | uint16 |  |  | last_fault | [11 empty] | /components/pcs_info | pcs_last_fault | Yes | Real value = Modbus value
Date of last fault |  | SV6.2 | Input Register |  | 1 |  |  |  |  | 1251 | 41252 | uint16 |  |  | last_fault_date | [11 empty] | /components/pcs_info | pcs_last_fault_date | Yes | Day = (Modbus value AND 0xF800) / 2^11
Time of last fault |  |  | Input Register |  | 1 |  |  |  |  | 1252 | 41253 | uint16 |  |  | last_fault_time | [11 empty] | /components/pcs_info | pcs_last_fault_time | Yes | Month = (Modbus value AND 0x0780) / 2^7
9th fault |  | SV6.3 | Input Register |  | 1 |  |  |  |  | 1253 | 41254 | uint16 |  |  | ninth_fault | [11 empty] | /components/pcs_info | pcs_ninth_fault | Yes | Year = (Modbus value AND 0x007F)
Date of 9th fault |  | SV6.4 | Input Register |  | 1 |  |  |  |  | 1254 | 41255 | uint16 |  |  | ninth_fault_date | [11 empty] | /components/pcs_info | pcs_ninth_fault_date | Yes | Hours = (Modbus value AND 0xFF00) / 2^8
Time of 9th fault |  |  | Input Register |  | 1 |  |  |  |  | 1255 | 41256 | uint16 |  |  | ninth_fault_time | [11 empty] | /components/pcs_info | pcs_ninth_fault_time | Yes | Minutes = (Modbus value AND 0x00FF)
8th fault |  | SV6.5 | Input Register |  | 1 |  |  |  |  | 1256 | 41257 | uint16 |  |  | eighth_fault | [11 empty] | /components/pcs_info | pcs_eighth_fault | Yes
Date of 8th fault |  | SV6.6 | Input Register |  | 1 |  |  |  |  | 1257 | 41258 | uint16 |  |  | eighth_fault_date | [11 empty] | /components/pcs_info | pcs_eighth_fault_date | Yes
Time of 8th fault |  |  | Input Register |  | 1 |  |  |  |  | 1258 | 41259 | uint16 |  |  | eighth_fault_time | [11 empty] | /components/pcs_info | pcs_eighth_fault_time | Yes
7th fault |  | SV6.7 | Input Register |  | 1 |  |  |  |  | 1259 | 41260 | uint16 |  |  | seventh_fault | [11 empty] | /components/pcs_info | pcs_seventh_fault | Yes
Date of 7th fault |  | SV6.8 | Input Register |  | 1 |  |  |  |  | 1260 | 41261 | uint16 |  |  | seventh_fault_date | [11 empty] | /components/pcs_info | pcs_seventh_fault_date | Yes
Time of 7th fault |  |  | Input Register |  | 1 |  |  |  |  | 1261 | 41262 | uint16 |  |  | seventh_fault_time | [11 empty] | /components/pcs_info | pcs_seventh_fault_time | Yes
6th fault |  | SV6.9 | Input Register |  | 1 |  |  |  |  | 1262 | 41263 | uint16 |  |  | sixth_fault | [11 empty] | /components/pcs_info | pcs_sixth_fault | Yes
Date of 6th fault |  | SV6.10 | Input Register |  | 1 |  |  |  |  | 1263 | 41264 | uint16 |  |  | sixth_fault_date | [11 empty] | /components/pcs_info | pcs_sixth_fault_date | Yes
Time of 6h fault |  |  | Input Register |  | 1 |  |  |  |  | 1264 | 41265 | uint16 |  |  | sixth_fault_time | [11 empty] | /components/pcs_info | pcs_sixth_fault_time | Yes
5th fault |  | SV6.11 | Input Register |  | 1 |  |  |  |  | 1265 | 41266 | uint16 |  |  | fifth_fault | [11 empty] | /components/pcs_info | pcs_fifth_fault | Yes
Date of 5th fault |  | SV6.12 | Input Register |  | 1 |  |  |  |  | 1266 | 41267 | uint16 |  |  | fifth_fault_date | [11 empty] | /components/pcs_info | pcs_fifth_fault_date | Yes
Time of 5th fault |  |  | Input Register |  | 1 |  |  |  |  | 1267 | 41268 | uint16 |  |  | fifth_fault_time | [11 empty] | /components/pcs_info | pcs_fifth_fault_time | Yes
4th fault |  | SV6.13 | Input Register |  | 1 |  |  |  |  | 1268 | 41269 | uint16 |  |  | fourth_fault | [11 empty] | /components/pcs_info | pcs_fourth_fault | Yes
Date of 4th fault |  | SV6.14 | Input Register |  | 1 |  |  |  |  | 1269 | 41270 | uint16 |  |  | fourth_fault_date | [11 empty] | /components/pcs_info | pcs_fourth_fault_date | Yes
Time of 4th fault |  |  | Input Register |  | 1 |  |  |  |  | 1270 | 41271 | uint16 |  |  | fourth_fault_time | [11 empty] | /components/pcs_info | pcs_fourth_fault_time | Yes
3rd fault |  | SV6.15 | Input Register |  | 1 |  |  |  |  | 1271 | 41272 | uint16 |  |  | third_fault | [11 empty] | /components/pcs_info | pcs_third_fault | Yes
Date of 3rd fault |  | SV6.16 | Input Register |  | 1 |  |  |  |  | 1272 | 41273 | uint16 |  |  | third_fault_date | [11 empty] | /components/pcs_info | pcs_third_fault_date | Yes
Time of 3rd fault |  |  | Input Register |  | 1 |  |  |  |  | 1273 | 41274 | uint16 |  |  | third_fault_time | [11 empty] | /components/pcs_info | pcs_third_fault_time | Yes
2nd fault |  | SV6.17 | Input Register |  | 1 |  |  |  |  | 1274 | 41275 | uint16 |  |  | second_fault | [11 empty] | /components/pcs_info | pcs_second_fault | Yes
Date of 2nd fault |  | SV6.18 | Input Register |  | 1 |  |  |  |  | 1275 | 41276 | uint16 |  |  | second_fault_date | [11 empty] | /components/pcs_info | pcs_second_fault_date | Yes
Time of 2nd fault |  |  | Input Register |  | 1 |  |  |  |  | 1276 | 41277 | uint16 |  |  | second_fault_time | [11 empty] | /components/pcs_info | pcs_second_fault_time | Yes
1st fault |  | SV6.19 | Input Register |  | 1 |  |  |  |  | 1277 | 41278 | uint16 |  |  | first_fault | [11 empty] | /components/pcs_info | pcs_first_fault | Yes
Date of 1st fault |  | SV6.20 | Input Register |  | 1 |  |  |  |  | 1278 | 41279 | uint16 |  |  | first_fault_date | [11 empty] | /components/pcs_info | pcs_first_fault_date | Yes
Time of 1st fault |  |  | Input Register |  | 1 |  |  |  |  | 1279 | 41280 | uint16 |  |  | first_fault_time | [11 empty] | /components/pcs_info | pcs_first_fault_time | Yes
Warning History | [15 empty] | pcs_info | [5 empty] | 2000 | 20 | 98
Last warning |  | SV7.1 | Input Register |  | 1 |  |  |  |  | 1300 | 41301 | uint16 |  |  | last_warning | [11 empty] | /components/pcs_info | pcs_last_warning | Yes | Real value = Modbus value
Date of last warning |  | SV7.2 | Input Register |  | 1 |  |  |  |  | 1301 | 41302 | uint16 |  |  | last_warning_date | [11 empty] | /components/pcs_info | pcs_last_warning_date | Yes | Day = (Modbus value AND 0xF800) / 2^11
Time of last warning |  |  | Input Register |  | 1 |  |  |  |  | 1302 | 41303 | uint16 |  |  | last_warning_time | [11 empty] | /components/pcs_info | pcs_last_warning_time | Yes | Month = (Modbus value AND 0x0780) / 2^7
9th warning |  | SV7.3 | Input Register |  | 1 |  |  |  |  | 1303 | 41304 | uint16 |  |  | ninth_warning | [11 empty] | /components/pcs_info | pcs_ninth_warning | Yes | Year = (Modbus value AND 0x007F)
Date of 9th warning |  | SV7.4 | Input Register |  | 1 |  |  |  |  | 1304 | 41305 | uint16 |  |  | ninth_warning_date | [11 empty] | /components/pcs_info | pcs_ninth_warning_date | Yes | Hours = (Modbus value AND 0xFF00) / 2^8
Time of 9th warning |  |  | Input Register |  | 1 |  |  |  |  | 1305 | 41306 | uint16 |  |  | ninth_warning_time | [11 empty] | /components/pcs_info | pcs_ninth_warning_time | Yes | Minutes = (Modbus value AND 0x00FF)
8th warning |  | SV7.5 | Input Register |  | 1 |  |  |  |  | 1306 | 41307 | uint16 |  |  | eighth_warning | [11 empty] | /components/pcs_info | pcs_eighth_warning | Yes
Date of 8th warning |  | SV7.6 | Input Register |  | 1 |  |  |  |  | 1307 | 41308 | uint16 |  |  | eighth_warning_date | [11 empty] | /components/pcs_info | pcs_eighth_warning_date | Yes
Time of 8th warning |  |  | Input Register |  | 1 |  |  |  |  | 1308 | 41309 | uint16 |  |  | eighth_warning_time | [11 empty] | /components/pcs_info | pcs_eighth_warning_time | Yes
7th warning |  | SV7.7 | Input Register |  | 1 |  |  |  |  | 1309 | 41310 | uint16 |  |  | seventh_warning | [11 empty] | /components/pcs_info | pcs_seventh_warning | Yes
Date of 7th warning |  | SV7.8 | Input Register |  | 1 |  |  |  |  | 1310 | 41311 | uint16 |  |  | seventh_warning_date | [11 empty] | /components/pcs_info | pcs_seventh_warning_date | Yes
Time of 7th warning |  |  | Input Register |  | 1 |  |  |  |  | 1311 | 41312 | uint16 |  |  | seventh_warning_time | [11 empty] | /components/pcs_info | pcs_seventh_warning_time | Yes
6th warning |  | SV7.9 | Input Register |  | 1 |  |  |  |  | 1312 | 41313 | uint16 |  |  | sixth_warning | [11 empty] | /components/pcs_info | pcs_sixth_warning | Yes
Date of 6th warning |  | SV7.10 | Input Register |  | 1 |  |  |  |  | 1313 | 41314 | uint16 |  |  | sixth_warning_date | [11 empty] | /components/pcs_info | pcs_sixth_warning_date | Yes
Time of 6h warning |  |  | Input Register |  | 1 |  |  |  |  | 1314 | 41315 | uint16 |  |  | sixth_warning_time | [11 empty] | /components/pcs_info | pcs_sixth_warning_time | Yes
5th warning |  | SV7.11 | Input Register |  | 1 |  |  |  |  | 1315 | 41316 | uint16 |  |  | fifth_warning | [11 empty] | /components/pcs_info | pcs_fifth_warning | Yes
Date of 5th warning |  | SV7.12 | Input Register |  | 1 |  |  |  |  | 1316 | 41317 | uint16 |  |  | fifth_warning_date | [11 empty] | /components/pcs_info | pcs_fifth_warning_date | Yes
Time of 5th warning |  |  | Input Register |  | 1 |  |  |  |  | 1317 | 41318 | uint16 |  |  | fifth_warning_time | [11 empty] | /components/pcs_info | pcs_fifth_warning_time | Yes
4th warning |  | SV7.13 | Input Register |  | 1 |  |  |  |  | 1318 | 41319 | uint16 |  |  | fourth_warning | [11 empty] | /components/pcs_info | pcs_fourth_warning | Yes
Date of 4th warning |  | SV7.14 | Input Register |  | 1 |  |  |  |  | 1319 | 41320 | uint16 |  |  | fourth_warning_date | [11 empty] | /components/pcs_info | pcs_fourth_warning_date | Yes
Time of 4th warning |  |  | Input Register |  | 1 |  |  |  |  | 1320 | 41321 | uint16 |  |  | fourth_warning_time | [11 empty] | /components/pcs_info | pcs_fourth_warning_time | Yes
3rd warning |  | SV7.15 | Input Register |  | 1 |  |  |  |  | 1321 | 41322 | uint16 |  |  | third_warning | [11 empty] | /components/pcs_info | pcs_third_warning | Yes
Date of 3rd warning |  | SV7.16 | Input Register |  | 1 |  |  |  |  | 1322 | 41323 | uint16 |  |  | third_warning_date | [11 empty] | /components/pcs_info | pcs_third_warning_date | Yes
Time of 3rd warning |  |  | Input Register |  | 1 |  |  |  |  | 1323 | 41324 | uint16 |  |  | third_warning_time | [11 empty] | /components/pcs_info | pcs_third_warning_time | Yes
2nd warning |  | SV7.17 | Input Register |  | 1 |  |  |  |  | 1324 | 41325 | uint16 |  |  | second_warning | [11 empty] | /components/pcs_info | pcs_second_warning | Yes
Date of 2nd warning |  | SV7.18 | Input Register |  | 1 |  |  |  |  | 1325 | 41326 | uint16 |  |  | second_warning_date | [11 empty] | /components/pcs_info | pcs_second_warning_date | Yes
Time of 2nd warning |  |  | Input Register |  | 1 |  |  |  |  | 1326 | 41327 | uint16 |  |  | second_warning_time | [11 empty] | /components/pcs_info | pcs_second_warning_time | Yes
1st warning |  | SV7.19 | Input Register |  | 1 |  |  |  |  | 1327 | 41328 | uint16 |  |  | first_warning | [11 empty] | /components/pcs_info | pcs_first_warning | Yes
Date of 1st warning |  | SV7.20 | Input Register |  | 1 |  |  |  |  | 1328 | 41329 | uint16 |  |  | first_warning_date | [11 empty] | /components/pcs_info | pcs_first_warning_date | Yes
Time of 1st warning |  |  | Input Register |  | 1 |  |  |  |  | 1329 | 41330 | uint16 |  |  | first_warning_time | [11 empty] | /components/pcs_info | pcs_first_warning_time | Yes
Event History | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
Last event |  | SV8.1 | Input Register |  | 1 |  |  |  |  | 1350 | 41351 | uint16 |  |  | last_event | [11 empty] | /components/pcs_info | pcs_last_event | Yes | Real value = Modbus value
Date of last event |  | SV8.2 | Input Register |  | 1 |  |  |  |  | 1351 | 41352 | uint16 |  |  | last_event_date | [11 empty] | /components/pcs_info | pcs_last_event_date | Yes | Day = (Modbus value AND 0xF800) / 2^11
Time of last event |  |  | Input Register |  | 1 |  |  |  |  | 1352 | 41353 | uint16 |  |  | last_event_time | [11 empty] | /components/pcs_info | pcs_last_event_time | Yes | Month = (Modbus value AND 0x0780) / 2^7
9th event |  | SV8.3 | Input Register |  | 1 |  |  |  |  | 1353 | 41354 | uint16 |  |  | ninth_event | [11 empty] | /components/pcs_info | pcs_ninth_event | Yes | Year = (Modbus value AND 0x007F)
Date of 9th event |  | SV8.4 | Input Register |  | 1 |  |  |  |  | 1354 | 41355 | uint16 |  |  | ninth_event_date | [11 empty] | /components/pcs_info | pcs_ninth_event_date | Yes | Hours = (Modbus value AND 0xFF00) / 2^8
Time of 9th event |  |  | Input Register |  | 1 |  |  |  |  | 1355 | 41356 | uint16 |  |  | ninth_event_time | [11 empty] | /components/pcs_info | pcs_ninth_event_time | Yes | Minutes = (Modbus value AND 0x00FF)
8th event |  | SV8.5 | Input Register |  | 1 |  |  |  |  | 1356 | 41357 | uint16 |  |  | eighth_event | [11 empty] | /components/pcs_info | pcs_eighth_event | Yes
Date of 8th event |  | SV8.6 | Input Register |  | 1 |  |  |  |  | 1357 | 41358 | uint16 |  |  | eighth_event_date | [11 empty] | /components/pcs_info | pcs_eighth_event_date | Yes
Time of 8th event |  |  | Input Register |  | 1 |  |  |  |  | 1358 | 41359 | uint16 |  |  | eighth_event_time | [11 empty] | /components/pcs_info | pcs_eighth_event_time | Yes
7th event |  | SV8.7 | Input Register |  | 1 |  |  |  |  | 1359 | 41360 | uint16 |  |  | seventh_event | [11 empty] | /components/pcs_info | pcs_seventh_event | Yes
Date of 7th event |  | SV8.8 | Input Register |  | 1 |  |  |  |  | 1360 | 41361 | uint16 |  |  | seventh_event_date | [11 empty] | /components/pcs_info | pcs_seventh_event_date | Yes
Time of 7th event |  |  | Input Register |  | 1 |  |  |  |  | 1361 | 41362 | uint16 |  |  | seventh_event_time | [11 empty] | /components/pcs_info | pcs_seventh_event_time | Yes
6th event |  | SV8.9 | Input Register |  | 1 |  |  |  |  | 1362 | 41363 | uint16 |  |  | sixth_event | [11 empty] | /components/pcs_info | pcs_sixth_event | Yes
Date of 6th event |  | SV8.10 | Input Register |  | 1 |  |  |  |  | 1363 | 41364 | uint16 |  |  | sixth_event_date | [11 empty] | /components/pcs_info | pcs_sixth_event_date | Yes
Time of 6h event |  |  | Input Register |  | 1 |  |  |  |  | 1364 | 41365 | uint16 |  |  | sixth_event_time | [11 empty] | /components/pcs_info | pcs_sixth_event_time | Yes
5th event |  | SV8.11 | Input Register |  | 1 |  |  |  |  | 1365 | 41366 | uint16 |  |  | fifth_event | [11 empty] | /components/pcs_info | pcs_fifth_event | Yes
Date of 5th event |  | SV8.12 | Input Register |  | 1 |  |  |  |  | 1366 | 41367 | uint16 |  |  | fifth_event_date | [11 empty] | /components/pcs_info | pcs_fifth_event_date | Yes
Time of 5th event |  |  | Input Register |  | 1 |  |  |  |  | 1367 | 41368 | uint16 |  |  | fifth_event_time | [11 empty] | /components/pcs_info | pcs_fifth_event_time | Yes
4th event |  | SV8.13 | Input Register |  | 1 |  |  |  |  | 1368 | 41369 | uint16 |  |  | fourth_event | [11 empty] | /components/pcs_info | pcs_fourth_event | Yes
Date of 4th event |  | SV8.14 | Input Register |  | 1 |  |  |  |  | 1369 | 41370 | uint16 |  |  | fourth_event_date | [11 empty] | /components/pcs_info | pcs_fourth_event_date | Yes
Time of 4th event |  |  | Input Register |  | 1 |  |  |  |  | 1370 | 41371 | uint16 |  |  | fourth_event_time | [11 empty] | /components/pcs_info | pcs_fourth_event_time | Yes
3rd event |  | SV8.15 | Input Register |  | 1 |  |  |  |  | 1371 | 41372 | uint16 |  |  | third_event | [11 empty] | /components/pcs_info | pcs_third_event | Yes
Date of 3rd event |  | SV8.16 | Input Register |  | 1 |  |  |  |  | 1372 | 41373 | uint16 |  |  | third_event_date | [11 empty] | /components/pcs_info | pcs_third_event_date | Yes
Time of 3rd event |  |  | Input Register |  | 1 |  |  |  |  | 1373 | 41374 | uint16 |  |  | third_event_time | [11 empty] | /components/pcs_info | pcs_third_event_time | Yes
2nd event |  | SV8.17 | Input Register |  | 1 |  |  |  |  | 1374 | 41375 | uint16 |  |  | second_event | [11 empty] | /components/pcs_info | pcs_second_event | Yes
Date of 2nd event |  | SV8.18 | Input Register |  | 1 |  |  |  |  | 1375 | 41376 | uint16 |  |  | second_event_date | [11 empty] | /components/pcs_info | pcs_second_event_date | Yes
Time of 2nd event |  |  | Input Register |  | 1 |  |  |  |  | 1376 | 41377 | uint16 |  |  | second_event_time | [11 empty] | /components/pcs_info | pcs_second_event_time | Yes
1st event |  | SV8.19 | Input Register |  | 1 |  |  |  |  | 1377 | 41378 | uint16 |  |  | first_event | [11 empty] | /components/pcs_info | pcs_first_event | Yes
Date of 1st event |  | SV8.20 | Input Register |  | 1 |  |  |  |  | 1378 | 41379 | uint16 |  |  | first_event_date | [11 empty] | /components/pcs_info | pcs_first_event_date | Yes
Time of 1st event |  |  | Input Register |  | 1 |  |  |  |  | 1379 | 41380 | uint16 |  |  | first_event_time | [11 empty] | /components/pcs_info | pcs_first_event_time | Yes
Modules Information | [15 empty] | pcs_info | [5 empty] | 200 | 20 | 98
Running modules |  | SV9.1.1 | Input Register |  | 1 |  |  |  |  | 1390 | 41391 | uint16 |  |  | running_modules | [11 empty] | /components/pcs_info | pcs_running_modules | Yes | Real value = Modbus value
Num running modules |  | SV9.1.2 | Input Register |  | 1 |  |  |  |  | 1391 | 41392 | uint16 |  |  | num_running_modules | [11 empty] | /components/pcs_info | pcs_num_running_modules | Yes | Real value = Modbus value
Next starting module |  | SV9.1.3 | Input Register |  | 1 |  |  |  |  | 1392 | 41393 | uint16 |  |  | next_starting_module | [11 empty] | /components/pcs_info | pcs_next_starting_module | Yes | Real value = Modbus value
Modules start stop |  | SV9.1.4 | Input Register |  | 1 |  |  |  |  | 1393 | 41394 | uint16 |  |  | modules_start_stop | [11 empty] | /components/pcs_info | pcs_modules_start_stop | Yes | Real value = Modbus value
Modules enable reg |  | SV9.1.5 | Input Register |  | 1 |  |  |  |  | 1394 | 41395 | uint16 |  |  | modules_enable_reg | [11 empty] | /components/pcs_info | pcs_modules_enable_reg | Yes | Real value = Modbus value
Selected module |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 1400 | 41401 | uint16 |  |  | selected_module | [11 empty] | /components/pcs_info | pcs_selected_module | Yes | Real value = Modbus value
Module status |  | SV9.3 | Input Register |  | 1 |  |  |  |  | 1401 | 41402 | uint16 |  |  | module_status | [11 empty] | /components/pcs_info | pcs_module_status | Yes | Real value = Modbus value
Current R |  | SV9.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 1402 | 41403 | uint16 |  |  | current_r | [11 empty] | /components/pcs_info | pcs_current_r | Yes | Real value = (Modbus value / 10)
Current S |  | SV9.5 | Input Register |  | 1 | 10 |  |  | 0.1 | 1403 | 41404 | uint16 |  |  | current_s | [11 empty] | /components/pcs_info | pcs_current_s | Yes | Real value = (Modbus value / 10)
Current T |  | SV9.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 1404 | 41405 | uint16 |  |  | current_t | [11 empty] | /components/pcs_info | pcs_current_t | Yes | Real value = (Modbus value / 10)
DC current |  | SV9.7 | Input Register |  | 1 | 10 |  |  | 0.1 | 1405 | 41406 | uint16 |  |  | dc_current | [11 empty] | /components/pcs_info | pcs_dc_current | Yes | Real value = (Modbus value / 10)
DC voltage (P) |  | SV9.8 | Input Register |  | 1 |  |  |  |  | 1406 | 41407 | uint16 |  |  | dc_voltage_p | [11 empty] | /components/pcs_info | pcs_dc_voltage_p | Yes | Real value = Modbus value
DC voltage (N) |  | SV9.9 | Input Register |  | 1 |  |  |  |  | 1407 | 41408 | uint16 |  |  | dc_voltage_n | [11 empty] | /components/pcs_info | pcs_dc_voltage_n | Yes | Real value = Modbus value
DC voltage |  | SV9.10 | Input Register |  | 1 |  |  |  |  | 1408 | 41409 | uint16 |  |  | dc_voltage | [11 empty] | /components/pcs_info | pcs_dc_voltage | Yes | Real value = Modbus value
P |  | SV9.11 | Input Register |  | 1 | 10 |  |  | 0.1 | 1409 | 41410 | uint16 |  |  | p | [11 empty] | /components/pcs_info | pcs_p | Yes | Real value = (Modbus value / 10)
Q |  | SV9.12 | Input Register |  | 1 | 10 |  |  | 0.1 | 1410 | 41411 | uint16 |  |  | q | [11 empty] | /components/pcs_info | pcs_q | Yes | Real value = (Modbus value / 10)
Ambient temperature |  | SV9.13 | Input Register |  | 1 |  |  |  |  | 1411 | 41412 | uint16 |  |  | ambient_temperature | [11 empty] | /components/pcs_info | pcs_ambient_temperature | Yes | Real value = Modbus value
Max temperature |  | SV9.14 | Input Register |  | 1 |  |  |  |  | 1412 | 41413 | uint16 |  |  | max_temperature | [11 empty] | /components/pcs_info | pcs_max_temperature | Yes | Real value = Modbus value
I/O status |  | SV9.15 | Input Register |  | 1 |  |  |  |  | 1413 | 41414 | uint16 |  |  | i_o_status | [11 empty] | /components/pcs_info | pcs_i_o_status | Yes | Real value = Modbus value
Temperature R1 |  | SV9.18 | Input Register |  | 1 |  |  |  |  | 1416 | 41417 | uint16 |  |  | temperature_r1 | [11 empty] | /components/pcs_info | pcs_temperature_r1 | Yes | Real value = Modbus value
Temperature R2 |  | SV9.19 | Input Register |  | 1 |  |  |  |  | 1417 | 41418 | uint16 |  |  | temperature_r2 | [11 empty] | /components/pcs_info | pcs_temperature_r2 | Yes | Real value = Modbus value
Temperature R3 |  | SV9.20 | Input Register |  | 1 |  |  |  |  | 1418 | 41419 | uint16 |  |  | temperature_r3 | [11 empty] | /components/pcs_info | pcs_temperature_r3 | Yes | Real value = Modbus value
Temperature S1 |  | SV9.21 | Input Register |  | 1 |  |  |  |  | 1419 | 41420 | uint16 |  |  | temperature_s1 | [11 empty] | /components/pcs_info | pcs_temperature_s1 | Yes | Real value = Modbus value
Temperature S2 |  | SV9.22 | Input Register |  | 1 |  |  |  |  | 1420 | 41421 | uint16 |  |  | temperature_s2 | [11 empty] | /components/pcs_info | pcs_temperature_s2 | Yes | Real value = Modbus value
Temperature S3 |  | SV9.23 | Input Register |  | 1 |  |  |  |  | 1421 | 41422 | uint16 |  |  | temperature_s3 | [11 empty] | /components/pcs_info | pcs_temperature_s3 | Yes | Real value = Modbus value
Temperature T1 |  | SV9.24 | Input Register |  | 1 |  |  |  |  | 1422 | 41423 | uint16 |  |  | temperature_t1 | [11 empty] | /components/pcs_info | pcs_temperature_t1 | Yes | Real value = Modbus value
Temperature T2 |  | SV9.25 | Input Register |  | 1 |  |  |  |  | 1423 | 41424 | uint16 |  |  | temperature_t2 | [11 empty] | /components/pcs_info | pcs_temperature_t2 | Yes | Real value = Modbus value
Temperature T3 |  | SV9.26 | Input Register |  | 1 |  |  |  |  | 1424 | 41425 | uint16 |  |  | temperature_t3 | [11 empty] | /components/pcs_info | pcs_temperature_t3 | Yes | Real value = Modbus value
DU | [15 empty] | pcs_info | [5 empty] | 200 | 20 | 98
DU Feedback Status |  | SV10.10 | Input Register |  | 1 |  |  |  |  | 7423 | 47424 | uint16 |  |  | du_feedback_status | [11 empty] | /components/pcs_info | pcs_du_feedback_status | Yes | Real value = Modbus value
BMS Summary | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
BMS Status |  | SV15.1.1 | Input Register |  | 1 |  |  |  |  | 7450 | 47451 | uint16 |  |  | bms1_status | [11 empty] | /components/pcs_info | pcs_bms1_status | Yes | Real value = Modbus value
Strings In Service |  | SV15.1.2 | Input Register |  | 1 |  |  |  |  | 7451 | 47452 | uint16 |  |  | bms1_strings_in_service | [11 empty] | /components/pcs_info | pcs_bms1_strings_in_service | Yes | Real value = Modbus value
Total Strings Count |  | SV15.1.3 | Input Register |  | 1 |  |  |  |  | 7452 | 47453 | uint16 |  |  | bms1_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms1_total_strings_count | Yes | Real value = Modbus value
System Voltage |  | SV15.1.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 7453 | 47454 | uint16 |  |  | bms1_system_voltage | [11 empty] | /components/pcs_info | pcs_bms1_system_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV15.1.5 | Input Register |  | 1 |  |  |  |  | 7454 | 47455 | uint16 |  |  | bms1_system_current | [11 empty] | /components/pcs_info | pcs_bms1_system_current | Yes | Real value = Modbus value
System SOC |  | SV15.1.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 7455 | 47456 | uint16 |  |  | bms1_system_soc | [11 empty] | /components/pcs_info | pcs_bms1_system_soc | Yes | Real value = (Modbus value / 10)
BMS Status |  | SV15.2.1 | Input Register |  | 1 |  |  |  |  | 7456 | 47457 | uint16 |  |  | bms2_status | [11 empty] | /components/pcs_info | pcs_bms2_status | Yes | Real value = Modbus value
Strings In Service |  | SV15.2.2 | Input Register |  | 1 |  |  |  |  | 7457 | 47458 | uint16 |  |  | bms2_strings_in_service | [11 empty] | /components/pcs_info | pcs_bms2_strings_in_service | Yes | Real value = Modbus value
Total Strings Count |  | SV15.2.3 | Input Register |  | 1 |  |  |  |  | 7458 | 47459 | uint16 |  |  | bms2_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms2_total_strings_count | Yes | Real value = Modbus value
System Voltage |  | SV15.2.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 7459 | 47460 | uint16 |  |  | bms2_system_voltage | [11 empty] | /components/pcs_info | pcs_bms2_system_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV15.2.5 | Input Register |  | 1 |  |  |  |  | 7460 | 47461 | uint16 |  |  | bms2_system_current | [11 empty] | /components/pcs_info | pcs_bms2_system_current | Yes | Real value = Modbus value
System SOC |  | SV15.2.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 7461 | 47462 | uint16 |  |  | bms2_system_soc | [11 empty] | /components/pcs_info | pcs_bms2_system_soc | Yes | Real value = (Modbus value / 10)
BMS Status |  | SV15.3.1 | Input Register |  | 1 |  |  |  |  | 7462 | 47463 | uint16 |  |  | bms3_status | [11 empty] | /components/pcs_info | pcs_bms3_status | Yes | Real value = Modbus value
Strings In Service |  | SV15.3.2 | Input Register |  | 1 |  |  |  |  | 7463 | 47464 | uint16 |  |  | bms3_strings_in_service | [11 empty] | /components/pcs_info | pcs_bms3_strings_in_service | Yes | Real value = Modbus value
Total Strings Count |  | SV15.3.3 | Input Register |  | 1 |  |  |  |  | 7464 | 47465 | uint16 |  |  | bms3_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms3_total_strings_count | Yes | Real value = Modbus value
System Voltage |  | SV15.3.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 7465 | 47466 | uint16 |  |  | bms3_system_voltage | [11 empty] | /components/pcs_info | pcs_bms3_system_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV15.3.5 | Input Register |  | 1 | 10 |  |  | 0.1 | 7466 | 47467 | uint16 |  |  | bms3_system_current | [11 empty] | /components/pcs_info | pcs_bms3_system_current | Yes | Real value = (Modbus value / 10)
System SOC |  | SV15.3.6 | Input Register |  | 1 |  |  |  |  | 7467 | 47468 | uint16 |  |  | bms3_system_soc | [11 empty] | /components/pcs_info | pcs_bms3_system_soc | Yes | Real value = Modbus value
BMS Information | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
BMS Select |  | SV16.1.1 | Input Register |  | 1 | 10 |  |  | 0.1 | 7500 | 47501 | uint16 |  |  | bms_select | [11 empty] | /components/pcs_info | pcs_bms_select | Yes | Real value = (Modbus value / 10)
Sys heartbeat |  | SV16.1.2 | Input Register |  | 1 |  |  |  |  | 7501 | 47502 | uint16 |  |  | bms_sys_heartbeat | [11 empty] | /components/pcs_info | pcs_bms_sys_heartbeat | Yes | Real value = Modbus value
Strings In Service |  | SV16.1.3 | Input Register |  | 1 |  |  |  |  | 7502 | 47503 | uint16 |  |  | bms_strings_service | [11 empty] | /components/pcs_info | pcs_bms_strings_service | Yes | Real value = Modbus value
Total Strings Count |  | SV16.1.4 | Input Register |  | 1 |  |  |  |  | 7503 | 47504 | uint16 |  |  | bms_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms_total_strings_count | Yes | Real value = Modbus value
Service Voltage |  | SV16.1.5 | Input Register |  | 1 | 10 |  |  | 0.1 | 7504 | 47505 | uint16 |  |  | bms_service_voltage | [11 empty] | /components/pcs_info | pcs_bms_service_voltage | Yes | Real value = (Modbus value / 10)
Service SOC |  | SV16.1.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 7505 | 47506 | uint16 |  |  | bms_service_soc | [11 empty] | /components/pcs_info | pcs_bms_service_soc | Yes | Real value = (Modbus value / 10)
System Voltage |  | SV16.1.7 | Input Register |  | 1 | 10 |  |  | 0.1 | 7506 | 47507 | uint16 |  |  | bms_voltage | [11 empty] | /components/pcs_info | pcs_bms_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV16.1.8 | Input Register |  | 1 |  |  |  |  | 7507 | 47508 | uint16 |  |  | bms_current | [11 empty] | /components/pcs_info | pcs_bms_current | Yes | Real value = Modbus value
System SOC |  | SV16.1.9 | Input Register |  | 1 | 10 |  |  | 0.1 | 7508 | 47509 | uint16 |  |  | bms_soc | [11 empty] | /components/pcs_info | pcs_bms_soc | Yes | Real value = (Modbus value / 10)
System SOH |  | SV16.1.10 | Input Register |  | 1 | 10 |  |  | 0.1 | 7509 | 47510 | uint16 |  |  | bms_soh | [11 empty] | /components/pcs_info | pcs_bms_soh | Yes | Real value = (Modbus value / 10)
System Mode |  | SV16.1.11 | Input Register |  | 1 |  |  |  |  | 7510 | 47511 | uint16 |  |  | bms_mode | [11 empty] | /components/pcs_info | pcs_bms_mode | Yes | Real value = Modbus value
Max Cell Volt Sys |  | SV16.1.12 | Input Register |  | 1 |  |  |  |  | 7511 | 47512 | uint16 |  |  | bms_max_v | [11 empty] | /components/pcs_info | pcs_bms_max_v | Yes | Real value = Modbus value
Min Cell Volt Sys |  | SV16.1.13 | Input Register |  | 1 |  |  |  |  | 7512 | 47513 | uint16 |  |  | bms_min_v | [11 empty] | /components/pcs_info | pcs_bms_min_v | Yes | Real value = Modbus value
Max Cell Temp Sys |  | SV16.1.14 | Input Register |  | 1 | 100 |  |  | 0.01 | 7513 | 47514 | uint16 |  |  | bms_max_temp | [11 empty] | /components/pcs_info | pcs_bms_max_temp | Yes | Real value = (Modbus value / 100)
Min Cell Temp Sys |  | SV16.1.15 | Input Register |  | 1 | 100 |  |  | 0.01 | 7514 | 47515 | uint16 |  |  | bms_min_temp | [11 empty] | /components/pcs_info | pcs_bms_min_temp | Yes | Real value = (Modbus value / 100)
Min. Partial String |  | SV16.1.16 | Input Register |  | 1 |  |  |  |  | 7515 | 47516 | uint16 |  |  | bms_min_partial_strings | [11 empty] | /components/pcs_info | pcs_bms_min_partial_strings | Yes | Real value = Modbus value
Partial Diff Voltage |  | SV16.1.17 | Input Register |  | 1 |  |  |  |  | 7516 | 47517 | uint16 |  |  | bms_partial_voltage | [11 empty] | /components/pcs_info | pcs_bms_partial_voltage | Yes | Real value = Modbus value
Sys Config Status |  | SV16.1.18 | Input Register |  | 1 |  |  |  |  | 7517 | 47518 | uint16 |  |  | bms_config_status | [11 empty] | /components/pcs_info | pcs_bms_config_status | Yes | Real value = Modbus value
Protection #4 |  | SV16.1.19 | Input Register |  | 1 |  |  |  |  | 7518 | 47519 | uint16 |  |  | bms_protection_4 | [11 empty] | /components/pcs_info | pcs_bms_protection_4 | Yes | Real value = Modbus value
Protection #3 |  | SV16.1.20 | Input Register |  | 1 |  |  |  |  | 7519 | 47520 | uint16 |  |  | bms_protection_3 | [11 empty] | /components/pcs_info | pcs_bms_protection_3 | Yes | Real value = Modbus value
Protection #2 |  | SV16.1.21 | Input Register |  | 1 |  |  |  |  | 7520 | 47521 | uint16 |  |  | bms_protection_2 | [11 empty] | /components/pcs_info | pcs_bms_protection_2 | Yes | Real value = Modbus value
Protection #1 |  | SV16.1.22 | Input Register |  | 1 |  |  |  |  | 7521 | 47522 | uint16 |  |  | bms_protection_1 | [11 empty] | /components/pcs_info | pcs_bms_protection_1 | Yes | Real value = Modbus value
Alarm #4 |  | SV16.1.23 | Input Register |  | 1 |  |  |  |  | 7522 | 47523 | uint16 |  |  | bms_alarm_4 | [11 empty] | /components/pcs_info | pcs_bms_alarm_4 | Yes | Real value = Modbus value
Alarm #3 |  | SV16.1.24 | Input Register |  | 1 |  |  |  |  | 7523 | 47524 | uint16 |  |  | bms_alarm_3 | [11 empty] | /components/pcs_info | pcs_bms_alarm_3 | Yes | Real value = Modbus value
Alarm #2 |  | SV16.1.25 | Input Register |  | 1 |  |  |  |  | 7524 | 47525 | uint16 |  |  | bms_alarm_2 | [11 empty] | /components/pcs_info | pcs_bms_alarm_2 | Yes | Real value = Modbus value
Alarm #1 |  | SV16.1.26 | Input Register |  | 1 |  |  |  |  | 7525 | 47526 | uint16 |  |  | bms_alarm_1 | [11 empty] | /components/pcs_info | pcs_bms_alarm_1 | Yes | Real value = Modbus value
DCL |  | SV16.1.27 | Input Register |  | 1 | 10 |  |  | 0.1 | 7526 | 47527 | uint16 |  |  | bms_dcl | [11 empty] | /components/pcs_info | pcs_bms_dcl | Yes | Real value = (Modbus value / 10)
CCL |  | SV16.1.28 | Input Register |  | 1 | 10 |  |  | 0.1 | 7527 | 47528 | uint16 |  |  | bms_ccl | [11 empty] | /components/pcs_info | pcs_bms_ccl | Yes | Real value = (Modbus value / 10)
Watchdog response |  | SV16.1.29 | Input Register |  | 1 |  |  |  |  | 7528 | 47529 | uint16 |  |  | bms_watchdog_response | [11 empty] | /components/pcs_info | pcs_bms_watchdog_response | Yes | Real value = Modbus value
Digital Input Status |  | SV16.1.30 | Input Register |  | 1 |  |  |  |  | 7529 | 47530 | uint16 |  |  | bms_dio_status | [11 empty] | /components/pcs_info | pcs_bms_dio_status | Yes | Real value = Modbus value
System Alarm Status |  | SV16.1.31 | Input Register |  | 1 |  |  |  |  | 7530 | 47531 | uint16 |  |  | bms_alarm_status | [11 empty] | /components/pcs_info | pcs_bms_alarm_status | Yes | Real value = Modbus value
BMS Enclosure | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
Door Contact |  | SV17.1 | Input Register |  | 1 |  |  |  |  | 7650 | 47651 | uint16 |  |  | bmsenc_door_contact | [11 empty] | /components/pcs_info | pcs_bmsenc_door_contact | Yes | Real value = Modbus value
FCP Alarm |  | SV17.2 | Input Register |  | 1 |  |  |  |  | 7651 | 47652 | uint16 |  |  | bmsenc_fcp_alarm | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_alarm | Yes | Real value = Modbus value
FCP Predischarge |  | SV17.3 | Input Register |  | 1 |  |  |  |  | 7652 | 47653 | uint16 |  |  | bmsenc_fcp_predischarge | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_predischarge | Yes | Real value = Modbus value
FCP Agent Release |  | SV17.4 | Input Register |  | 1 |  |  |  |  | 7653 | 47654 | uint16 |  |  | bmsenc_fcp_release | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_release | Yes | Real value = Modbus value
FCP Trouble Sup |  | SV17.5 | Input Register |  | 1 |  |  |  |  | 7654 | 47655 | uint16 |  |  | bmsenc_fcp_sup | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_sup | Yes | Real value = Modbus value
DC 1 Disconnected |  | SV17.6 | Input Register |  | 1 |  |  |  |  | 7655 | 47656 | uint16 |  |  | bmsenc_dc_disconnected_1 | [11 empty] | /components/pcs_info | pcs_bmsenc_dc_disconnected_1 | Yes | Real value = Modbus value
DC 2 Disconnected |  | SV17.7 | Input Register |  | 1 |  |  |  |  | 7656 | 47657 | uint16 |  |  | bmsenc_dc_disconnected_2 | [11 empty] | /components/pcs_info | pcs_bmsenc_dc_disconnected_2 | Yes | Real value = Modbus value
Emergency Stop |  | SV17.8 | Input Register |  | 1 |  |  |  |  | 7657 | 47658 | uint16 |  |  | bmsenc_emergency_stop | [11 empty] | /components/pcs_info | pcs_bmsenc_emergency_stop | Yes | Real value = Modbus value
UPS Battery Failure |  | SV17.9 | Input Register |  | 1 |  |  |  |  | 7658 | 47659 | uint16 |  |  | bmsenc_ups_failure | [11 empty] | /components/pcs_info | pcs_bmsenc_ups_failure | Yes | Real value = Modbus value
UPS DC OK |  | SV17.10 | Input Register |  | 1 |  |  |  |  | 7659 | 47660 | uint16 |  |  | bmsenc_ups_ok | [11 empty] | /components/pcs_info | pcs_bmsenc_ups_ok | Yes | Real value = Modbus value
Temp Humidity T |  | SV17.11 | Input Register |  | 1 |  |  |  |  | 7660 | 47661 | uint16 |  |  | bmsenc_temp_humidity_t | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_humidity_t | Yes | Real value = Modbus value
Temp Humidity H |  | SV17.12 | Input Register |  | 1 |  |  |  |  | 7661 | 47662 | uint16 |  |  | bmsenc_temp_humidity_h | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_humidity_h | Yes | Real value = Modbus value
Temp 1 |  | SV17.13 | Input Register |  | 1 | 10 |  |  | 0.1 | 7662 | 47663 | uint16 |  |  | bmsenc_temp_1 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_1 | Yes | Real value = (Modbus value / 10)
Temp 2 |  | SV17.14 | Input Register |  | 1 | 10 |  |  | 0.1 | 7663 | 47664 | uint16 |  |  | bmsenc_temp_2 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_2 | Yes | Real value = (Modbus value / 10)
Temp 3 |  | SV17.15 | Input Register |  | 1 | 10 |  |  | 0.1 | 7664 | 47665 | uint16 |  |  | bmsenc_temp_3 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_3 | Yes | Real value = (Modbus value / 10)
Temp 4 |  | SV17.16 | Input Register |  | 1 | 10 |  |  | 0.1 | 7665 | 47666 | uint16 |  |  | bmsenc_temp_4 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_4 | Yes | Real value = (Modbus value / 10)
Temp 5 |  | SV17.17 | Input Register |  | 1 | 10 |  |  | 0.1 | 7666 | 47667 | uint16 |  |  | bmsenc_temp_5 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_5 | Yes | Real value = (Modbus value / 10)
Temp 6 |  | SV17.18 | Input Register |  | 1 | 10 |  |  | 0.1 | 7667 | 47668 | uint16 |  |  | bmsenc_temp_6 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_6 | Yes | Real value = (Modbus value / 10)
BMS Transformer | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
Transformer Alarms |  | SV18.1 | Input Register |  | 1 |  |  |  |  | 7680 | 47681 | uint16 |  |  | transformer_alarms | [11 empty] | /components/pcs_info | pcs_transformer_alarms | Yes | Real value = Modbus value
BMS HVAC | [15 empty] | pcs_info | [5 empty] | 500 | 20 | 98
HVAC signals 1 |  | SV19.1 | Input Register |  | 1 |  |  |  |  | 7690 | 47691 | uint16 |  |  | hvac_signals_1 | [11 empty] | /components/pcs_info | pcs_hvac_signals_1 | Yes | Real value = Modbus value
HVAC signals 2 |  | SV19.2 | Input Register |  | 1 |  |  |  |  | 7691 | 47692 | uint16 |  |  | hvac_signals_2 | [11 empty] | /components/pcs_info | pcs_hvac_signals_2 | Yes | Real value = Modbus value
HVAC signals 3 |  | SV19.3 | Input Register |  | 1 |  |  |  |  | 7692 | 47693 | uint16 |  |  | hvac_signals_3 | [11 empty] | /components/pcs_info | pcs_hvac_signals_3 | Yes | Real value = Modbus value
HVAC signals 4 |  | SV19.4 | Input Register |  | 1 |  |  |  |  | 7693 | 47694 | uint16 |  |  | hvac_signals_4 | [11 empty] | /components/pcs_info | pcs_hvac_signals_4 | Yes | Real value = Modbus value
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A6: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A14: Tony Olivo: Do not add rows below this line, the script will break
Note on A15: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B15: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D15: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E15: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F15: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G15: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H15: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J15: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on L15: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on M15: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on N15: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on O15: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on P15: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Z15: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AA15: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AB15: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AC15: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AD15: Tony Olivo: Yes/No whether to include in the client/server config
Note on AE15: Tony Olivo: For humans
Note on AF15: Tony Olivo: For humans
Note on AG15: Tony Olivo: Ranges are for humans only
Note on AK15: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with

## 04_26_2022
Connection Name | PCMS
Connection Name | PCMS
Device Protocol | Modbus TCP
Device Protocol Version | 6.0 WIP
Device Name | pe_pcs_1
Device ID String | pe_pcs_1
ip_address | 192.168.112.13
Device Port (502 typical)
Serial Device (if RTU)
Baud Rate (4800, 9600, 14400, 19200, 38400, 57600, 115200 typical)
Parity (none, even, odd)
Data Bits (8 typical) | Columns marked in green are REQUIRED
Stop Bits (1 typical)
RTU Device ID (1 typical)
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address | Address Original | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
PCS Controls | [15 empty] | pe_pcs_controls | [5 empty] | 200 | 0 | 98
Remote Control Functions
Start | Control | G0.1 | Holding Register |  | 1 |  |  |  |  | 3009 | 43010 | uint16 |  |  | start | [11 empty] | /components/pcs_controls | pcs_start | Yes | 1 = Start
Stop | Control | G0.2 | Holding Register |  | 1 |  |  |  |  | 3010 | 43011 | uint16 |  |  | stop | [11 empty] | /components/pcs_controls | pcs_stop | Yes | 1 = Stop
Reset | Control | G0.3 | Holding Register |  | 1 |  |  |  |  | 3011 | 43012 | uint16 |  |  | reset | [11 empty] | /components/pcs_controls | pcs_reset | Yes | 1 = Reset
E-Stop | Control | G0.4 | Holding Register |  | 1 |  |  |  |  | 3199 | 43200 | uint16 |  |  | e_stop | [11 empty] | /components/pcs_controls | pcs_e_stop | Yes | 1 = Estop
Selector Control
Selector Config | Control |  | Holding Register |  | 1 |  |  |  |  | 2013 |  | uint16 |  |  | selector_config | [13 empty] | Yes
Start Control Mode | Control |  | Holding Register |  | 1 |  |  |  |  | 2040 |  | uint16 |  |  | start_control_mode | [13 empty] | Yes
Selector Status | Control |  | Holding Register |  | 1 |  |  |  |  | 2041 |  | uint16 |  |  | selector_status | [13 empty] | Yes
General
Access Code | Control | G1.2 | Input Register |  | 1 |  |  |  |  | 2 | 40003 | uint16 |  |  | access | [11 empty] | /components/pcs_controls | pcs_access | Yes | G1: General
User | Control | G1.3 | Input Register |  | 1 |  |  |  |  | 3 | 40004 | uint16 |  |  | user | [11 empty] | /components/pcs_controls | pcs_user | Yes
User Password | Control | G1.4 | Holding Register |  | 1 |  |  |  |  | 4 | 40005 | uint16 |  |  | user_pw | [11 empty] | /components/pcs_controls | pcs_user_pw | Yes
seconds | Control | G1.5.1 | Holding Register | Sec | 1 |  |  |  |  | 5 | 40006 | uint16 |  |  | seconds | [11 empty] | /components/pcs_controls | pcs_seconds | Yes
Minutes | Control | G1.5.2 | Holding Register | Min | 1 |  |  |  |  | 6 | 40007 | uint16 |  |  | minutes | [11 empty] | /components/pcs_controls | pcs_minutes | Yes
Hours | Control | G1.5.3 | Holding Register | Hrs | 1 |  |  |  |  | 7 | 40008 | uint16 |  |  | hours | [11 empty] | /components/pcs_controls | pcs_hours | Yes
Day | Control | G1.5.4 | Holding Register | Day | 1 |  |  |  |  | 8 | 40009 | uint16 |  |  | day | [11 empty] | /components/pcs_controls | pcs_day | Yes
Month | Control | G1.5.5 | Holding Register | Month | 1 |  |  |  |  | 9 | 40010 | uint16 |  |  | month | [11 empty] | /components/pcs_controls | pcs_month | Yes
Year | Control | G1.5.6 | Holding Register | Year | 1 |  |  |  |  | 10 | 40011 | uint16 |  |  | year | [11 empty] | /components/pcs_controls | pcs_year | Yes
UTC offset | Control | G1.6 | Holding Register | UTC | 1 |  |  |  |  | 11 | 40012 | int16 |  |  | utc | [11 empty] | /components/pcs_controls | pcs_utc | Yes | -720 to 840
Running Conditions
Vdc Low | Control | G2.1.1 | Holding Register | V | 1 |  |  |  |  | 30 | 40031 | uint16 |  |  | vdc_low | [11 empty] | /components/pcs_controls | pcs_vdc_low | Yes | G2: Running conditions. 0 to 1500 Volts
Vac Low | Control | G2.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 31 | 40032 | uint16 |  |  | vac_low | [11 empty] | /components/pcs_controls | pcs_vac_low | Yes | 80.0 to 100.0
Vac High | Control | G2.1.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 32 | 40033 | uint16 |  |  | vac_high | [11 empty] | /components/pcs_controls | pcs_vac_high | Yes | 100.0 to 120
Start Delay | Control | G2.1.6 | Holding Register | Sec | 1 |  |  |  |  | 35 | 40036 | uint16 |  |  | start_delay | [11 empty] | /components/pcs_controls | pcs_start_delay | Yes | 0 to 600 Seconds
Limits
P Limit | Control | G3.1.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 100 | 40101 | uint16 |  |  | p_limit | [11 empty] | /components/pcs_controls | pcs_p_limit | Yes | G3: Limits. 100 = 10000
Q Limit | Control | G3.1.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 101 | 40102 | uint16 |  |  | q_limit | [11 empty] | /components/pcs_controls | pcs_q_limit | Yes | 0 to 150 % 100=10000
P / Q Priority | Control | G3.1.3 | Holding Register |  | 1 |  |  |  |  | 102 | 40103 | uint16 |  |  | p_q_priority | [11 empty] | /components/pcs_controls | pcs_p_q_priority | Yes | 0=P, 1= Q
S limit | Control | G3.1.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 103 | 40104 | unt16 |  |  | s_limit | [11 empty] | /components/pcs_controls | pcs_s_limit | Yes | 0-200% 0, to 20000
P algorithm priority | Control | G3.1.5 | Holding Register |  | 1 |  |  |  |  | 104 | 40105 | uint16 |  |  | p_algo_pri | [11 empty] | /components/pcs_controls | pcs_p_algo_pri | Yes | 0=min, 1=P(f) priority, 2=P(v)piority
Gradients
LVRT Reference | Control | G4.2.1.8 | Holding Register | % | 1 |  |  |  |  | 192 | 40193 | uint16 |  |  | lvrt_ref | [11 empty] | /components/pcs_controls | pcs_lvrt_ref | Yes | G4: Algorithms
OVRT Reference | Control | G4.3.1.8 | Holding Register | % | 1 |  |  |  |  | 193 | 40194 | uint16 |  |  | ovrt_ref | [11 empty] | /components/pcs_controls | pcs_ovrt_ref | Yes
Night Mode Enable | Control | G4.7.1 | Holding Register |  | 1 |  |  |  |  | 260 | 40261 | uint16 |  |  | night_mode_enable | [11 empty] | /components/pcs_controls | pcs_night_mode_enable | Yes | 0=No, 1=Yes
Night Mode Q ref | Control | G4.7.2 | Holding Register |  | 1 | 100 |  |  | 0.01 | 261 | 40262 | int16 |  |  | night_mode_q_ref | [11 empty] | /components/pcs_controls | pcs_night_mode_q_ref | Yes | -100 to 100 ,100 = 10000
Night Mode Vbus Ref | Control | G4.7.3 | Holding Register | V | 1 | 1 |  |  | 1 | 262 | 40263 | uint16 |  |  | night_mode_vbus_ref | [11 empty] | /components/pcs_controls | pcs_night_mode_vbus_ref | Yes | 961 to 1250
Night Mode Activate | Control | G4.7.4 | Holding Register |  | 1 |  |  |  |  | 263 | 40264 | uint16 |  |  | night_mode_activate | [11 empty] | /components/pcs_controls | pcs_night_mode_activate | Yes | 0=No, 1= Yes
P Start Gradient Enable | Control | G4.8.1.1 | Holding Register |  | 1 |  |  |  |  | 276 | 40277 | uint16 |  |  | start_grad_p_enable | [11 empty] | /components/pcs_controls | pcs_start_grad_p_enable | Yes | 0=No, 1= Yes
P Start Gradient | Control | G4.8.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 277 | 40278 | uint16 |  |  | start_grad_p | [11 empty] | /components/pcs_controls | pcs_start_grad_p | Yes | 0.1 to 30000.0 % , 0 to 30000
Q Start Gradient Enable | Control | G4.8.1.3 | Holding Register |  | 1 |  |  |  |  | 278 | 40279 | uint16 |  |  | start_grad_q_enable | [11 empty] | /components/pcs_controls | pcs_start_grad_q_enable | Yes | 0=No, 1= Yes
Q Start Gradient | Control | G4.8.1.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 279 | 40280 | uint16 |  |  | start_grad_q | [11 empty] | /components/pcs_controls | pcs_start_grad_q | Yes | 0.1 to 30000.0 % , 0 to 30000
P Rise Gradient Enable | Control | G4.8.2.1 | Holding Register |  | 1 |  |  |  |  | 280 | 40281 | uint16 |  |  | rise_grad_p_enable | [11 empty] | /components/pcs_controls | pcs_rise_grad_p_enable | Yes | 0=No, 1= Yes
P Rise Gradient | Control | G4.8.2.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 281 | 40282 | uint16 |  |  | rise_grad_p | [11 empty] | /components/pcs_controls | pcs_rise_grad_p | Yes
Q Rise Gradient Enable | Control | G4.8.2.3 | Holding Register |  | 1 |  |  |  |  | 282 | 40283 | uint16 |  |  | rise_grad_q_enable | [11 empty] | /components/pcs_controls | pcs_rise_grad_q_enable | Yes | 0=No, 1= Yes
Q Rise Gradient | Control | G4.8.2.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 283 | 40284 | uint16 |  |  | rise_grad_q | [11 empty] | /components/pcs_controls | pcs_rise_grad_q | Yes
P Drop Gradient Enable | Control | G4.8.3.1 | Holding Register |  | 1 |  |  |  |  | 284 | 40285 | uint16 |  |  | drop_grad_p_enable | [11 empty] | /components/pcs_controls | pcs_drop_grad_p_enable | Yes | 0=No, 1= Yes
P Drop Gradient | Control | G4.8.3.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 285 | 40286 | uint16 |  |  | drop_grad_p | [11 empty] | /components/pcs_controls | pcs_drop_grad_p | Yes
Q Drop Gradient Enable | Control | G4.8.3.3 | Holding Register |  | 1 |  |  |  |  | 286 | 40287 | uint16 |  |  | drop_grad_q_enable | [11 empty] | /components/pcs_controls | pcs_drop_grad_q_enable | Yes | 0=No, 1= Yes
Q Drop Gradient | Control | G4.8.3.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 287 | 40288 | uint16 |  |  | drop_grad_q | [11 empty] | /components/pcs_controls | pcs_drop_grad_q | Yes
P Stop Gradient Enable | Control | G4.8.4.1 | Holding Register |  | 1 |  |  |  |  | 288 | 40289 | uint16 |  |  | stop_grad_p_enable | [11 empty] | /components/pcs_controls | pcs_stop_grad_p_enable | Yes | 0=No, 1= Yes
P Stop Gradient | Control | G4.8.4.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 289 | 40290 | uint16 |  |  | stop_grad_p | [11 empty] | /components/pcs_controls | pcs_stop_grad_p | Yes
Q Stop Gradient Enable | Control | G4.8.4.3 | Holding Register |  | 1 |  |  |  |  | 290 | 40291 | uint16 |  |  | stop_grad_q_enable | [11 empty] | /components/pcs_controls | pcs_stop_grad_q_enable | Yes | 0=No, 1= Yes
Q Stop Gradient | Control | G4.8.4.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 291 | 40292 | uint16 |  |  | stop_grad_q | [11 empty] | /components/pcs_controls | pcs_stop_grad_q | Yes
Trackers Enable | Control | G4.9.1 | Holding Register |  | 1 |  |  |  |  | 292 | 40293 | uint16 |  |  | tracker_enable | [11 empty] | /components/pcs_controls | pcs_tracker_enable | Yes | 0=No, 1= Yes
Trackers Vac Out | Control | G4.9.2 | Holding Register | V | 1 |  |  |  |  | 293 | 40294 | uint16 |  |  | tracker_vac_out | [11 empty] | /components/pcs_controls | pcs_tracker_vac_out | Yes
Trackers Vac min | Control | G4.9.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 294 | 40295 | uint16 |  |  | tracker_vac_min | [11 empty] | /components/pcs_controls | pcs_tracker_vac_min | Yes | 00 to 100, 0 to 1000
Trackers Time Start | Control | G4.9.4 | Holding Register | Sec | 1 | 10 |  |  | 0.1 | 295 | 40296 | uint16 |  |  | tracker_time_start | [11 empty] | /components/pcs_controls | pcs_tracker_time_start | Yes | 0.1 to 15 s , 0 to 150
V/P Enable | Control | G4.10.1 | Holding Register |  | 1 |  |  |  |  | 820 | 40821 | uint16 |  |  | vp_enable | [11 empty] | /components/pcs_controls | pcs_vp_enable | Yes
V/P V1 | Control | G4.10.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 821 | 40822 | uint16 |  |  | vp_v1 | [11 empty] | /components/pcs_controls | pcs_vp_v1 | Yes | 100 to g4_10_3%
V/P V2 | Control | G4.10.3 | Holding Register | % | 1 | 100 |  |  | 0.01 | 822 | 40823 | uint16 |  |  | vp_v2 | [11 empty] | /components/pcs_controls | pcs_vp_v2 | Yes | G4.10.2% to 140%, G4.10.2 to 14000
V/P P1 | Control | G4.10.4 | Holding Register | % | 1 | 100 |  |  | 0.01 | 823 | 40824 | uint16 |  |  | vp_p1 | [11 empty] | /components/pcs_controls | pcs_vp_p1 | Yes | G4.10.5% to 100%, G4.10.5 to 10000
V/P P2 | Control | G4.10.5 | Holding Register | % | 1 | 100 |  |  | 0.01 | 824 | 40825 | uint16 |  |  | vp_p2 | [11 empty] | /components/pcs_controls | pcs_vp_p2 | Yes | 0 to G4.10.4% , 0 to G4.10.4
V/P Hysteresis | Control | G4.10.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 825 | 40826 | uint16 |  |  | vp_hysteresis | [11 empty] | /components/pcs_controls | pcs_vp_hysteresis | Yes | 0 to 10%, 0 to 100
V/P Delay Hysterisis | Control | G4.10.8 | Holding Register | S | 1 | 10 |  |  | 0.1 | 827 | 40828 | uint16 |  |  | vp_delay_hysteresis | [11 empty] | /components/pcs_controls | pcs_vp_delay_hysteresis | Yes | 0.0 to 90 Sec, 0 to 900
V/P Response Time | Control | G4.10.9 | Holding Register | S | 1 | 10 |  |  | 0.1 | 828 | 40829 | uint16 |  |  | vp_response_tiime | [11 empty] | /components/pcs_controls | pcs_vp_response_tiime | Yes | 0.0 to 90.0s, 0 to 900
V/P Ref Power Rel | Control | G4.10.10 | Holding Register |  | 1 |  |  |  |  | 818 | 40819 | uint16 |  |  | vp_ref_power | [11 empty] | /components/pcs_controls | pcs_vp_ref_power | Yes | 0=rel, 1= abs
V/P Recover Mode | Control | G4.10.11 | Holding Register |  | 1 |  |  |  |  | 819 | 40820 | uint16 |  |  | vp_rec_mode | [11 empty] | /components/pcs_controls | pcs_vp_rec_mode | Yes | 0=Abs, 1= Rel
SVR Enable | Control | G4.11.1 | Holding Register |  | 1 |  |  |  |  | 540 | 40541 | uint16 |  |  | svr_enable | [11 empty] | /components/pcs_controls | pcs_svr_enable | Yes | Suppression of Voltage Rise 0=No, 1=Yes
SVR V1 Threshold | Control | G4.11.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 541 | 40542 | uint16 |  |  | svr_v1_threshold | [11 empty] | /components/pcs_controls | pcs_svr_v1_threshold | Yes | 100.0% to G4.11.7%, 1000 to G4.11.7
SVR V1 Hysteresis | Control | G4.11.3 | Holding Register | % | 1 | 10 |  |  | 0.1 | 543 | 40544 | uint16 |  |  | svr_v1_hysteresis | [11 empty] | /components/pcs_controls | pcs_svr_v1_hysteresis | Yes | 0.5 to 10%, 5 to 100
SVR Grad Inj Q | Control | G4.11.4 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 545 | 40546 | uint16 |  |  | svr_grad_inject | [11 empty] | /components/pcs_controls | pcs_svr_grad_inject | Yes | 0.1 to 200.0 %/S, 1 to 2000
SVR Grad Recover Q | Control | G4.11.5 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 546 | 40547 | uint16 |  |  | svr_grad_recover_q | [11 empty] | /components/pcs_controls | pcs_svr_grad_recover_q | Yes | 0.1% to 200.0%, 1 to 2000
SVR CosFi limit | Control | G4.11.6 | Holding Register |  | 1 | 100 |  |  | 0.01 | 549 | 40550 | uint16 |  |  | svr_cosfi_limit | [11 empty] | /components/pcs_controls | pcs_svr_cosfi_limit | Yes | 0.80 to 1.00. 80 to 100
SVR V2 Threshold | Control | G4.11.7 | Holding Register | % | 1 | 10 |  |  | 0.1 | 542 | 40543 | uint16 |  |  | svr_v2_threshold | [11 empty] | /components/pcs_controls | pcs_svr_v2_threshold | Yes | G4.11.2% to 120%, G4.11.2 to 1200
SVR V2 Hysteresis | Control | G4.11.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 544 | 40545 | uint16 |  |  | svr_v2_hysetresis | [11 empty] | /components/pcs_controls | pcs_svr_v2_hysetresis | Yes | 0.5 to 10%, 5 to 100
SVR Grad Reduction P | Control | G4.11.9 | Holding Register |  | 1 | 10 |  |  | 0.1 | 547 | 40548 | uint16 |  |  | svr_grad_reduction_p | [11 empty] | /components/pcs_controls | pcs_svr_grad_reduction_p | Yes | 0.1 to 200 %/S, 1 to 2000
SVR Grad Recover P | Control | G4.11.10 | Holding Register | %/S | 1 | 10 |  |  | 0.1 | 548 | 40549 | uint16 |  |  | svr_grad_recover_p | [11 empty] | /components/pcs_controls | pcs_svr_grad_recover_p | Yes | 0.1% to 200.0%, 1 to 2000
Active Balancing Activate | Control | G4.12.1.2 | Holding Register |  | 1 |  |  |  |  | 7021 | 47022 | uint16 |  |  | active_bal_activate | [11 empty] | /components/pcs_controls | pcs_active_bal_activate | Yes | 0=No, 1= Yes
Bank Balancing Activate | Control | G4.12.2.2 | Holding Register |  | 1 |  |  |  |  | 7024 | 47025 | uint16 |  |  | bank_bal_activate | [11 empty] | /components/pcs_controls | pcs_bank_bal_activate | Yes | 0=No, 1= Yes
Bank Balancing Reconnect Gradient | Control | G4.12.2.5 | Holding Register |  | 1 |  |  |  |  | 7027 | 47028 | uint16 |  |  | bank_bal_reconnect_grad | [11 empty] | /components/pcs_controls | pcs_bank_bal_reconnect_grad | Yes | 0.1 to 3000.0 %/s
Constant Voltage Standby Activate | Control | G4.12.3.2 | Holding Register |  | 1 |  |  |  |  | 7029 | 47030 | uint16 |  |  | cvsb_activate | [11 empty] | /components/pcs_controls | pcs_cvsb_activate | Yes | 0=No, 1= Yes
Constant Voltage Standby Time to Enter | Control | G4.12.3.3 | Holding Register |  | 1 |  |  |  |  | 7030 | 47031 | uint16 |  |  | cvsb_time_to_enter | [11 empty] | /components/pcs_controls | pcs_cvsb_time_to_enter | Yes | 60 to 3600s
Protections
LV Protections Enable | Control | G5.1.1 | Holding Register |  | 1 |  |  |  |  | 300 | 40301 | uint16 |  |  | lv_enable | [11 empty] | /components/pcs_controls | pcs_lv_enable | Yes | G5: Protections
LV Interpolation | Control | G5.1.1b | Holding Register |  | 1 |  |  |  |  | 308 | 40309 | uint16 |  |  | lv_interpolation | [11 empty] | /components/pcs_controls | pcs_lv_interpolation | Yes | 0=No, 1= Yes
LV Slow Protection | Control | G5.1.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 301 | 40302 | uint16 |  |  | lv_slow | [11 empty] | /components/pcs_controls | pcs_lv_slow | Yes | 0 to 100%, 10 to 1000
LV Delay Slow Protection | Control | G5.1.3 | Holding Register | S | 1 | 100 |  |  | 0.01 | 302 | 40303 | uint16 |  |  | lv_delay_slow | [11 empty] | /components/pcs_controls | pcs_lv_delay_slow | Yes | 0.0 to 6550.0S , 0 to 65500
LV Fast Protection | Control | G5.1.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 303 | 40304 | uint16 |  |  | lv_fast | [11 empty] | /components/pcs_controls | pcs_lv_fast | Yes | 0 to 100%, 10 to 1000
LV Delay Fast Protection | Control | G5.1.5 | Holding Register | S | 1 | 100 |  |  | 0.01 | 304 | 40305 | uint16 |  |  | lv_delay_fast | [11 empty] | /components/pcs_controls | pcs_lv_delay_fast | Yes | 0.0 to 6550.0S , 0 to 65500
LV Fast Protection 2 | Control | G5.1.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 375 | 40376 | uint16 |  |  | lv_fast_2 | [11 empty] | /components/pcs_controls | pcs_lv_fast_2 | Yes | 0 to 100%, 10 to 1000
LV Delay Fast Protection 2 | Control | G5.1.7 | Holding Register | S | 1 | 100 |  |  | 0.01 | 376 | 40377 | uint16 |  |  | lv_delay_fast_2 | [11 empty] | /components/pcs_controls | pcs_lv_delay_fast_2 | Yes | 0.0 to 6550.0S , 0 to 65500
LV Very Fast Protection | Control | G5.1.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 305 | 40306 | uint16 |  |  | lv_very_fast | [11 empty] | /components/pcs_controls | pcs_lv_very_fast | Yes | 0 to 100%, 10 to 1000
LV Delay Very Fast Protection | Control | G5.1.9 | Holding Register | S | 1 | 100 |  |  | 0.01 | 306 | 40307 | uint16 |  |  | lv_delay_very_fast | [11 empty] | /components/pcs_controls | pcs_lv_delay_very_fast | Yes | 0.0 to 6550.0S , 0 to 65500
LV Very Fast Protection 2 | Control | G5.1.10 | Holding Register | % | 1 | 10 |  |  | 0.1 | 377 | 40378 | uint16 |  |  | lv_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lv_very_fast_2 | Yes | 0 to 100%, 10 to 1000
LV Delay Very Fast Protection 2 | Control | G5.1.11 | Holding Register | S | 1 | 100 |  |  | 0.01 | 378 | 40379 | uint16 |  |  | lv_delay_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lv_delay_very_fast_2 | Yes | 0.0 to 6550.0S , 0 to 65500
HV Protections Enable | Control | G5.2.1 | Holding Register |  | 1 |  |  |  |  | 310 | 40311 | uint16 |  |  | hv_enable | [11 empty] | /components/pcs_controls | pcs_hv_enable | Yes
HV Interpolation | Control | G5.2.1b | Holding Register |  | 1 |  |  |  |  | 317 | 40318 | uint16 |  |  | hv_interpolation | [11 empty] | /components/pcs_controls | pcs_hv_interpolation | Yes | 0=No, 1= Yes
HV Slow Protection | Control | G5.2.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 311 | 40312 | uint16 |  |  | hv_slow | [11 empty] | /components/pcs_controls | pcs_hv_slow | Yes | 0 to 100%, 10 to 1000
HV Delay Slow Protection | Control | G5.2.3 | Holding Register | S | 1 | 100 |  |  | 0.01 | 312 | 40313 | uint16 |  |  | hv_delay_slow | [11 empty] | /components/pcs_controls | pcs_hv_delay_slow | Yes | 0.0 to 6550.0S , 0 to 65500
HV Fast Protection | Control | G5.2.4 | Holding Register | % | 1 | 10 |  |  | 0.1 | 313 | 40314 | uint16 |  |  | hv_fast | [11 empty] | /components/pcs_controls | pcs_hv_fast | Yes | 0 to 100%, 10 to 1000
HV Delay Fast Protection | Control | G5.2.5 | Holding Register | S | 1 | 100 |  |  | 0.01 | 314 | 40315 | uint16 |  |  | hv_delay_fast | [11 empty] | /components/pcs_controls | pcs_hv_delay_fast | Yes | 0.0 to 6550.0S , 0 to 65500
HV Fast Protection 2 | Control | G5.2.6 | Holding Register | % | 1 | 10 |  |  | 0.1 | 379 | 40380 | uint16 |  |  | hv_fast_2 | [11 empty] | /components/pcs_controls | pcs_hv_fast_2 | Yes | 0 to 100%, 10 to 1000
HV Delay Fast Protection 2 | Control | G5.2.7 | Holding Register | S | 1 | 100 |  |  | 0.01 | 380 | 40381 | uint16 |  |  | hv_delay_fast_2 | [11 empty] | /components/pcs_controls | pcs_hv_delay_fast_2 | Yes | 0.0 to 6550.0S , 0 to 65500
HV Very Fast Protection | Control | G5.2.8 | Holding Register | % | 1 | 10 |  |  | 0.1 | 315 | 40316 | uint16 |  |  | hv_very_fast | [11 empty] | /components/pcs_controls | pcs_hv_very_fast | Yes | 0 to 100%, 10 to 1000
HV Delay Very Fast Protection | Control | G5.2.9 | Holding Register | S | 1 | 100 |  |  | 0.01 | 316 | 40317 | uint16 |  |  | hv_delay_very_fast | [11 empty] | /components/pcs_controls | pcs_hv_delay_very_fast | Yes | 0.0 to 6550.0S , 0 to 65500
HV Very Fast Protection 2 | Control | G5.2.10 | Holding Register | % | 1 | 10 |  |  | 0.1 | 381 | 40382 | uint16 |  |  | hv_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hv_very_fast_2 | Yes | 0 to 100%, 10 to 1000
HV Delay Very Fast Protection 2 | Control | G5.2.11 | Holding Register | S | 1 | 100 |  |  | 0.01 | 382 | 40383 | uint16 |  |  | hv_delay_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hv_delay_very_fast_2 | Yes | 0.0 to 6550.0S , 0 to 65500
LF Protections Enable | Control | G5.3.1 | Holding Register |  | 1 |  |  |  |  | 320 | 40321 | uint16 |  |  | lf_enable | [11 empty] | /components/pcs_controls | pcs_lf_enable | Yes
LF Slow Protection | Control | G5.3.2 | Holding Register | % | 1 | 10 |  |  | 0.1 | 321 | 40322 | uint16 |  |  | lf_slow | [11 empty] | /components/pcs_controls | pcs_lf_slow | Yes | 0 to 100%, 10 to 1000
LF Delay Slow Protection | Control | G5.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 322 | 40323 | uint16 |  |  | lf_delay_slow | [11 empty] | /components/pcs_controls | pcs_lf_delay_slow | Yes
LF Slow 2 Protection | Control | G5.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 383 | 40384 | uint16 |  |  | lf_slow_2 | [11 empty] | /components/pcs_controls | pcs_lf_slow_2 | Yes
LF Delay Slow 2 Protection | Control | G5.3.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 384 | 40385 | uint16 |  |  | lf_delay_slow_2 | [11 empty] | /components/pcs_controls | pcs_lf_delay_slow_2 | Yes
LF Fast Protection | Control | G5.3.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 323 | 40324 | uint16 |  |  | lf_fast | [11 empty] | /components/pcs_controls | pcs_lf_fast | Yes
LF Delay Fast Protection | Control | G5.3.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 324 | 40325 | uint16 |  |  | lf_delay_fast | [11 empty] | /components/pcs_controls | pcs_lf_delay_fast | Yes
LF Very Fast Protection | Control | G5.3.8 | Holding Register |  | 1 | 100 |  |  | 0.01 | 325 | 40326 | uint16 |  |  | lf_very_fast | [11 empty] | /components/pcs_controls | pcs_lf_very_fast | Yes
LF Delay Very Fast Protection | Control | G5.3.9 | Holding Register |  | 1 | 10 |  |  | 0.1 | 326 | 40327 | uint16 |  |  | lf_delay_very_fast | [11 empty] | /components/pcs_controls | pcs_lf_delay_very_fast | Yes
LF Very Fast 2 Protection | Control | G5.3.10 | Holding Register |  | 1 | 10 |  |  | 0.1 | 385 | 40386 | uint16 |  |  | lf_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lf_very_fast_2 | Yes
LF Delay Very Fast 2 Protection | Control | G5.3.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 386 | 40387 | uint16 |  |  | lf_delay_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_lf_delay_very_fast_2 | Yes
HF Protections Enable | Control | G5.4.1 | Holding Register |  | 1 |  |  |  |  | 330 | 40331 | uint16 |  |  | hf_enable | [11 empty] | /components/pcs_controls | pcs_hf_enable | Yes
HF Slow Protection |  | G5.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 331 | 40332 | uint16 |  |  | hf_slow | [11 empty] | /components/pcs_controls | pcs_hf_slow | Yes
HF Delay Slow Protection |  | G5.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 332 | 40333 | uint16 |  |  | hf_delay_slow | [11 empty] | /components/pcs_controls | pcs_hf_delay_slow | Yes
HF Slow 2 Protection |  | G5.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 387 | 40388 | uint16 |  |  | hf_slow_2 | [11 empty] | /components/pcs_controls | pcs_hf_slow_2 | Yes
HF Delay Slow 2 Protection |  | G5.4.5 | Holding Register |  | 1 | 100 |  |  | 0.01 | 388 | 40389 | uint16 |  |  | hf_delay_slow_2 | [11 empty] | /components/pcs_controls | pcs_hf_delay_slow_2 | Yes
HF Fast Protection |  | G5.4.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 333 | 40334 | uint16 |  |  | hf_fast | [11 empty] | /components/pcs_controls | pcs_hf_fast | Yes
HF Delay Fast Protection |  | G5.4.7 | Holding Register |  | 1 | 100 |  |  | 0.01 | 334 | 40335 | uint16 |  |  | hf_delay_fast | [11 empty] | /components/pcs_controls | pcs_hf_delay_fast | Yes
HF Very Fast Protection |  | G5.4.8 | Holding Register |  | 1 | 10 |  |  | 0.1 | 335 | 40336 | uint16 |  |  | hf_very_fast | [11 empty] | /components/pcs_controls | pcs_hf_very_fast | Yes
HF Delay Very Fast Protection |  | G5.4.9 | Holding Register |  | 1 | 100 |  |  | 0.01 | 336 | 40337 | uint16 |  |  | hf_delay_very_fast | [11 empty] | /components/pcs_controls | pcs_hf_delay_very_fast | Yes
HF Very Fast 2 Protection |  | G5.4.10 | Holding Register |  | 1 | 10 |  |  | 0.1 | 389 | 40390 | uint16 |  |  | hf_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hf_very_fast_2 | Yes
HF Delay Very Fast 2 Protection |  | G5.4.11 | Holding Register |  | 1 | 100 |  |  | 0.01 | 390 | 40391 | uint16 |  |  | hf_delay_very_fast_2 | [11 empty] | /components/pcs_controls | pcs_hf_delay_very_fast_2 | Yes
Enable 5.4b.1.1 |  | G5.4b.1.1 | Holding Register |  | 1 |  |  |  |  | 730 | 40731 | uint16 |  |  | hv_hf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_1 | Yes
V1 = 120% |  | G5.4b.1.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 731 | 40732 | uint16 |  |  | hv_hf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_1_V1 | Yes
f1 = 62.00 Hz |  | G5.4b.1.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 732 | 40733 | uint16 |  |  | hv_hf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_1_f1 | Yes
t1 = 1.0 s |  | G5.4b.1.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 733 | 40734 | uint16 |  |  | hv_hf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_1_t1 | Yes
Enable 5.4b.2.1 |  | G5.4b.2.1 | Holding Register |  | 1 |  |  |  |  | 734 | 40735 | uint16 |  |  | lv_hf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_2 | Yes
V2 = 80% |  | G5.4b.2.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 735 | 40736 | uint16 |  |  | lv_hf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_2_V2 | Yes
f2 = 62.00 Hz |  | G5.4b.2.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 736 | 40737 | uint16 |  |  | lv_hf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_2_f2 | Yes
t2 = 1.0 s |  | G5.4b.2.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 737 | 40738 | uint16 |  |  | lv_hf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_2_t2 | Yes
Enable 5.4b.3.1 |  | G5.4b.3.1 | Holding Register |  | 1 |  |  |  |  | 738 | 40739 | uint16 |  |  | hv_lf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_3 | Yes
V3 = 120% |  | G5.4b.3.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 739 | 40740 | uint16 |  |  | hv_lf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_3_V3 | Yes
f3 = 58.00 Hz |  | G5.4b.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 740 | 40741 | uint16 |  |  | hv_lf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_3_f3 | Yes
t3 = 1.0 s |  | G5.4b.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 741 | 40742 | uint16 |  |  | hv_lf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_3_t3 | Yes
Enable 5.4b.4.1 |  | G5.4b.4.1 | Holding Register |  | 1 |  |  |  |  | 472 | 40473 | uint16 |  |  | lv_lf_enable | [11 empty] | /components/pcs_controls | pcs_enable_5_4b_4 | Yes
V4 = 80% |  | G5.4b.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 473 | 40474 | uint16 |  |  | lv_lf_V | [11 empty] | /components/pcs_controls | pcs_5_4b_4_V4 | Yes
f4 = 58.00 Hz |  | G5.4b.4.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 474 | 40475 | uint16 |  |  | lv_lf_f | [11 empty] | /components/pcs_controls | pcs_5_4b_4_f4 | Yes
t4 = 1.0 s |  | G5.4b.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 475 | 40476 | uint16 |  |  | lv_lf_t | [11 empty] | /components/pcs_controls | pcs_5_4b_4_t4 | Yes
Unbalance Protections |  | G5.5.1 | Holding Register |  | 1 |  |  |  |  | 340 | 40341 | uint16 |  |  | unbalance_enable | [11 empty] | /components/pcs_controls | pcs_unbalance_enable | Yes
I unbalance |  | G5.5.2 | Holding Register |  | 1 | 1 |  |  | 1 | 341 | 40342 | uint16 |  |  | unbalance_i_threshold | [11 empty] | /components/pcs_controls | pcs_unbalance_i_threshold | Yes
I unbalance min |  | G5.5.2b | Holding Register |  | 1 | 1 |  |  | 1 | 347 | 40348 | uint16 |  |  | unbalance_i_min | [11 empty] | /components/pcs_controls | pcs_unbalance_i_min | Yes
Delay I unbalance |  | G5.5.3 | Holding Register |  | 1 | 1 |  |  | 1 | 342 | 40343 | uint16 |  |  | unbalance_i_delay | [11 empty] | /components/pcs_controls | pcs_unbalance_i_delay | Yes
Unbalance V |  | G5.5.4 | Holding Register |  | 1 | 1 |  |  | 1 | 343 | 40344 | uint16 |  |  | unbalance_v_threshold | [11 empty] | /components/pcs_controls | pcs_unbalance_v_threshold | Yes
Delay Unbalance V |  | G5.5.5 | Holding Register |  | 1 | 1 |  |  | 1 | 344 | 40345 | uint16 |  |  | unbalance_v_delay | [11 empty] | /components/pcs_controls | pcs_unbalance_v_delay | Yes
Anti Islanding Enable |  | G5.6.1 | Holding Register |  | 1 |  |  |  |  | 350 | 40351 | uint16 |  |  | antiislanding_enable | [11 empty] | /components/pcs_controls | pcs_antiislanding_enable | Yes
IGBTs temp thres fit=125 C |  | G5.7.1 | Holding Register |  | 1 | 1 |  |  | 1 | 360 | 40361 | uint16 |  |  | igbt_temp_thres_fit | [11 empty] | /components/pcs_controls | pcs_igbt_temp_thres_fit | Yes
IGBTs temp hist =10 C |  | G5.7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 361 | 40362 | uint16 |  |  | igbt_temp_hist | [11 empty] | /components/pcs_controls | pcs_igbt_temp_hist | Yes
Module temp thres fit=85 C |  | G5.7.3 | Holding Register |  | 1 | 1 |  |  | 1 | 362 | 40363 | uint16 |  |  | module_temp_thres_fit | [11 empty] | /components/pcs_controls | pcs_module_temp_thres_fit | Yes
Module temp thist=10 C |  | G5.7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 363 | 40364 | uint16 |  |  | module_temp_hist | [11 empty] | /components/pcs_controls | pcs_module_temp_hist | Yes
Internal temp thres fit=85 C |  | G5.7.5 | Holding Register |  | 1 | 1 |  |  | 1 | 364 | 40365 | uint16 |  |  | internal_temp_thres_fit | [11 empty] | /components/pcs_controls | pcs_internal_temp_thres_fit | Yes
HVPL Enable 5.9.1 |  | G5.9.1 | Holding Register |  | 1 |  |  |  |  | 391 | 40392 | uint16 |  |  | hvpl_enable | [11 empty] | /components/pcs_controls | pcs_hvpl_enable | Yes
HVPL Activation Level = 5% |  | G5.9.2 | Holding Register |  | 1 | 1 |  |  | 1 | 392 | 40393 | uint16 |  |  | hvpl_activation_level_5 | [11 empty] | /components/pcs_controls | pcs_hvpl_activation_level_5 | Yes
HVPL Scale = 1000 |  | G5.9.3 | Holding Register |  | 1 | 1 |  |  | 1 | 393 | 40394 | uint16 |  |  | hvpl_scale_1000 | [11 empty] | /components/pcs_controls | pcs_hvpl_scale_1000 | Yes
HVPL Fault Level = 0 |  | G5.9.4 | Holding Register |  | 1 | 1 |  |  | 1 | 394 | 40395 | uint16 |  |  | hvpl_fault_level_0 | [11 empty] | /components/pcs_controls | pcs_hvpl_fault_level_0 | Yes
HVPL filter = 0.100 Hz |  | G5.9.5 | Holding Register |  | 1 | 1000 |  |  | 0.001 | 395 | 40396 | uint16 |  |  | hvpl_filter_hz_100_hz | [11 empty] | /components/pcs_controls | pcs_hvpl_filter_hz_100_hz | Yes
HVPL delay fault = 2.0 s |  | G5.9.6 | Holding Register |  | 1 | 10 |  |  | 0.1 | 396 | 40397 | uint16 |  |  | hvpl_delay_fault_s_0_s | [11 empty] | /components/pcs_controls | pcs_hvpl_delay_fault_s_0_s | Yes
HVPL Start Test |  | G5.9.7 | Holding Register |  | 1 |  |  |  |  | 397 | 40398 | uint16 |  |  | hvpl_start_test | [11 empty] | /components/pcs_controls | pcs_hvpl_start_test | Yes
HVPL Test Level = -20% |  | G5.9.8 | Holding Register |  | 1 | 1 |  |  | 1 | 398 | 40399 | int16 |  |  | hvpl_test_level_20 | [11 empty] | /components/pcs_controls | pcs_hvpl_test_level_20 | Yes
Earth Current |  | G5.11.1 | Holding Register | % | 1 | 10 |  |  | 0.1 | 370 | 40371 | uint16 |  |  | earth_current | [11 empty] | /components/pcs_controls | pcs_earth_current | Yes
Delay High Vdc = 1 s |  | G5.11.2 | Holding Register | s | 1 | 1 |  |  | 1 | 371 | 40372 | uint16 |  |  | high_vdc_delay | [11 empty] | /components/pcs_controls | pcs_high_vdc_delay | Yes
DU Overcurrent = 400.0 A |  | G5.11.3 | Holding Register | A | 1 | 10 |  |  | 0.1 | 372 | 40373 | uint16 |  |  | du_overcurrent | [11 empty] | /components/pcs_controls | pcs_du_overcurrent | Yes
MV manometer fault = off |  | G5.11.4 | Holding Register |  | 1 | 1 |  |  | 1 | 480 | 40481 | uint16 |  |  | mv_manometer_fault | [11 empty] | /components/pcs_controls | pcs_mv_manometer_fault | Yes
MV manometer delay = 10 s |  | G5.11.5 | Holding Register | s | 1 | 1 |  |  | 1 | 481 | 40482 | uint16 |  |  | mv_manometer_delay | [11 empty] | /components/pcs_controls | pcs_mv_manometer_delay | Yes
LV manometer fault = off |  | G5.11.6 | Holding Register |  | 1 | 1 |  |  | 1 | 482 | 40483 | uint16 |  |  | lv_manometer_fault | [11 empty] | /components/pcs_controls | pcs_lv_manometer_fault | Yes
LV manometer delay = 10 s |  | G5.11.7 | Holding Register | s | 1 | 1 |  |  | 1 | 483 | 40484 | uint16 |  |  | lv_manometer_delay | [11 empty] | /components/pcs_controls | pcs_lv_manometer_delay | Yes
Communications
Display Baudrate = 115200 |  | G6.1.1 | Holding Register | bps | 1 |  |  |  |  | 400 | 40401 | uint16 |  |  | display_baudrate | [11 empty] | /components/pcs_controls | pcs_display_baudrate | Yes
Modbus Address=150 |  | G6.1.2 | Holding Register |  | 1 |  |  |  |  | 401 | 40402 | uint16 |  |  | modbus_address | [11 empty] | /components/pcs_controls | pcs_modbus_address | Yes
Modbus Baudrate=19200 bps |  | G6.1.3 | Holding Register | bps | 1 |  |  |  |  | 402 | 40403 | uint16 |  |  | modbus_baudrate | [11 empty] | /components/pcs_controls | pcs_modbus_baudrate | Yes
Modbus Parity |  | G6.1.4 | Holding Register |  | 1 |  |  |  |  | 403 | 40404 | uint16 |  |  | modbus_parity | [11 empty] | /components/pcs_controls | pcs_modbus_parity | Yes
Modbus Stop bits |  | G6.1.5 | Holding Register |  | 1 |  |  |  |  | 404 | 40405 | uint16 |  |  | modbus_stop_bits | [11 empty] | /components/pcs_controls | pcs_modbus_stop_bits | Yes
Modbus Master |  | G6.1.6 | Holding Register |  | 1 |  |  |  |  | 405 | 40406 | uint16 |  |  | modbus_master | [11 empty] | /components/pcs_controls | pcs_modbus_master | Yes
Automatic IP |  | G6.2.1 | Holding Register |  | 1 |  |  |  |  | 410 | 40411 | uint16 |  |  | automatic_ip | [11 empty] | /components/pcs_controls | pcs_automatic_ip | Yes
Assigned IP A |  | G6.2.1.1a | Holding Register |  | 1 |  |  |  |  | 411 | 40412 | uint16 |  |  | assigned_ip_a | [11 empty] | /components/pcs_controls | pcs_assigned_ip_a | Yes
Assigned IP B |  | G6.2.1.1b | Holding Register |  | 1 |  |  |  |  | 412 | 40413 | uint16 |  |  | assigned_ip_b | [11 empty] | /components/pcs_controls | pcs_assigned_ip_b | Yes
Assigned IP C |  | G6.2.1.1c | Holding Register |  | 1 |  |  |  |  | 413 | 40414 | uint16 |  |  | assigned_ip_c | [11 empty] | /components/pcs_controls | pcs_assigned_ip_c | Yes
Assigned IP D |  | G6.2.1.1d | Holding Register |  | 1 |  |  |  |  | 414 | 40415 | uint16 |  |  | assigned_ip_d | [11 empty] | /components/pcs_controls | pcs_assigned_ip_d | Yes
Assigned Subnet A |  | G6.2.1.2a | Holding Register |  | 1 |  |  |  |  | 415 | 40416 | uint16 |  |  | assigned_subnet_a | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_a | Yes
Assigned Subnet B |  | G6.2.1.2b | Holding Register |  | 1 |  |  |  |  | 416 | 40417 | uint16 |  |  | assigned_subnet_b | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_b | Yes
Assigned Subnet C |  | G6.2.1.2c | Holding Register |  | 1 |  |  |  |  | 417 | 40418 | uint16 |  |  | assigned_subnet_c | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_c | Yes
Assigned Subnet D |  | G6.2.1.2d | Holding Register |  | 1 |  |  |  |  | 418 | 40419 | uint16 |  |  | assigned_subnet_d | [11 empty] | /components/pcs_controls | pcs_assigned_subnet_d | Yes
Assigned Gateway A |  | G6.2.1.3a | Holding Register |  | 1 |  |  |  |  | 419 | 40420 | uint16 |  |  | assigned_gateway_a | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_a | Yes
Assigned Gateway B |  | G6.2.1.3b | Holding Register |  | 1 |  |  |  |  | 420 | 40421 | uint16 |  |  | assigned_gateway_b | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_b | Yes
Assigned Gateway C |  | G6.2.1.3c | Holding Register |  | 1 |  |  |  |  | 421 | 40422 | uint16 |  |  | assigned_gateway_c | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_c | Yes
Assigned Gateway D |  | G6.2.1.3d | Holding Register |  | 1 |  |  |  |  | 422 | 40423 | uint16 |  |  | assigned_gateway_d | [11 empty] | /components/pcs_controls | pcs_assigned_gateway_d | Yes
IP address A |  | G6.2.2a | Holding Register |  | 1 |  |  |  |  | 423 | 40424 | uint16 |  |  | ip_address_a | [11 empty] | /components/pcs_controls | pcs_ip_address_a | Yes
IP address B |  | G6.2.2b | Holding Register |  | 1 |  |  |  |  | 424 | 40425 | uint16 |  |  | ip_address_b | [11 empty] | /components/pcs_controls | pcs_ip_address_b | Yes
IP address C |  | G6.2.2c | Holding Register |  | 1 |  |  |  |  | 425 | 40426 | uint16 |  |  | ip_address_c | [11 empty] | /components/pcs_controls | pcs_ip_address_c | Yes
IP address D |  | G6.2.2d | Holding Register |  | 1 |  |  |  |  | 426 | 40427 | uint16 |  |  | ip_address_d | [11 empty] | /components/pcs_controls | pcs_ip_address_d | Yes
Subnet A |  | G6.2.3a | Holding Register |  | 1 |  |  |  |  | 427 | 40428 | uint16 |  |  | subnet_a | [11 empty] | /components/pcs_controls | pcs_subnet_a | Yes
Subnet B |  | G6.2.3b | Holding Register |  | 1 |  |  |  |  | 428 | 40429 | uint16 |  |  | subnet_b | [11 empty] | /components/pcs_controls | pcs_subnet_b | Yes
Subnet C |  | G6.2.3c | Holding Register |  | 1 |  |  |  |  | 429 | 40430 | uint16 |  |  | subnet_c | [11 empty] | /components/pcs_controls | pcs_subnet_c | Yes
Subnet D |  | G6.2.3d | Holding Register |  | 1 |  |  |  |  | 430 | 40431 | uint16 |  |  | subnet_d | [11 empty] | /components/pcs_controls | pcs_subnet_d | Yes
Gateway A |  | G6.2.4a | Holding Register |  | 1 |  |  |  |  | 431 | 40432 | uint16 |  |  | gateway_a | [11 empty] | /components/pcs_controls | pcs_gateway_a | Yes
Gateway B |  | G6.2.4b | Holding Register |  | 1 |  |  |  |  | 432 | 40433 | uint16 |  |  | gateway_b | [11 empty] | /components/pcs_controls | pcs_gateway_b | Yes
Gateway C |  | G6.2.4c | Holding Register |  | 1 |  |  |  |  | 433 | 40434 | uint16 |  |  | gateway_c | [11 empty] | /components/pcs_controls | pcs_gateway_c | Yes
Gateway D |  | G6.2.4d | Holding Register |  | 1 |  |  |  |  | 434 | 40435 | uint16 |  |  | gateway_d | [11 empty] | /components/pcs_controls | pcs_gateway_d | Yes
Mac A |  | G6.2.5a | Holding Register |  | 1 |  |  |  |  | 435 | 40436 | uint16 |  |  | mac_a | [11 empty] | /components/pcs_controls | pcs_mac_a | Yes
Mac B |  | G6.2.5b | Holding Register |  | 1 |  |  |  |  | 436 | 40437 | uint16 |  |  | mac_b | [11 empty] | /components/pcs_controls | pcs_mac_b | Yes
Mac C |  | G6.2.5c | Holding Register |  | 1 |  |  |  |  | 437 | 40438 | uint16 |  |  | mac_c | [11 empty] | /components/pcs_controls | pcs_mac_c | Yes
Mac D |  | G6.2.5d | Holding Register |  | 1 |  |  |  |  | 438 | 40439 | uint16 |  |  | mac_d | [11 empty] | /components/pcs_controls | pcs_mac_d | Yes
Mac E |  | G6.2.5e | Holding Register |  | 1 |  |  |  |  | 439 | 40440 | uint16 |  |  | mac_e | [11 empty] | /components/pcs_controls | pcs_mac_e | Yes
Mac F |  | G6.2.5e | Holding Register |  | 1 |  |  |  |  | 440 | 40441 | uint16 |  |  | mac_f | [11 empty] | /components/pcs_controls | pcs_mac_f | Yes
Watchdog timer input |  | G6.3 | Holding Register |  | 1 | 1 |  |  | 1 | 4251 | 44252 | uint16 |  |  | ppc_watchdog_ref | [11 empty] | /components/pcs_controls | pcs_ppc_watchdog_ref | Yes
Reset refs time = 4s |  | G6.3.1 | Holding Register |  | 1 | 1 |  |  | 1 | 4252 | 44253 | uint16 |  |  | reset_refs_time_s | [11 empty] | /components/pcs_controls | pcs_reset_refs_time_s | Yes
Comms Fault time = 60 s |  | G6.3.2 | Holding Register |  | 1 | 1 |  |  | 1 | 4253 | 44254 | uint16 |  |  | comms_fault_time_s_s | [11 empty] | /components/pcs_controls | pcs_comms_fault_time_s_s | Yes
Home P ref = 0.0% |  | G6.3.3 | Holding Register |  | 1 | 100 |  |  | 0.01 | 4254 | 44255 | uint16 |  |  | home_p_ref_0_0 | [11 empty] | /components/pcs_controls | pcs_home_p_ref_0_0 | Yes
Home Q ref = 0.0% |  | G6.3.4 | Holding Register |  | 1 | 100 |  |  | 0.01 | 4255 | 44256 | int16 |  |  | home_q_ref_0_0 | [11 empty] | /components/pcs_controls | pcs_home_q_ref_0_0 | Yes
Auto Reset
Auto Reset Enable |  | G7.1 | Holding Register |  | 1 |  |  |  |  | 500 | 40501 | uint16 |  |  | auto_reset_enable | [11 empty] | /components/pcs_controls | pcs_enable_g_1 | Yes
Number of Retries |  | G7.2 | Holding Register |  | 1 | 1 |  |  | 1 | 501 | 40502 | uint16 |  |  | number_of_retries | [11 empty] | /components/pcs_controls | pcs_number_of_retries | Yes
Delay between retries = 30 s |  | G7.3 | Holding Register |  | 1 | 10 |  |  | 0.1 | 502 | 40503 | uint16 |  |  | delay_between_retries_s_s | [11 empty] | /components/pcs_controls | pcs_delay_between_retries_s_s | Yes
Reset Retries timeout |  | G7.4 | Holding Register |  | 1 | 1 |  |  | 1 | 503 | 40504 | uint16 |  |  | reset_retries_timeout | [11 empty] | /components/pcs_controls | pcs_reset_retries_timeout | Yes
All Faults enabled |  | G7.5 | Holding Register |  | 1 |  |  |  |  | 504 | 40505 | uint16 |  |  | all_faults_enabled | [11 empty] | /components/pcs_controls | pcs_all_faults_enabled | Yes
Faults allowed number = 0 |  | G7.6 | Holding Register |  | 1 |  |  |  |  | 505 | 40506 | uint16 |  |  | faults_allowed_number | [11 empty] | /components/pcs_controls | pcs_faults_allowed_number | Yes
Faults allowed 1 = No Faults |  | G7.6.1 | Holding Register |  | 1 |  |  |  |  | 506 | 40507 | uint16 |  |  | faults_allowed_1 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_1 | Yes
Faults allowed 2 = No Faults |  | G7.6.2 | Holding Register |  | 1 |  |  |  |  | 507 | 40508 | uint16 |  |  | faults_allowed_2 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_2 | Yes
Faults allowed 3 = No Faults |  | G7.6.3 | Holding Register |  | 1 |  |  |  |  | 508 | 40509 | uint16 |  |  | faults_allowed_3 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_3 | Yes
Faults allowed 4 = No Faults |  | G7.6.4 | Holding Register |  | 1 |  |  |  |  | 509 | 40510 | uint16 |  |  | faults_allowed_4 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_4 | Yes
Faults allowed 5 = No Faults |  | G7.6.5 | Holding Register |  | 1 |  |  |  |  | 510 | 40511 | uint16 |  |  | faults_allowed_5 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_5 | Yes
Faults allowed 6 = No Faults |  | G7.6.6 | Holding Register |  | 1 |  |  |  |  | 511 | 40512 | uint16 |  |  | faults_allowed_6 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_6 | Yes
Faults allowed 7 = No Faults |  | G7.6.7 | Holding Register |  | 1 |  |  |  |  | 512 | 40513 | uint16 |  |  | faults_allowed_7 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_7 | Yes
Faults allowed 8 = No Faults |  | G7.6.8 | Holding Register |  | 1 |  |  |  |  | 513 | 40514 | uint16 |  |  | faults_allowed_8 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_8 | Yes
Faults allowed 9 = No Faults |  | G7.6.9 | Holding Register |  | 1 |  |  |  |  | 514 | 40515 | uint16 |  |  | faults_allowed_9 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_9 | Yes
Faults allowed 10 = No Faults |  | G7.6.10 | Holding Register |  | 1 |  |  |  |  | 515 | 40516 | uint16 |  |  | faults_allowed_10 | [11 empty] | /components/pcs_controls | pcs_faults_allowed_10 | Yes
Faults exception number = 0 |  | G7.7 | Holding Register |  | 1 |  |  |  |  | 516 | 40517 | uint16 |  |  | faults_exception_number | [11 empty] | /components/pcs_controls | pcs_faults_exception_number | Yes
Faults exception 1 = No faults |  | G7.7.1 | Holding Register |  | 1 |  |  |  |  | 517 | 40518 | uint16 |  |  | faults_exception_1 | [11 empty] | /components/pcs_controls | pcs_faults_exception_1 | Yes
Faults exception 2 = No faults |  | G.7.2 | Holding Register |  | 1 |  |  |  |  | 518 | 40519 | uint16 |  |  | faults_exception_2 | [11 empty] | /components/pcs_controls | pcs_faults_exception_2 | Yes
Faults exception 3 = No faults |  | G7.7.3 | Holding Register |  | 1 |  |  |  |  | 519 | 40520 | uint16 |  |  | faults_exception_3 | [11 empty] | /components/pcs_controls | pcs_faults_exception_3 | Yes
Faults exception 4 = No faults |  | G7.7.4 | Holding Register |  | 1 |  |  |  |  | 520 | 40521 | uint16 |  |  | faults_exception_4 | [11 empty] | /components/pcs_controls | pcs_faults_exception_4 | Yes
Faults exception 5 = No faults |  | G7.7.5 | Holding Register |  | 1 |  |  |  |  | 521 | 40522 | uint16 |  |  | faults_exception_5 | [11 empty] | /components/pcs_controls | pcs_faults_exception_5 | Yes
Faults exception 6 = No faults |  | G7.7.6 | Holding Register |  | 1 |  |  |  |  | 522 | 40523 | uint16 |  |  | faults_exception_6 | [11 empty] | /components/pcs_controls | pcs_faults_exception_6 | Yes
Faults exception 7 = No faults |  | G7.7.7 | Holding Register |  | 1 |  |  |  |  | 523 | 40524 | uint16 |  |  | faults_exception_7 | [11 empty] | /components/pcs_controls | pcs_faults_exception_7 | Yes
Faults exception 8 = No faults |  | G7.7.8 | Holding Register |  | 1 |  |  |  |  | 524 | 40525 | uint16 |  |  | faults_exception_8 | [11 empty] | /components/pcs_controls | pcs_faults_exception_8 | Yes
Faults exception 9 = No faults |  | G7.7.9 | Holding Register |  | 1 |  |  |  |  | 525 | 40526 | uint16 |  |  | faults_exception_9 | [11 empty] | /components/pcs_controls | pcs_faults_exception_9 | Yes
Faults exception 10 = No faults |  | G7.7.10 | Holding Register |  | 1 |  |  |  |  | 526 | 40527 | uint16 |  |  | faults_exception_10 | [11 empty] | /components/pcs_controls | pcs_faults_exception_10 | Yes
Control
P control Mode |  | G8.1.1 | Holding Register |  | 1 |  |  |  |  | 550 | 40551 | uint16 |  |  | p_control_mode | [11 empty] | /components/pcs_controls | pcs_p_control_mode | Yes
Q control Mode = Q |  | G8.1.2 | Holding Register |  | 1 |  |  |  |  | 551 | 40552 | uint16 |  |  | q_control_mode | [11 empty] | /components/pcs_controls | pcs_q_control_mode | Yes
P reference = 100% |  | G8.1.3.0.0 | Holding Register | % | 1 | 100 |  |  | 0.01 | 552 | 40553 | int16 |  |  | p_p_reference | [11 empty] | /components/pcs_controls | pcs_p_p_reference | Yes
Id reference = 100% |  | G8.1.3.0.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 553 | 40554 | int16 |  |  | p_id_reference | [11 empty] | /components/pcs_controls | pcs_p_id_reference | Yes
Cos phi reference = 1.000 |  | G8.1.4.0 | Holding Register | % | 1 | 1000 |  |  | 0.001 | 555 | 40556 | int16 |  |  | q_cosphi_reference | [11 empty] | /components/pcs_controls | pcs_q_cosphi_reference | Yes
Iq reference = 0 |  | G8.1.4.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 556 | 40557 | int16 |  |  | q_iq_reference | [11 empty] | /components/pcs_controls | pcs_q_iq_reference | Yes
Q reference = 0.0% |  | G8.1.4.2 | Holding Register | % | 1 | 100 |  |  | 0.01 | 557 | 40558 | int16 |  |  | q_q_reference | [11 empty] | /components/pcs_controls | pcs_q_q_reference | Yes
Vref = 100.00% |  | G8.1.4.3 | Holding Register | % | 1 | 100 |  |  | 0.01 | 575 | 40576 | int16 |  |  | q_v_reference | [11 empty] | /components/pcs_controls | pcs_q_v_reference | Yes
Excitation |  | G8.1.5.0 | Holding Register |  | 1 |  |  |  |  | 558 | 40559 | uint16 |  |  | excitation | [11 empty] | /components/pcs_controls | pcs_excitation | Yes | 0 = cap, 1 = ind
V1=90% |  | G8.1.5.1 | Holding Register | % | 1 | 100 |  |  | 0.01 | 576 | 40577 | uint16 |  |  | vq_v1 | [11 empty] | /components/pcs_controls | pcs_vq_v1 | Yes
V2 = 92.00% |  | G8.1.6 | Holding Register | % | 1 | 100 |  |  | 0.01 | 577 | 40578 | uint16 |  |  | vq_v2 | [11 empty] | /components/pcs_controls | pcs_vq_v2 | Yes
V3 = 108.00% |  | G8.1.7 | Holding Register | % | 1 | 100 |  |  | 0.01 | 578 | 40579 | uint16 |  |  | vq_v3 | [11 empty] | /components/pcs_controls | pcs_vq_v3 | Yes
V4 = 110.00% |  | G8.1.8 | Holding Register | % | 1 | 100 |  |  | 0.01 | 579 | 40580 | uint16 |  |  | vq_v4 | [11 empty] | /components/pcs_controls | pcs_vq_v4 | Yes
Q1 = 48.43% |  | G8.1.9 | Holding Register | % | 1 | 100 |  |  | 0.01 | 580 | 40581 | uint16 |  |  | vq_q1 | [11 empty] | /components/pcs_controls | pcs_vq_q1 | Yes
Q2 = 0.00% |  | G8.1.10 | Holding Register | % | 1 | 100 |  |  | 0.01 | 581 | 40582 | uint16 |  |  | vq_q2 | [11 empty] | /components/pcs_controls | pcs_vq_q2 | Yes
Q3 = 0.00% |  | G8.1.11 | Holding Register | % | 1 | 100 |  |  | 0.01 | 582 | 40583 | uint16 |  |  | vq_q3 | [11 empty] | /components/pcs_controls | pcs_vq_q3 | Yes
Q4 = 48.43% |  | G8.1.12 | Holding Register | % | 1 | 100 |  |  | 0.01 | 583 | 40584 | uint16 |  |  | vq_q4 | [11 empty] | /components/pcs_controls | pcs_vq_q4 | Yes
V hysterisis = 1.0% |  | G8.1.13 | Holding Register | % | 1 | 10 |  |  | 0.1 | 584 | 40585 | uint16 |  |  | vq_hysterisis | [11 empty] | /components/pcs_controls | pcs_vq_hysterisis | Yes
P activation = 20% |  | G8.1.14 | Holding Register | % | 1 | 10 |  |  | 0.1 | 585 | 40586 | uint16 |  |  | vq_p_activation | [11 empty] | /components/pcs_controls | pcs_vq_p_activation | Yes
P deactivation = 5.0% |  | G8.1.15 | Holding Register | % | 1 | 10 |  |  | 0.1 | 586 | 40587 | uint16 |  |  | vq_p_deactivation | [11 empty] | /components/pcs_controls | pcs_vq_p_deactivation | Yes
Response Tdelay = 0.3 s |  | G8.1.16 | Holding Register | s | 1 | 10 |  |  | 0.1 | 587 | 40588 | uint16 |  |  | vq_response_delay | [11 empty] | /components/pcs_controls | pcs_vq_response_delay | Yes
Response Time = 5.0 s |  | G8.1.17 | Holding Register | s | 1 | 10 |  |  | 0.1 | 588 | 40589 | uint16 |  |  | vq_response_time | [11 empty] | /components/pcs_controls | pcs_vq_response_time | Yes
Q reference 1 = 0.00% |  | G8.1.4a | Holding Register | % | 1 | 100 |  |  | 0.01 | 597 | 40598 | int16 |  |  | q_reference_1 | [11 empty] | /components/pcs_controls | q_reference_1 | Yes
Q reference 2 = 0.00% |  | G8.1.4b | Holding Register | % | 1 | 100 |  |  | 0.01 | 598 | 40599 | int16 |  |  | q_reference_2 | [11 empty] | /components/pcs_controls | q_reference_2 | Yes
Q reference 3 = 0.00% |  | G8.1.4a | Holding Register | % | 1 | 100 |  |  | 0.01 | 599 | 40600 | int16 |  |  | q_reference_3 | [11 empty] | /components/pcs_controls | q_reference_3 | Yes
Control
P DC reference 1 = 100% |  | G8.1.3a | Holding Register | % | 1 | 100 |  |  | 0.01 | 7141 | 47142 | int16 |  |  | p_dc_reference_1 | [11 empty] | /components/pcs_controls | pcs_p_dc_reference_1 | Yes
P DC reference 2 = 100% |  | G8.1.3b | Holding Register | % | 1 | 100 |  |  | 0.01 | 7142 | 47143 | int16 |  |  | p_dc_reference_2 | [11 empty] | /components/pcs_controls | pcs_p_dc_reference_2 | Yes
P DC reference 3 = 100% |  | G8.1.3c | Holding Register | % | 1 | 100 |  |  | 0.01 | 7143 | 47144 | int16 |  |  | p_dc_reference_3 | [11 empty] | /components/pcs_controls | pcs_p_dc_reference_3 | Yes
P AC reference 1 = 100% |  | G8.1.3a | Holding Register | % | 1 | 100 |  |  | 0.01 | 7144 | 47145 | int16 |  |  | p_ac_reference_1 | [11 empty] | /components/pcs_controls | pcs_p_ac_reference_1 | Yes
P AC reference 2 = 100% |  | G8.1.3b | Holding Register | % | 1 | 100 |  |  | 0.01 | 7145 | 47146 | int16 |  |  | p_ac_reference_2 | [11 empty] | /components/pcs_controls | pcs_p_ac_reference_2 | Yes
P AC reference 3 = 100% |  | G8.1.3c | Holding Register | % | 1 | 100 |  |  | 0.01 | 7146 | 47147 | int16 |  |  | p_ac_reference_3 | [11 empty] | /components/pcs_controls | pcs_p_ac_reference_3 | Yes
Leak Protection
Leak Protection Type |  | G9.2.1 | Holding Register |  | 1 |  |  |  |  | 7150 | 47151 | uint16 |  |  | leak_protection_type_1 | [11 empty] | /components/pcs_controls | pcs_leak_protection_type_1 | Yes
IMI Activation |  | G9.2.1a | Holding Register |  | 1 |  |  |  |  | 7151 | 47152 | uint16 |  |  | leak_imi_activation_1 | [11 empty] | /components/pcs_controls | pcs_leak_imi_activation_1 | Yes
Fault Threshold = 5.0kOhms |  | G9.2.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7152 | 47153 | uint16 |  |  | leak_fault_threshold_1 | [11 empty] | /components/pcs_controls | pcs_leak_fault_threshold_1 | Yes
Fault Recover Threshold = 115% |  | G9.2.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 7153 | 47154 | uint16 |  |  | leak_fault_recover_threshold_1 | [11 empty] | /components/pcs_controls | pcs_leak_fault_recover_threshold_1 | Yes
Warning Theshold=50.0kOhms |  | G9.2.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7154 | 47155 | uint16 |  |  | leak_warning_theshold_1 | [11 empty] | /components/pcs_controls | pcs_leak_warning_theshold_1 | Yes
Self Test exec per = 1440 |  | G9.2.7 | Holding Register |  | 1 | 1 |  |  | 1 | 7157 | 47158 | uint16 |  |  | leak_self_test_exec_period_1 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_exec_period_1 | Yes
Self Test Manual Command |  | G9.2.8 | Holding Register |  | 1 | 1 |  |  | 1 | 7158 | 47159 | uint16 |  |  | leak_self_test_manual_command_1 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_manual_command_1 | Yes
Leak Protection Type |  | G9.3.1 | Holding Register |  | 1 |  |  |  |  | 7160 | 47161 | uint16 |  |  | leak_protection_type_2 | [11 empty] | /components/pcs_controls | pcs_leak_protection_type_2 | Yes
IMI Activation |  | G9.3.1a | Holding Register |  | 1 |  |  |  |  | 7161 | 47162 | uint16 |  |  | leak_imi_activation_2 | [11 empty] | /components/pcs_controls | pcs_leak_imi_activation_2 | Yes
Fault Threshold = 5.0kOhms |  | G9.3.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7162 | 47163 | uint16 |  |  | leak_fault_threshold_2 | [11 empty] | /components/pcs_controls | pcs_leak_fault_threshold_2 | Yes
Fault Recover Threshold = 115% |  | G9.3.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 7163 | 47164 | uint16 |  |  | leak_fault_recover_threshold_2 | [11 empty] | /components/pcs_controls | pcs_leak_fault_recover_threshold_2 | Yes
Warning Theshold=50.0kOhms |  | G9.3.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7164 | 47165 | uint16 |  |  | leak_warning_theshold_2 | [11 empty] | /components/pcs_controls | pcs_leak_warning_theshold_2 | Yes
Self Test exec per = 1440 |  | G9.3.7 | Holding Register |  | 1 | 1 |  |  | 1 | 7167 | 47168 | uint16 |  |  | leak_self_test_exec_period_2 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_exec_period_2 | Yes
Self Test Manual Command |  | G9.3.8 | Holding Register |  | 1 | 1 |  |  | 1 | 7168 | 47169 | uint16 |  |  | leak_self_test_manual_command_2 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_manual_command_2 | Yes
Leak Protection Type |  | G9.4.1 | Holding Register |  | 1 |  |  |  |  | 7170 | 47171 | uint16 |  |  | leak_protection_type_3 | [11 empty] | /components/pcs_controls | pcs_leak_protection_type_3 | Yes
IMI Activation |  | G9.4.1a | Holding Register |  | 1 |  |  |  |  | 7171 | 47172 | uint16 |  |  | leak_imi_activation_3 | [11 empty] | /components/pcs_controls | pcs_leak_imi_activation_3 | Yes
Fault Threshold = 5.0kOhms |  | G9.4.2 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7172 | 47173 | uint16 |  |  | leak_fault_threshold_3 | [11 empty] | /components/pcs_controls | pcs_leak_fault_threshold_3 | Yes
Fault Recover Threshold = 115% |  | G9.4.3 | Holding Register |  | 1 | 2000 |  |  | 0.0005 | 7173 | 47174 | uint16 |  |  | leak_fault_recover_threshold_3 | [11 empty] | /components/pcs_controls | pcs_leak_fault_recover_threshold_3 | Yes
Warning Theshold=50.0kOhms |  | G9.4.4 | Holding Register |  | 1 | 10 |  |  | 0.1 | 7174 | 47175 | uint16 |  |  | leak_warning_theshold_3 | [11 empty] | /components/pcs_controls | pcs_leak_warning_theshold_3 | Yes
Self Test exec per = 1440 |  | G9.4.7 | Holding Register |  | 1 | 1 |  |  | 1 | 7177 | 47178 | uint16 |  |  | leak_self_test_exec_period_3 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_exec_period_3 | Yes
Self Test Manual Command |  | G9.4.8 | Holding Register |  | 1 | 1 |  |  | 1 | 7178 | 47179 | uint16 |  |  | leak_self_test_manual_command_3 | [11 empty] | /components/pcs_controls | pcs_leak_self_test_manual_command_3 | Yes
DU Configuration
Du Type = HEM |  | G10.1 | Holding Register |  | 1 | 1 |  |  | 1 | 649 | 40650 | uint16 |  |  | du_type | [11 empty] | /components/pcs_controls | pcs_du_type | Yes
Working Mode = GFDI + IMI |  | G10.2 | Holding Register |  | 1 | 1 |  |  | 1 | 650 | 40651 | uint16 |  |  | working_mode | [11 empty] | /components/pcs_controls | pcs_working_mode | Yes
Enabled NEC = NEC 2017 |  | G10.2b | Holding Register |  | 1 | 1 |  |  | 1 | 648 | 40649 | uint16 |  |  | enabled_nec | [11 empty] | /components/pcs_controls | pcs_enabled_nec | Yes
Battery Configuration
Battery Module Model |  | G15.1.1 | Holding Register |  | 1 | 1 |  |  | 1 | 7050 | 47051 | uint16 |  |  | battery_module_model | [11 empty] | /components/pcs_controls | pcs_battery_module_model | Yes
BMS Banks Enabled |  | G15.1.2 | Holding Register |  | 1 | 1 |  |  | 1 | 7051 | 47052 | uint16 |  |  | bms_banks_enabled | [11 empty] | /components/pcs_controls | pcs_bms_banks_enabled | Yes
PCS Info | [15 empty] | pe_pcs_info | [5 empty] | 200 | 0 | 98
Grid Visualization
Grid voltage RS |  | SV1.1 | Input Register |  | 1 | 1 |  |  | 1 | 1000 | 41001 | uint16 |  |  | grid_voltage_rs | [11 empty] | /components/pcs_info | pcs_grid_voltage_rs | Yes | Real value = (Modbus value / 10)
Grid voltage ST |  | SV1.2 | Input Register |  | 1 | 1 |  |  | 1 | 1001 | 41002 | uint16 |  |  | grid_voltage_st | [11 empty] | /components/pcs_info | pcs_grid_voltage_st | Yes | Real value = (Modbus value / 10)
Grid voltage TR |  | SV1.3 | Input Register |  | 1 | 1 |  |  | 1 | 1002 | 41003 | uint16 |  |  | grid_voltage_tr | [11 empty] | /components/pcs_info | pcs_grid_voltage_tr | Yes | Real value = (Modbus value / 10)
Grid current I1 |  | SV1.4 | Input Register |  | 1 | 1 |  |  | 1 | 1003 | 41004 | int16 |  |  | grid_current_1 | [11 empty] | /components/pcs_info | pcs_grid_current_1 | Yes | Real value = (Modbus value / 10)
Grid current I2 |  | SV1.5 | Input Register |  | 1 | 1 |  |  | 1 | 1004 | 41005 | int16 |  |  | grid_current_2 | [11 empty] | /components/pcs_info | pcs_grid_current_2 | Yes | Real value = (Modbus value / 10)
Grid current I3 |  | SV1.6 | Input Register |  | 1 | 1 |  |  | 1 | 1005 | 41006 | int16 |  |  | grid_current_3 | [11 empty] | /components/pcs_info | pcs_grid_current_3 | Yes | Real value = (Modbus value / 10)
P |  | SV1.7 | Input Register |  | 1 |  |  |  |  | 1007 | 41008 | int16 |  |  | active_power | [11 empty] | /components/pcs_info | pcs_active_power | Yes | Real value = Modbus value
Q |  | SV1.8 | Input Register |  | 1 |  |  |  |  | 1008 | 41009 | int16 |  |  | reactive_power | [11 empty] | /components/pcs_info | pcs_reactive_power | Yes | Real value = Modbus value
S |  | SV1.9 | Input Register |  | 1 |  |  |  |  | 1009 | 41010 | int16 |  |  | apparent_power | [11 empty] | /components/pcs_info | pcs_apparent_power | Yes | Real value = Modbus value
Cos phi |  | SV1.10 | Input Register |  | 1 | 1000 |  |  | 0.001 | 1010 | 41011 | int16 |  |  | cosphi | [11 empty] | /components/pcs_info | pcs_cosphi | Yes | Real value = (Modbus value / 1000)
Grid frequency |  | SV1.11 | Input Register |  | 1 | 1000 |  |  | 0.001 | 1011 | 41012 | uint16 |  |  | grid_frequency | [11 empty] | /components/pcs_info | pcs_grid_frequency | Yes | Real value = (Modbus value / 100)
POI V estimated |  | SV1.13 | Input Register |  | 1 |  |  |  |  | 1013 | 41014 | uint16 |  |  | poi_v_est | [11 empty] | /components/pcs_info | pcs_poi_v_est | Yes | Real value = Modbus value
Grid voltage RS (Low Voltage) |  | SV1.1 | Input Register |  | 1 |  |  |  |  | 1020 |  | uint16 |  |  | grid_voltage_rs_lv | [11 empty] | /components/pcs_info | pcs_grid_voltage_rs_lv | Yes | Real value = Modbus value
Grid voltage ST (Low Voltage) |  | SV1.2 | Input Register |  | 1 |  |  |  |  | 1021 |  | uint16 |  |  | grid_voltage_st_lv | [11 empty] | /components/pcs_info | pcs_grid_voltage_st_lv | Yes | Real value = Modbus value
Grid voltage TR (Low Voltage) |  | SV1.2 | Input Register |  | 1 |  |  |  |  | 1022 |  | uint16 |  |  | grid_voltage_tr_lv | [11 empty] | /components/pcs_info | pcs_grid_voltage_tr_lv | Yes | Real value = Modbus value
DC Inputs
DC Voltage Bus 1 |  | SV2.1.1 | Input Register |  | 1 |  |  |  |  | 7400 | 47401 | uint16 |  |  | vdc_bus_1 | [11 empty] | /components/pcs_info | pcs_vdc_bus_1 | Yes | Real value = Modbus value
DC Voltage Bus 2 |  | SV2.1.2 | Input Register |  | 1 |  |  |  |  | 7401 | 47402 | uint16 |  |  | vdc_bus_2 | [11 empty] | /components/pcs_info | pcs_vdc_bus_2 | Yes | Real value = Modbus value
DC Voltage Bus 3 |  | SV2.1.3 | Input Register |  | 1 |  |  |  |  | 7402 | 47403 | uint16 |  |  | vdc_bus_3 | [11 empty] | /components/pcs_info | pcs_vdc_bus_3 | Yes | Real value = Modbus value
DC voltage last linp |  | SV2.3 | Input Register |  | 1 |  |  |  |  | 1052 | 41053 | uint16 |  |  | vdc_last_linp | [11 empty] | /components/pcs_info | pcs_vdc_last_linp | Yes | Real value = Modbus value
BESS 1 voltage bus |  | SV2.4.1 | Input Register |  | 1 | 10 |  |  | 0.1 | 7403 | 47404 | uint16 |  |  | bess_1_v | [11 empty] | /components/pcs_info | pcs_bess_1_v | Yes | Real value = (Modbus value / 10)
BESS 2 voltage bus |  | SV2.4.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 7404 | 47405 | uint16 |  |  | bess_2_v | [11 empty] | /components/pcs_info | pcs_bess_2_v | Yes | Real value = (Modbus value / 10)
BESS 3 voltage bus |  | SV2.4.3 | Input Register |  | 1 | 10 |  |  | 0.1 | 7405 | 47406 | uint16 |  |  | bess_3_v | [11 empty] | /components/pcs_info | pcs_bess_3_v | Yes | Real value = (Modbus value / 10)
DC input power |  | SV2.5 | Input Register |  | 1 |  |  |  |  | 1060 | 41061 | int16 |  |  | dc_p_input | [11 empty] | /components/pcs_info | pcs_dc_p_input | Yes | Real value = Modbus value
BESS1 DC input power |  | SV2.5a | Input Register |  | 1 |  |  |  |  | 7406 | 47407 | uint16 |  |  | bess_1_p_input | [11 empty] | /components/pcs_info | pcs_bess_1_p_input | Yes | Real value = Modbus value
BESS2 DC input power |  | SV2.5b | Input Register |  | 1 |  |  |  |  | 7407 | 47408 | uint16 |  |  | bess_2_p_input | [11 empty] | /components/pcs_info | pcs_bess_2_p_input | Yes | Real value = Modbus value
BESS3 DC input power |  | SV2.5c | Input Register |  | 1 |  |  |  |  | 7408 | 47409 | uint16 |  |  | bess_3_p_input | [11 empty] | /components/pcs_info | pcs_bess_3_p_input | Yes | Real value = Modbus value
DC input current total |  | SV2.6 | Input Register |  | 1 |  |  |  |  | 1061 | 41062 | int16 |  |  | dc_total_i_input | [11 empty] | /components/pcs_info | pcs_dc_total_i_input | Yes | Real value = Modbus value
DC input current 1 |  | SV2.6a | Input Register |  | 1 |  |  |  |  | 7409 | 47410 | uint16 |  |  | dc_1_i_input | [11 empty] | /components/pcs_info | pcs_dc_1_i_input | Yes | Real value = Modbus value
DC input current 2 |  | SV2.6b | Input Register |  | 1 |  |  |  |  | 7410 | 47411 | uint16 |  |  | dc_2_i_input | [11 empty] | /components/pcs_info | pcs_dc_2_i_input | Yes | Real value = Modbus value
DC input current 3 |  | SV2.6c | Input Register |  | 1 |  |  |  |  | 7411 | 47412 | uint16 |  |  | dc_3_i_input | [11 empty] | /components/pcs_info | pcs_dc_3_i_input | Yes | Real value = Modbus value
Ref current DC BESS1 |  | SV2.8 | Input Register |  | 1 |  |  |  |  | 7412 | 47413 | uint16 |  |  | bess_1_idcref | [11 empty] | /components/pcs_info | pcs_bess_1_idcref | Yes | Real value = Modbus value
Ref current DC BESS2 |  | SV2.9 | Input Register |  | 1 |  |  |  |  | 7413 | 47414 | uint16 |  |  | bess_2_idcref | [11 empty] | /components/pcs_info | pcs_bess_2_idcref | Yes | Real value = Modbus value
Ref current DC BESS3 |  | SV2.10 | Input Register |  | 1 |  |  |  |  | 7414 | 47415 | uint16 |  |  | bess_3_idcref | [11 empty] | /components/pcs_info | pcs_bess_3_idcref | Yes | Real value = Modbus value
Insulation Monitoring
Insulation Status |  | SV3.2.1 | Input Register |  | 1 |  |  |  |  | 1102 | 41103 | uint16 |  |  | insulation_status_1 | [11 empty] | /components/pcs_info | pcs_insulation_status_1 | Yes | Real value = Modbus value
Insulation Resistor MSB |  | SV3.2.2a | Input Register |  | 1 |  |  |  |  | 1103 | 41104 | uint16 |  |  | insulation_resistor_msb_1 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_msb_1 | Yes | – MSB
Resistor LSB |  | SV3.2.2b | Input Register |  | 1 |  |  |  |  | 1104 | 41105 | uint16 |  |  | insulation_resistor_lsb_1 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_lsb_1 | Yes | – MSB
Insulation Measurement started time |  | SV3.2.3 | Input Register |  | 1 |  |  |  |  | 1105 | 41106 | uint16 |  |  | insulation_measurement_started_time_1 | [11 empty] | /components/pcs_info | pcs_insulation_measurement_started_time_1 | Yes | Real value = Modbus value
Insulation Self-test started time |  | SV3.2.4 | Input Register |  | 1 |  |  |  |  | 1106 | 41107 | uint16 |  |  | insulation_self_test_started_time_1 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_started_time_1 | Yes | Real value = Modbus value
Insulation Self-test exec countdown |  | SV3.2.5 | Input Register |  | 1 |  |  |  |  | 1107 | 41108 | uint16 |  |  | insulation_self_test_exec_countdown_1 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_exec_countdown_1 | Yes | Real value = Modbus value
Insulation Status update |  | SV3.2.6 | Input Register |  | 1 |  |  |  |  | 1108 | 41109 | uint16 |  |  | insulation_status_update_1 | [11 empty] | /components/pcs_info | pcs_insulation_status_update_1 | Yes | Real value = Modbus value
Insulation Status |  | SV3.3.1 | Input Register |  | 1 |  |  |  |  | 7482 | 47483 | uint16 |  |  | insulation_status_2 | [11 empty] | /components/pcs_info | pcs_insulation_status_2 | Yes | Real value = Modbus value
Insulation Resistor MSB |  | SV3.3.2a | Input Register |  | 1 |  |  |  |  | 7483 | 47484 | uint16 |  |  | insulation_resistor_msb_2 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_msb_2 | Yes
Resistor LSB |  | SV3.3.2b | Input Register |  | 1 |  |  |  |  | 7484 | 47485 | uint16 |  |  | insulation_resistor_lsb_2 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_lsb_2 | Yes | Real value = Modbus value
Insulation Measurement started time |  | SV3.3.3 | Input Register |  | 1 |  |  |  |  | 7485 | 47486 | uint16 |  |  | insulation_measurement_started_time_2 | [11 empty] | /components/pcs_info | pcs_insulation_measurement_started_time_2 | Yes | Real value = Modbus value
Insulation Self-test started time |  | SV3.3.4 | Input Register |  | 1 |  |  |  |  | 7486 | 47487 | uint16 |  |  | insulation_self_test_started_time_2 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_started_time_2 | Yes | Real value = Modbus value
Insulation Self-test exec countdown |  | SV3.3.5 | Input Register |  | 1 |  |  |  |  | 7487 | 47488 | uint16 |  |  | insulation_self_test_exec_countdown_2 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_exec_countdown_2 | Yes | Real value = Modbus value
Insulation Status update |  | SV3.3.6 | Input Register |  | 1 |  |  |  |  | 7488 | 47489 | uint16 |  |  | insulation_status_update_2 | [11 empty] | /components/pcs_info | pcs_insulation_status_update_2 | Yes | Real value = Modbus value
Insulation Status |  | SV3.4.1 | Input Register |  | 1 |  |  |  |  | 7491 | 47492 | uint16 |  |  | insulation_status_3 | [11 empty] | /components/pcs_info | pcs_insulation_status_3 | Yes | Real value = Modbus value
Insulation Resistor MSB |  | SV3.4.2a | Input Register |  | 1 |  |  |  |  | 7492 | 47493 | uint16 |  |  | insulation_resistor_msb_3 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_msb_3 | Yes
Resistor LSB |  | SV3.4.2b | Input Register |  | 1 |  |  |  |  | 7493 | 47494 | uint16 |  |  | insulation_resistor_lsb_3 | [11 empty] | /components/pcs_info | pcs_insulation_resistor_lsb_3 | Yes | Real value = Modbus value
Insulation Measurement started time |  | SV3.4.3 | Input Register |  | 1 |  |  |  |  | 7494 | 47495 | uint16 |  |  | insulation_measurement_started_time_3 | [11 empty] | /components/pcs_info | pcs_insulation_measurement_started_time_3 | Yes | Real value = Modbus value
Insulation Self-test started time |  | SV3.4.4 | Input Register |  | 1 |  |  |  |  | 7495 | 47496 | uint16 |  |  | insulation_self_test_started_time_3 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_started_time_3 | Yes | Real value = Modbus value
Insulation Self-test exec countdown |  | SV3.4.5 | Input Register |  | 1 |  |  |  |  | 7496 | 47497 | uint16 |  |  | insulation_self_test_exec_countdown_3 | [11 empty] | /components/pcs_info | pcs_insulation_self_test_exec_countdown_3 | Yes | Real value = Modbus value
Insulation Status update |  | SV3.4.6 | Input Register |  | 1 |  |  |  |  | 7497 | 47498 | uint16 |  |  | insulation_status_update_3 | [11 empty] | /components/pcs_info | pcs_insulation_status_update_3 | Yes | Real value = Modbus value
Internal Visualization
Current fault |  | SV4.1.1 | Input Register |  | 1 |  |  |  |  | 1120 | 41121 | uint16 |  |  | current_fault | [11 empty] | /components/pcs_info | pcs_current_fault | Yes | Real value = Modbus value
Current fault module |  | SV4.1.1b | Input Register |  | 1 |  |  |  |  | 1130 | 41131 | uint16 |  |  | current_fault_module | [11 empty] | /components/pcs_info | pcs_current_fault_module | Yes | Real value = Modbus value
Current warning |  | SV4.1.2 | Input Register |  | 1 |  |  |  |  | 1121 | 41122 | uint16 |  |  | current_warning | [11 empty] | /components/pcs_info | pcs_current_warning | Yes | Real value = Modbus value
Current status |  | SV4.1.3 | Input Register |  | 1 |  |  |  |  | 1122 | 41123 | uint16 |  |  | current_status | [11 empty] | /components/pcs_info | pcs_current_status | Yes | Real value = Modbus value
Internal temperature |  | SV4.1.4 | Input Register |  | 1 |  |  |  |  | 1123 | 41124 | uint16 |  |  | internal_temperature | [11 empty] | /components/pcs_info | pcs_internal_temperature | Yes | Real value = Modbus value
Max IGBTs temperature |  | SV4.1.5 | Input Register |  | 1 |  |  |  |  | 1124 | 41125 | uint16 |  |  | max_igbts_temperature | [11 empty] | /components/pcs_info | pcs_max_igbts_temperature | Yes | Real value = Modbus value
Max modules temperature |  | SV4.1.6 | Input Register |  | 1 |  |  |  |  | 1125 | 41126 | uint16 |  |  | max_modules_temperature | [11 empty] | /components/pcs_info | pcs_max_modules_temperature | Yes | Real value = Modbus value
Internal input status |  | SV4.1.7 | Input Register |  | 1 |  |  |  |  | 1126 | 41127 | uint16 |  |  | internal_input_status | [11 empty] | /components/pcs_info | pcs_internal_input_status | Yes | Real value = Modbus value
Internal output status |  | SV4.1.8 | Input Register |  | 1 |  |  |  |  | 1127 | 41128 | uint16 |  |  | internal_output_status | [11 empty] | /components/pcs_info | pcs_internal_output_status | Yes | Real value = Modbus value
AC module admission temperature |  | SV4.1.9 | Input Register |  | 1 | 10 |  |  | 0.1 | 1128 | 41129 | uint16 |  |  | ac_module_admission_temperature | [11 empty] | /components/pcs_info | pcs_ac_module_admission_temperature | Yes | Real value = (Modbus value / 10)
Current normative |  | SV4.1.10 | Input Register |  | 1 |  |  |  |  | 1129 | 41130 | uint16 |  |  | current_normative | [11 empty] | /components/pcs_info | pcs_current_normative | Yes | Real value = Modbus value
Internal humidity |  | SV4.1.11 | Input Register |  | 1 |  |  |  |  | 1131 | 41132 | uint16 |  |  | internal_humidity | [11 empty] | /components/pcs_info | pcs_internal_humidity | Yes | Real value = Modbus value
LV manometer |  | SV4.1.12 | Input Register |  | 1 |  |  |  |  | 1132 | 41133 | uint16 |  |  | lv_manometer | [11 empty] | /components/pcs_info | pcs_lv_manometer | Yes | Real value = Modbus value
Power source 1 |  | SV4.1.14 | Input Register |  | 1 | 100 |  |  | 0.01 | 1134 | 41135 | uint16 |  |  | power_source_1 | [11 empty] | /components/pcs_info | pcs_power_source_1 | Yes | Real value = (Modbus value / 100)
Power source 2 |  | SV4.1.15 | Input Register |  | 1 | 100 |  |  | 0.01 | 1135 | 41136 | uint16 |  |  | power_source_2 | [11 empty] | /components/pcs_info | pcs_power_source_2 | Yes | Real value = (Modbus value / 100)
P limit inst |  | SV4.2.1 | Input Register |  | 1 | 10000 |  |  | 0.0001 | 1140 | 41141 | uint16 |  |  | p_limit_inst | [11 empty] | /components/pcs_info | pcs_p_limit_inst | Yes | Real value = (Modbus value / 10000)
Q limit inst |  | SV4.2.2 | Input Register |  | 1 | 10000 |  |  | 0.0001 | 1141 | 41142 | uint16 |  |  | q_limit_inst | [11 empty] | /components/pcs_info | pcs_q_limit_inst | Yes | Real value = (Modbus value / 10000)
Start conditions all |  | SV4.3.1 | Input Register |  | 1 |  |  |  |  | 1150 | 41151 | uint16 |  |  | start_conditions_all | [11 empty] | /components/pcs_info | pcs_start_conditions_all | Yes | Real value = Modbus value
Start conditions V |  | SV4.3.2 | Input Register |  | 1 |  |  |  |  | 1151 | 41152 | uint16 |  |  | start_conditions_v | [11 empty] | /components/pcs_info | pcs_start_conditions_v | Yes | Real value = Modbus value
Start conditions f |  | SV4.3.3 | Input Register |  | 1 |  |  |  |  | 1152 | 41153 | uint16 |  |  | start_conditions_f | [11 empty] | /components/pcs_info | pcs_start_conditions_f | Yes | Real value = Modbus value
Start conditions Vdc |  | SV4.3.4 | Input Register |  | 1 |  |  |  |  | 1153 | 41154 | uint16 |  |  | start_conditions_vdc | [11 empty] | /components/pcs_info | pcs_start_conditions_vdc | Yes | Real value = Modbus value
Start conditions P |  | SV4.3.6 | Input Register |  | 1 |  |  |  |  | 1155 | 41156 | uint16 |  |  | start_conditions_p | [11 empty] | /components/pcs_info | pcs_start_conditions_p | Yes | Real value = Modbus value
Start conditions SOC = No |  | SV4.3.7 | Input Register |  | 1 |  |  |  |  | 1156 | 41157 | uint16 |  |  | start_conditions_soc_no | [11 empty] | /components/pcs_info | pcs_start_conditions_soc_no | Yes | Real value = Modbus value
Inverter type |  | SV4.4.1.1 | Input Register |  | 1 |  |  |  |  | 1182 | 41183 | uint16 |  |  | inverter_type | [11 empty] | /components/pcs_info | pcs_inverter_type | Yes | Real value = Modbus value
Nominal AC voltage |  | SV4.4.1.2 | Input Register |  | 1 |  |  |  |  | 1160 | 41161 | uint16 |  |  | nominal_ac_voltage | [11 empty] | /components/pcs_info | pcs_nominal_ac_voltage | Yes | Real value = Modbus value
Nominal S |  | SV4.4.1.3 | Input Register |  | 1 | 100 |  |  | 0.01 | 1164 | 41165 | uint16 |  |  | nominal_s | [11 empty] | /components/pcs_info | pcs_nominal_s | Yes | Real value = (Modbus value / 100)
Number of modules |  | SV4.4.1.4 | Input Register |  | 1 |  |  |  |  | 1165 | 41166 | uint16 |  |  | number_of_modules | [11 empty] | /components/pcs_info | pcs_number_of_modules | Yes | Real value = Modbus value
Number of BUS = 2 |  | SV4.4.1.4a | Input Register |  | 1 |  |  |  |  | 1169 | 41170 | uint16 |  |  | number_of_bus | [11 empty] | /components/pcs_info | pcs_number_of_bus | Yes | Real value = Modbus value
Number of MPPs |  | SV4.4.1.5 | Input Register |  | 1 |  |  |  |  | 1166 | 41167 | uint16 |  |  | number_of_mpps | [11 empty] | /components/pcs_info | pcs_number_of_mpps | Yes | Real value = Modbus value
Nominal bus voltage |  | SV4.4.1.6 | Input Register |  | 1 |  |  |  |  | 1162 | 41163 | uint16 |  |  | nominal_bus_voltage | [11 empty] | /components/pcs_info | pcs_nominal_bus_voltage | Yes | Real value = Modbus value
Max AC current |  | SV4.4.1.7 | Input Register |  | 1 |  |  |  |  | 1161 | 41162 | uint16 |  |  | max_ac_current | [11 empty] | /components/pcs_info | pcs_max_ac_current | Yes | Real value = Modbus value
Max DC current |  | SV4.4.1.8 | Input Register |  | 1 |  |  |  |  | 1163 | 41164 | uint16 |  |  | max_dc_current | [11 empty] | /components/pcs_info | pcs_max_dc_current | Yes | Real value = Modbus value
Inductive I limit |  | SV4.4.3.1 | Input Register |  | 1 |  |  |  |  | 1183 | 41184 | uint16 |  |  | inductive_i_limit | [11 empty] | /components/pcs_info | pcs_inductive_i_limit | Yes | Real value = Modbus value
Capacitive I limit |  | SV4.4.3.2 | Input Register |  | 1 |  |  |  |  | 1184 | 41185 | uint16 |  |  | capacitive_i_limit | [11 empty] | /components/pcs_info | pcs_capacitive_i_limit | Yes | Real value = Modbus value
Max P limit |  | SV4.4.3.3 | Input Register |  | 1 | 100 |  |  | 0.01 | 1185 | 41186 | uint16 |  |  | max_p_limit | [11 empty] | /components/pcs_info | pcs_max_p_limit | Yes | Real value = (Modbus value / 100)
Max Q limit |  | SV4.4.3.4 | Input Register |  | 1 | 100 |  |  | 0.01 | 1186 | 41187 | uint16 |  |  | max_q_limit | [11 empty] | /components/pcs_info | pcs_max_q_limit | Yes | Real value = (Modbus value / 100)
Max S limit |  | SV4.4.3.5 | Input Register |  | 1 | 100 |  |  | 0.01 | 1187 | 41188 | uint16 |  |  | max_s_limit | [11 empty] | /components/pcs_info | pcs_max_s_limit | Yes | Real value = (Modbus value / 100)
R (mOhm) |  | SV4.4.5.1 | Input Register |  | 1 | 100 |  |  | 0.01 | 1145 | 41146 | uint16 |  |  | r_mohm | [11 empty] | /components/pcs_info | pcs_r_mohm | Yes | Real value = (Modbus value / 100)
L (uH) |  | SV4.4.5.2 | Input Register |  | 1 |  |  |  |  | 1146 | 41147 | uint16 |  |  | l_uh | [11 empty] | /components/pcs_info | pcs_l_uh | Yes | Real value = Modbus value
C (uF) |  | SV4.4.5.3 | Input Register |  | 1 | 100 |  |  | 0.01 | 1147 | 41148 | uint16 |  |  | c_uf | [11 empty] | /components/pcs_info | pcs_c_uf | Yes | Real value = (Modbus value / 100)
Lc (uH) |  | SV4.4.5.4 | Input Register |  | 1 | 100 |  |  | 0.01 | 1148 | 41149 | uint16 |  |  | lc_uh | [11 empty] | /components/pcs_info | pcs_lc_uh | Yes | Real value = (Modbus value / 100)
Counters
Select module |  | SV5.1.1 | Input Register |  | 1 |  |  |  |  | 1200 | 41201 | uint16 |  |  | select_module | [11 empty] | /components/pcs_info | pcs_select_module | Yes | Real value = Modbus value
Daily energy MSB |  | SV5.1.2 | Input Register |  | 1 |  |  |  |  | 1201 | 41202 | uint16 |  |  | daily_energy_msb | [11 empty] | /components/pcs_info | pcs_daily_energy_msb | Yes | – MSB
Daily energy LSB |  | SV5.1.2 | Input Register |  | 1 |  |  |  |  | 1202 | 41203 | uint16 |  |  | daily_energy_lsb | [11 empty] | /components/pcs_info | pcs_daily_energy_lsb | Yes | – LSB Real value = Modbus value
Yesterday energy MSB |  | SV5.1.3 | Input Register |  | 1 |  |  |  |  | 1203 | 41204 | uint16 |  |  | yesterday_energy_msb | [11 empty] | /components/pcs_info | pcs_yesterday_energy_msb | Yes | – MSB
Yesterday energy LSB |  | SV5.1.3 | Input Register |  | 1 |  |  |  |  | 1204 | 41205 | uint16 |  |  | yesterday_energy_lsb | [11 empty] | /components/pcs_info | pcs_yesterday_energy_lsb | Yes | – LSB Real value = Modbus value
Current month energy MSB |  | SV5.1.4 | Input Register |  | 1 |  |  |  |  | 1205 | 41206 | uint16 |  |  | current_month_energy_msb | [11 empty] | /components/pcs_info | pcs_current_month_energy_msb | Yes | – MSB
Current month energy LSB |  | SV5.1.4 | Input Register |  | 1 |  |  |  |  | 1206 | 41207 | uint16 |  |  | current_month_energy_lsb | [11 empty] | /components/pcs_info | pcs_current_month_energy_lsb | Yes | – LSB Real value = Modbus value
Last month energy MSB |  | SV5.1.5 | Input Register |  | 1 |  |  |  |  | 1207 | 41208 | uint16 |  |  | last_month_energy_msb | [11 empty] | /components/pcs_info | pcs_last_month_energy_msb | Yes | – MSB
Last month energy LSB |  | SV5.1.5 | Input Register |  | 1 |  |  |  |  | 1208 | 41209 | uint16 |  |  | last_month_energy_lsb | [11 empty] | /components/pcs_info | pcs_last_month_energy_lsb | Yes | – LSB Real value = Modbus value
Total energy MSB |  | SV5.1.6 | Input Register |  | 1 |  |  |  |  | 1209 | 41210 | uint16 |  |  | total_energy_msb | [11 empty] | /components/pcs_info | pcs_total_energy_msb | Yes | – MSB
Total energy LSB |  | SV5.1.6 | Input Register |  | 1 |  |  |  |  | 1210 | 41211 | uint16 |  |  | total_energy_lsb | [11 empty] | /components/pcs_info | pcs_total_energy_lsb | Yes | – LSB Real value = Modbus value
Consum. daily energy MSB |  | SV5.1.7 | Input Register |  | 1 |  |  |  |  | 1230 | 41231 | uint16 |  |  | consum_daily_energy_msb | [11 empty] | /components/pcs_info | pcs_consum_daily_energy_msb | Yes | – MSB
Consum. daily energy LSB |  | SV5.1.7 | Input Register |  | 1 |  |  |  |  | 1231 | 41232 | uint16 |  |  | consum_daily_energy_lsb | [11 empty] | /components/pcs_info | pcs_consum_daily_energy_lsb | Yes | – LSB Real value = Modbus value
Consum. total energy MSB |  | SV5.1.8 | Input Register |  | 1 |  |  |  |  | 1232 | 41233 | uint16 |  |  | consum_total_energy_msb | [11 empty] | /components/pcs_info | pcs_consum_total_energy_msb | Yes | – MSB
Consum. total energy LSB |  | SV5.1.8 | Input Register |  | 1 |  |  |  |  | 1233 | 41234 | uint16 |  |  | consum_total_energy_lsb | [11 empty] | /components/pcs_info | pcs_consum_total_energy_lsb | Yes | – LSB Real value = Modbus value
Select module reactive energy |  | SV5.2.1 | Input Register |  | 1 |  |  |  |  | 1211 | 41212 | uint16 |  |  | select_module_reactive_energy | [11 empty] | /components/pcs_info | pcs_select_module_reactive_energy | Yes | Real value = Modbus value
Daily reactive energy MSB |  | SV5.2.2 | Input Register |  | 1 |  |  |  |  | 1212 | 41213 | uint16 |  |  | daily_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_daily_reactive_energy_msb | Yes | – MSB
Daily reactive energy LSB |  | SV5.2.2 | Input Register |  | 1 |  |  |  |  | 1213 | 41214 | uint16 |  |  | daily_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_daily_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Yesterday reactive energy MSB |  | SV5.2.3 | Input Register |  | 1 |  |  |  |  | 1214 | 41215 | uint16 |  |  | yesterday_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_yesterday_reactive_energy_msb | Yes | – MSB
Yesterday reactive energy LSB |  | SV5.2.3 | Input Register |  | 1 |  |  |  |  | 1215 | 41216 | uint16 |  |  | yesterday_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_yesterday_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Current month reactive energy MSB |  | SV5.2.4 | Input Register |  | 1 |  |  |  |  | 1216 | 41217 | uint16 |  |  | current_month_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_current_month_reactive_energy_msb | Yes | – MSB
Current month reactive energy LSB |  | SV5.2.4 | Input Register |  | 1 |  |  |  |  | 1217 | 41218 | uint16 |  |  | current_month_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_current_month_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Last month reactive energy MSB |  | SV5.2.5 | Input Register |  | 1 |  |  |  |  | 1218 | 41219 | uint16 |  |  | last_month_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_last_month_reactive_energy_msb | Yes | – MSB
Last month reactive energy LSB |  | SV5.2.5 | Input Register |  | 1 |  |  |  |  | 1219 | 41220 | uint16 |  |  | last_month_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_last_month_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Total reactive energy MSB |  | SV5.2.6 | Input Register |  | 1 |  |  |  |  | 1220 | 41221 | uint16 |  |  | total_reactive_energy_msb | [11 empty] | /components/pcs_info | pcs_total_reactive_energy_msb | Yes | – MSB
Total reactive energy LSB |  | SV5.2.6 | Input Register |  | 1 |  |  |  |  | 1221 | 41222 | uint16 |  |  | total_reactive_energy_lsb | [11 empty] | /components/pcs_info | pcs_total_reactive_energy_lsb | Yes | – LSB Real value = Modbus value
Total run time years |  | SV5.3.1 | Input Register |  | 1 |  |  |  |  | 1222 | 41223 | uint16 |  |  | total_run_time_years | [11 empty] | /components/pcs_info | pcs_total_run_time_years | Yes | Real value = Modbus value
Total run time days |  | SV5.3.2 | Input Register |  | 1 |  |  |  |  | 1223 | 41224 | uint16 |  |  | total_run_time_days | [11 empty] | /components/pcs_info | pcs_total_run_time_days | Yes | Real value = Modbus value
Total run time hours |  | SV5.3.3 | Input Register |  | 1 |  |  |  |  | 1224 | 41225 | uint16 |  |  | total_run_time_hours | [11 empty] | /components/pcs_info | pcs_total_run_time_hours | Yes | Real value = Modbus value
Partial run time years |  | SV5.3.4 | Input Register |  | 1 |  |  |  |  | 1225 | 41226 | uint16 |  |  | partial_run_time_years | [11 empty] | /components/pcs_info | pcs_partial_run_time_years | Yes | Real value = Modbus value
Partial run time days |  | SV5.3.5 | Input Register |  | 1 |  |  |  |  | 1226 | 41227 | uint16 |  |  | partial_run_time_days | [11 empty] | /components/pcs_info | pcs_partial_run_time_days | Yes | Real value = Modbus value
Partial run time hours |  | SV5.3.6 | Input Register |  | 1 |  |  |  |  | 1227 | 41228 | uint16 |  |  | partial_run_time_hours | [11 empty] | /components/pcs_info | pcs_partial_run_time_hours | Yes | Real value = Modbus value
Total number of grid connections |  | SV5.4.1 | Input Register |  | 1 |  |  |  |  | 1228 | 41229 | uint16 |  |  | total_grid_connections | [11 empty] | /components/pcs_info | pcs_total_grid_connections | Yes | Real value = Modbus value
Partial number of grid connections |  | SV5.4.2 | Input Register |  | 1 |  |  |  |  | 1229 | 41230 | uint16 |  |  | partial_grid_connections | [11 empty] | /components/pcs_info | pcs_partial_grid_connections | Yes | Real value = Modbus value
Fault History
Last fault |  | SV6.1 | Input Register |  | 1 |  |  |  |  | 1250 | 41251 | uint16 |  |  | last_fault | [11 empty] | /components/pcs_info | pcs_last_fault | Yes | Real value = Modbus value
Date of last fault |  | SV6.2 | Input Register |  | 1 |  |  |  |  | 1251 | 41252 | uint16 |  |  | last_fault_date | [11 empty] | /components/pcs_info | pcs_last_fault_date | Yes | Day = (Modbus value AND 0xF800) / 2^11
Time of last fault |  |  | Input Register |  | 1 |  |  |  |  | 1252 | 41253 | uint16 |  |  | last_fault_time | [11 empty] | /components/pcs_info | pcs_last_fault_time | Yes | Month = (Modbus value AND 0x0780) / 2^7
9th fault |  | SV6.3 | Input Register |  | 1 |  |  |  |  | 1253 | 41254 | uint16 |  |  | ninth_fault | [11 empty] | /components/pcs_info | pcs_ninth_fault | Yes | Year = (Modbus value AND 0x007F)
Date of 9th fault |  | SV6.4 | Input Register |  | 1 |  |  |  |  | 1254 | 41255 | uint16 |  |  | ninth_fault_date | [11 empty] | /components/pcs_info | pcs_ninth_fault_date | Yes | Hours = (Modbus value AND 0xFF00) / 2^8
Time of 9th fault |  |  | Input Register |  | 1 |  |  |  |  | 1255 | 41256 | uint16 |  |  | ninth_fault_time | [11 empty] | /components/pcs_info | pcs_ninth_fault_time | Yes | Minutes = (Modbus value AND 0x00FF)
8th fault |  | SV6.5 | Input Register |  | 1 |  |  |  |  | 1256 | 41257 | uint16 |  |  | eighth_fault | [11 empty] | /components/pcs_info | pcs_eighth_fault | Yes
Date of 8th fault |  | SV6.6 | Input Register |  | 1 |  |  |  |  | 1257 | 41258 | uint16 |  |  | eighth_fault_date | [11 empty] | /components/pcs_info | pcs_eighth_fault_date | Yes
Time of 8th fault |  |  | Input Register |  | 1 |  |  |  |  | 1258 | 41259 | uint16 |  |  | eighth_fault_time | [11 empty] | /components/pcs_info | pcs_eighth_fault_time | Yes
7th fault |  | SV6.7 | Input Register |  | 1 |  |  |  |  | 1259 | 41260 | uint16 |  |  | seventh_fault | [11 empty] | /components/pcs_info | pcs_seventh_fault | Yes
Date of 7th fault |  | SV6.8 | Input Register |  | 1 |  |  |  |  | 1260 | 41261 | uint16 |  |  | seventh_fault_date | [11 empty] | /components/pcs_info | pcs_seventh_fault_date | Yes
Time of 7th fault |  |  | Input Register |  | 1 |  |  |  |  | 1261 | 41262 | uint16 |  |  | seventh_fault_time | [11 empty] | /components/pcs_info | pcs_seventh_fault_time | Yes
6th fault |  | SV6.9 | Input Register |  | 1 |  |  |  |  | 1262 | 41263 | uint16 |  |  | sixth_fault | [11 empty] | /components/pcs_info | pcs_sixth_fault | Yes
Date of 6th fault |  | SV6.10 | Input Register |  | 1 |  |  |  |  | 1263 | 41264 | uint16 |  |  | sixth_fault_date | [11 empty] | /components/pcs_info | pcs_sixth_fault_date | Yes
Time of 6h fault |  |  | Input Register |  | 1 |  |  |  |  | 1264 | 41265 | uint16 |  |  | sixth_fault_time | [11 empty] | /components/pcs_info | pcs_sixth_fault_time | Yes
5th fault |  | SV6.11 | Input Register |  | 1 |  |  |  |  | 1265 | 41266 | uint16 |  |  | fifth_fault | [11 empty] | /components/pcs_info | pcs_fifth_fault | Yes
Date of 5th fault |  | SV6.12 | Input Register |  | 1 |  |  |  |  | 1266 | 41267 | uint16 |  |  | fifth_fault_date | [11 empty] | /components/pcs_info | pcs_fifth_fault_date | Yes
Time of 5th fault |  |  | Input Register |  | 1 |  |  |  |  | 1267 | 41268 | uint16 |  |  | fifth_fault_time | [11 empty] | /components/pcs_info | pcs_fifth_fault_time | Yes
4th fault |  | SV6.13 | Input Register |  | 1 |  |  |  |  | 1268 | 41269 | uint16 |  |  | fourth_fault | [11 empty] | /components/pcs_info | pcs_fourth_fault | Yes
Date of 4th fault |  | SV6.14 | Input Register |  | 1 |  |  |  |  | 1269 | 41270 | uint16 |  |  | fourth_fault_date | [11 empty] | /components/pcs_info | pcs_fourth_fault_date | Yes
Time of 4th fault |  |  | Input Register |  | 1 |  |  |  |  | 1270 | 41271 | uint16 |  |  | fourth_fault_time | [11 empty] | /components/pcs_info | pcs_fourth_fault_time | Yes
3rd fault |  | SV6.15 | Input Register |  | 1 |  |  |  |  | 1271 | 41272 | uint16 |  |  | third_fault | [11 empty] | /components/pcs_info | pcs_third_fault | Yes
Date of 3rd fault |  | SV6.16 | Input Register |  | 1 |  |  |  |  | 1272 | 41273 | uint16 |  |  | third_fault_date | [11 empty] | /components/pcs_info | pcs_third_fault_date | Yes
Time of 3rd fault |  |  | Input Register |  | 1 |  |  |  |  | 1273 | 41274 | uint16 |  |  | third_fault_time | [11 empty] | /components/pcs_info | pcs_third_fault_time | Yes
2nd fault |  | SV6.17 | Input Register |  | 1 |  |  |  |  | 1274 | 41275 | uint16 |  |  | second_fault | [11 empty] | /components/pcs_info | pcs_second_fault | Yes
Date of 2nd fault |  | SV6.18 | Input Register |  | 1 |  |  |  |  | 1275 | 41276 | uint16 |  |  | second_fault_date | [11 empty] | /components/pcs_info | pcs_second_fault_date | Yes
Time of 2nd fault |  |  | Input Register |  | 1 |  |  |  |  | 1276 | 41277 | uint16 |  |  | second_fault_time | [11 empty] | /components/pcs_info | pcs_second_fault_time | Yes
1st fault |  | SV6.19 | Input Register |  | 1 |  |  |  |  | 1277 | 41278 | uint16 |  |  | first_fault | [11 empty] | /components/pcs_info | pcs_first_fault | Yes
Date of 1st fault |  | SV6.20 | Input Register |  | 1 |  |  |  |  | 1278 | 41279 | uint16 |  |  | first_fault_date | [11 empty] | /components/pcs_info | pcs_first_fault_date | Yes
Time of 1st fault |  |  | Input Register |  | 1 |  |  |  |  | 1279 | 41280 | uint16 |  |  | first_fault_time | [11 empty] | /components/pcs_info | pcs_first_fault_time | Yes
Warning History
Last warning |  | SV7.1 | Input Register |  | 1 |  |  |  |  | 1300 | 41301 | uint16 |  |  | last_warning | [11 empty] | /components/pcs_info | pcs_last_warning | Yes | Real value = Modbus value
Date of last warning |  | SV7.2 | Input Register |  | 1 |  |  |  |  | 1301 | 41302 | uint16 |  |  | last_warning_date | [11 empty] | /components/pcs_info | pcs_last_warning_date | Yes | Day = (Modbus value AND 0xF800) / 2^11
Time of last warning |  |  | Input Register |  | 1 |  |  |  |  | 1302 | 41303 | uint16 |  |  | last_warning_time | [11 empty] | /components/pcs_info | pcs_last_warning_time | Yes | Month = (Modbus value AND 0x0780) / 2^7
9th warning |  | SV7.3 | Input Register |  | 1 |  |  |  |  | 1303 | 41304 | uint16 |  |  | ninth_warning | [11 empty] | /components/pcs_info | pcs_ninth_warning | Yes | Year = (Modbus value AND 0x007F)
Date of 9th warning |  | SV7.4 | Input Register |  | 1 |  |  |  |  | 1304 | 41305 | uint16 |  |  | ninth_warning_date | [11 empty] | /components/pcs_info | pcs_ninth_warning_date | Yes | Hours = (Modbus value AND 0xFF00) / 2^8
Time of 9th warning |  |  | Input Register |  | 1 |  |  |  |  | 1305 | 41306 | uint16 |  |  | ninth_warning_time | [11 empty] | /components/pcs_info | pcs_ninth_warning_time | Yes | Minutes = (Modbus value AND 0x00FF)
8th warning |  | SV7.5 | Input Register |  | 1 |  |  |  |  | 1306 | 41307 | uint16 |  |  | eighth_warning | [11 empty] | /components/pcs_info | pcs_eighth_warning | Yes
Date of 8th warning |  | SV7.6 | Input Register |  | 1 |  |  |  |  | 1307 | 41308 | uint16 |  |  | eighth_warning_date | [11 empty] | /components/pcs_info | pcs_eighth_warning_date | Yes
Time of 8th warning |  |  | Input Register |  | 1 |  |  |  |  | 1308 | 41309 | uint16 |  |  | eighth_warning_time | [11 empty] | /components/pcs_info | pcs_eighth_warning_time | Yes
7th warning |  | SV7.7 | Input Register |  | 1 |  |  |  |  | 1309 | 41310 | uint16 |  |  | seventh_warning | [11 empty] | /components/pcs_info | pcs_seventh_warning | Yes
Date of 7th warning |  | SV7.8 | Input Register |  | 1 |  |  |  |  | 1310 | 41311 | uint16 |  |  | seventh_warning_date | [11 empty] | /components/pcs_info | pcs_seventh_warning_date | Yes
Time of 7th warning |  |  | Input Register |  | 1 |  |  |  |  | 1311 | 41312 | uint16 |  |  | seventh_warning_time | [11 empty] | /components/pcs_info | pcs_seventh_warning_time | Yes
6th warning |  | SV7.9 | Input Register |  | 1 |  |  |  |  | 1312 | 41313 | uint16 |  |  | sixth_warning | [11 empty] | /components/pcs_info | pcs_sixth_warning | Yes
Date of 6th warning |  | SV7.10 | Input Register |  | 1 |  |  |  |  | 1313 | 41314 | uint16 |  |  | sixth_warning_date | [11 empty] | /components/pcs_info | pcs_sixth_warning_date | Yes
Time of 6h warning |  |  | Input Register |  | 1 |  |  |  |  | 1314 | 41315 | uint16 |  |  | sixth_warning_time | [11 empty] | /components/pcs_info | pcs_sixth_warning_time | Yes
5th warning |  | SV7.11 | Input Register |  | 1 |  |  |  |  | 1315 | 41316 | uint16 |  |  | fifth_warning | [11 empty] | /components/pcs_info | pcs_fifth_warning | Yes
Date of 5th warning |  | SV7.12 | Input Register |  | 1 |  |  |  |  | 1316 | 41317 | uint16 |  |  | fifth_warning_date | [11 empty] | /components/pcs_info | pcs_fifth_warning_date | Yes
Time of 5th warning |  |  | Input Register |  | 1 |  |  |  |  | 1317 | 41318 | uint16 |  |  | fifth_warning_time | [11 empty] | /components/pcs_info | pcs_fifth_warning_time | Yes
4th warning |  | SV7.13 | Input Register |  | 1 |  |  |  |  | 1318 | 41319 | uint16 |  |  | fourth_warning | [11 empty] | /components/pcs_info | pcs_fourth_warning | Yes
Date of 4th warning |  | SV7.14 | Input Register |  | 1 |  |  |  |  | 1319 | 41320 | uint16 |  |  | fourth_warning_date | [11 empty] | /components/pcs_info | pcs_fourth_warning_date | Yes
Time of 4th warning |  |  | Input Register |  | 1 |  |  |  |  | 1320 | 41321 | uint16 |  |  | fourth_warning_time | [11 empty] | /components/pcs_info | pcs_fourth_warning_time | Yes
3rd warning |  | SV7.15 | Input Register |  | 1 |  |  |  |  | 1321 | 41322 | uint16 |  |  | third_warning | [11 empty] | /components/pcs_info | pcs_third_warning | Yes
Date of 3rd warning |  | SV7.16 | Input Register |  | 1 |  |  |  |  | 1322 | 41323 | uint16 |  |  | third_warning_date | [11 empty] | /components/pcs_info | pcs_third_warning_date | Yes
Time of 3rd warning |  |  | Input Register |  | 1 |  |  |  |  | 1323 | 41324 | uint16 |  |  | third_warning_time | [11 empty] | /components/pcs_info | pcs_third_warning_time | Yes
2nd warning |  | SV7.17 | Input Register |  | 1 |  |  |  |  | 1324 | 41325 | uint16 |  |  | second_warning | [11 empty] | /components/pcs_info | pcs_second_warning | Yes
Date of 2nd warning |  | SV7.18 | Input Register |  | 1 |  |  |  |  | 1325 | 41326 | uint16 |  |  | second_warning_date | [11 empty] | /components/pcs_info | pcs_second_warning_date | Yes
Time of 2nd warning |  |  | Input Register |  | 1 |  |  |  |  | 1326 | 41327 | uint16 |  |  | second_warning_time | [11 empty] | /components/pcs_info | pcs_second_warning_time | Yes
1st warning |  | SV7.19 | Input Register |  | 1 |  |  |  |  | 1327 | 41328 | uint16 |  |  | first_warning | [11 empty] | /components/pcs_info | pcs_first_warning | Yes
Date of 1st warning |  | SV7.20 | Input Register |  | 1 |  |  |  |  | 1328 | 41329 | uint16 |  |  | first_warning_date | [11 empty] | /components/pcs_info | pcs_first_warning_date | Yes
Time of 1st warning |  |  | Input Register |  | 1 |  |  |  |  | 1329 | 41330 | uint16 |  |  | first_warning_time | [11 empty] | /components/pcs_info | pcs_first_warning_time | Yes
Event History
Last event |  | SV8.1 | Input Register |  | 1 |  |  |  |  | 1350 | 41351 | uint16 |  |  | last_event | [11 empty] | /components/pcs_info | pcs_last_event | Yes | Real value = Modbus value
Date of last event |  | SV8.2 | Input Register |  | 1 |  |  |  |  | 1351 | 41352 | uint16 |  |  | last_event_date | [11 empty] | /components/pcs_info | pcs_last_event_date | Yes | Day = (Modbus value AND 0xF800) / 2^11
Time of last event |  |  | Input Register |  | 1 |  |  |  |  | 1352 | 41353 | uint16 |  |  | last_event_time | [11 empty] | /components/pcs_info | pcs_last_event_time | Yes | Month = (Modbus value AND 0x0780) / 2^7
9th event |  | SV8.3 | Input Register |  | 1 |  |  |  |  | 1353 | 41354 | uint16 |  |  | ninth_event | [11 empty] | /components/pcs_info | pcs_ninth_event | Yes | Year = (Modbus value AND 0x007F)
Date of 9th event |  | SV8.4 | Input Register |  | 1 |  |  |  |  | 1354 | 41355 | uint16 |  |  | ninth_event_date | [11 empty] | /components/pcs_info | pcs_ninth_event_date | Yes | Hours = (Modbus value AND 0xFF00) / 2^8
Time of 9th event |  |  | Input Register |  | 1 |  |  |  |  | 1355 | 41356 | uint16 |  |  | ninth_event_time | [11 empty] | /components/pcs_info | pcs_ninth_event_time | Yes | Minutes = (Modbus value AND 0x00FF)
8th event |  | SV8.5 | Input Register |  | 1 |  |  |  |  | 1356 | 41357 | uint16 |  |  | eighth_event | [11 empty] | /components/pcs_info | pcs_eighth_event | Yes
Date of 8th event |  | SV8.6 | Input Register |  | 1 |  |  |  |  | 1357 | 41358 | uint16 |  |  | eighth_event_date | [11 empty] | /components/pcs_info | pcs_eighth_event_date | Yes
Time of 8th event |  |  | Input Register |  | 1 |  |  |  |  | 1358 | 41359 | uint16 |  |  | eighth_event_time | [11 empty] | /components/pcs_info | pcs_eighth_event_time | Yes
7th event |  | SV8.7 | Input Register |  | 1 |  |  |  |  | 1359 | 41360 | uint16 |  |  | seventh_event | [11 empty] | /components/pcs_info | pcs_seventh_event | Yes
Date of 7th event |  | SV8.8 | Input Register |  | 1 |  |  |  |  | 1360 | 41361 | uint16 |  |  | seventh_event_date | [11 empty] | /components/pcs_info | pcs_seventh_event_date | Yes
Time of 7th event |  |  | Input Register |  | 1 |  |  |  |  | 1361 | 41362 | uint16 |  |  | seventh_event_time | [11 empty] | /components/pcs_info | pcs_seventh_event_time | Yes
6th event |  | SV8.9 | Input Register |  | 1 |  |  |  |  | 1362 | 41363 | uint16 |  |  | sixth_event | [11 empty] | /components/pcs_info | pcs_sixth_event | Yes
Date of 6th event |  | SV8.10 | Input Register |  | 1 |  |  |  |  | 1363 | 41364 | uint16 |  |  | sixth_event_date | [11 empty] | /components/pcs_info | pcs_sixth_event_date | Yes
Time of 6h event |  |  | Input Register |  | 1 |  |  |  |  | 1364 | 41365 | uint16 |  |  | sixth_event_time | [11 empty] | /components/pcs_info | pcs_sixth_event_time | Yes
5th event |  | SV8.11 | Input Register |  | 1 |  |  |  |  | 1365 | 41366 | uint16 |  |  | fifth_event | [11 empty] | /components/pcs_info | pcs_fifth_event | Yes
Date of 5th event |  | SV8.12 | Input Register |  | 1 |  |  |  |  | 1366 | 41367 | uint16 |  |  | fifth_event_date | [11 empty] | /components/pcs_info | pcs_fifth_event_date | Yes
Time of 5th event |  |  | Input Register |  | 1 |  |  |  |  | 1367 | 41368 | uint16 |  |  | fifth_event_time | [11 empty] | /components/pcs_info | pcs_fifth_event_time | Yes
4th event |  | SV8.13 | Input Register |  | 1 |  |  |  |  | 1368 | 41369 | uint16 |  |  | fourth_event | [11 empty] | /components/pcs_info | pcs_fourth_event | Yes
Date of 4th event |  | SV8.14 | Input Register |  | 1 |  |  |  |  | 1369 | 41370 | uint16 |  |  | fourth_event_date | [11 empty] | /components/pcs_info | pcs_fourth_event_date | Yes
Time of 4th event |  |  | Input Register |  | 1 |  |  |  |  | 1370 | 41371 | uint16 |  |  | fourth_event_time | [11 empty] | /components/pcs_info | pcs_fourth_event_time | Yes
3rd event |  | SV8.15 | Input Register |  | 1 |  |  |  |  | 1371 | 41372 | uint16 |  |  | third_event | [11 empty] | /components/pcs_info | pcs_third_event | Yes
Date of 3rd event |  | SV8.16 | Input Register |  | 1 |  |  |  |  | 1372 | 41373 | uint16 |  |  | third_event_date | [11 empty] | /components/pcs_info | pcs_third_event_date | Yes
Time of 3rd event |  |  | Input Register |  | 1 |  |  |  |  | 1373 | 41374 | uint16 |  |  | third_event_time | [11 empty] | /components/pcs_info | pcs_third_event_time | Yes
2nd event |  | SV8.17 | Input Register |  | 1 |  |  |  |  | 1374 | 41375 | uint16 |  |  | second_event | [11 empty] | /components/pcs_info | pcs_second_event | Yes
Date of 2nd event |  | SV8.18 | Input Register |  | 1 |  |  |  |  | 1375 | 41376 | uint16 |  |  | second_event_date | [11 empty] | /components/pcs_info | pcs_second_event_date | Yes
Time of 2nd event |  |  | Input Register |  | 1 |  |  |  |  | 1376 | 41377 | uint16 |  |  | second_event_time | [11 empty] | /components/pcs_info | pcs_second_event_time | Yes
1st event |  | SV8.19 | Input Register |  | 1 |  |  |  |  | 1377 | 41378 | uint16 |  |  | first_event | [11 empty] | /components/pcs_info | pcs_first_event | Yes
Date of 1st event |  | SV8.20 | Input Register |  | 1 |  |  |  |  | 1378 | 41379 | uint16 |  |  | first_event_date | [11 empty] | /components/pcs_info | pcs_first_event_date | Yes
Time of 1st event |  |  | Input Register |  | 1 |  |  |  |  | 1379 | 41380 | uint16 |  |  | first_event_time | [11 empty] | /components/pcs_info | pcs_first_event_time | Yes
Modules Information
Running modules |  | SV9.1.1 | Input Register |  | 1 |  |  |  |  | 1390 | 41391 | uint16 |  |  | running_modules | [11 empty] | /components/pcs_info | pcs_running_modules | Yes | Real value = Modbus value
Num running modules |  | SV9.1.2 | Input Register |  | 1 |  |  |  |  | 1391 | 41392 | uint16 |  |  | num_running_modules | [11 empty] | /components/pcs_info | pcs_num_running_modules | Yes | Real value = Modbus value
Next starting module |  | SV9.1.3 | Input Register |  | 1 |  |  |  |  | 1392 | 41393 | uint16 |  |  | next_starting_module | [11 empty] | /components/pcs_info | pcs_next_starting_module | Yes | Real value = Modbus value
Modules start stop |  | SV9.1.4 | Input Register |  | 1 |  |  |  |  | 1393 | 41394 | uint16 |  |  | modules_start_stop | [11 empty] | /components/pcs_info | pcs_modules_start_stop | Yes | Real value = Modbus value
Modules enable reg |  | SV9.1.5 | Input Register |  | 1 |  |  |  |  | 1394 | 41395 | uint16 |  |  | modules_enable_reg | [11 empty] | /components/pcs_info | pcs_modules_enable_reg | Yes | Real value = Modbus value
Selected module |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 1400 | 41401 | uint16 |  |  | selected_module | [11 empty] | /components/pcs_info | pcs_selected_module | Yes | Real value = Modbus value
Module status |  | SV9.3 | Input Register |  | 1 |  |  |  |  | 1401 | 41402 | uint16 |  |  | module_status | [11 empty] | /components/pcs_info | pcs_module_status | Yes | Real value = Modbus value
Current R |  | SV9.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 1402 | 41403 | uint16 |  |  | current_r | [11 empty] | /components/pcs_info | pcs_current_r | Yes | Real value = (Modbus value / 10)
Current S |  | SV9.5 | Input Register |  | 1 | 10 |  |  | 0.1 | 1403 | 41404 | uint16 |  |  | current_s | [11 empty] | /components/pcs_info | pcs_current_s | Yes | Real value = (Modbus value / 10)
Current T |  | SV9.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 1404 | 41405 | uint16 |  |  | current_t | [11 empty] | /components/pcs_info | pcs_current_t | Yes | Real value = (Modbus value / 10)
DC current |  | SV9.7 | Input Register |  | 1 | 10 |  |  | 0.1 | 1405 | 41406 | uint16 |  |  | dc_current | [11 empty] | /components/pcs_info | pcs_dc_current | Yes | Real value = (Modbus value / 10)
DC voltage (P) |  | SV9.8 | Input Register |  | 1 |  |  |  |  | 1406 | 41407 | uint16 |  |  | dc_voltage_p | [11 empty] | /components/pcs_info | pcs_dc_voltage_p | Yes | Real value = Modbus value
DC voltage (N) |  | SV9.9 | Input Register |  | 1 |  |  |  |  | 1407 | 41408 | uint16 |  |  | dc_voltage_n | [11 empty] | /components/pcs_info | pcs_dc_voltage_n | Yes | Real value = Modbus value
DC voltage |  | SV9.10 | Input Register |  | 1 |  |  |  |  | 1408 | 41409 | uint16 |  |  | dc_voltage | [11 empty] | /components/pcs_info | pcs_dc_voltage | Yes | Real value = Modbus value
P |  | SV9.11 | Input Register |  | 1 | 10 |  |  | 0.1 | 1409 | 41410 | uint16 |  |  | p | [11 empty] | /components/pcs_info | pcs_p | Yes | Real value = (Modbus value / 10)
Q |  | SV9.12 | Input Register |  | 1 | 10 |  |  | 0.1 | 1410 | 41411 | uint16 |  |  | q | [11 empty] | /components/pcs_info | pcs_q | Yes | Real value = (Modbus value / 10)
Ambient temperature |  | SV9.13 | Input Register |  | 1 |  |  |  |  | 1411 | 41412 | uint16 |  |  | ambient_temperature | [11 empty] | /components/pcs_info | pcs_ambient_temperature | Yes | Real value = Modbus value
Max temperature |  | SV9.14 | Input Register |  | 1 |  |  |  |  | 1412 | 41413 | uint16 |  |  | max_temperature | [11 empty] | /components/pcs_info | pcs_max_temperature | Yes | Real value = Modbus value
I/O status |  | SV9.15 | Input Register |  | 1 |  |  |  |  | 1413 | 41414 | uint16 |  |  | i_o_status | [11 empty] | /components/pcs_info | pcs_i_o_status | Yes | Real value = Modbus value
Temperature R1 |  | SV9.18 | Input Register |  | 1 |  |  |  |  | 1416 | 41417 | uint16 |  |  | temperature_r1 | [11 empty] | /components/pcs_info | pcs_temperature_r1 | Yes | Real value = Modbus value
Temperature R2 |  | SV9.19 | Input Register |  | 1 |  |  |  |  | 1417 | 41418 | uint16 |  |  | temperature_r2 | [11 empty] | /components/pcs_info | pcs_temperature_r2 | Yes | Real value = Modbus value
Temperature R3 |  | SV9.20 | Input Register |  | 1 |  |  |  |  | 1418 | 41419 | uint16 |  |  | temperature_r3 | [11 empty] | /components/pcs_info | pcs_temperature_r3 | Yes | Real value = Modbus value
Temperature S1 |  | SV9.21 | Input Register |  | 1 |  |  |  |  | 1419 | 41420 | uint16 |  |  | temperature_s1 | [11 empty] | /components/pcs_info | pcs_temperature_s1 | Yes | Real value = Modbus value
Temperature S2 |  | SV9.22 | Input Register |  | 1 |  |  |  |  | 1420 | 41421 | uint16 |  |  | temperature_s2 | [11 empty] | /components/pcs_info | pcs_temperature_s2 | Yes | Real value = Modbus value
Temperature S3 |  | SV9.23 | Input Register |  | 1 |  |  |  |  | 1421 | 41422 | uint16 |  |  | temperature_s3 | [11 empty] | /components/pcs_info | pcs_temperature_s3 | Yes | Real value = Modbus value
Temperature T1 |  | SV9.24 | Input Register |  | 1 |  |  |  |  | 1422 | 41423 | uint16 |  |  | temperature_t1 | [11 empty] | /components/pcs_info | pcs_temperature_t1 | Yes | Real value = Modbus value
Temperature T2 |  | SV9.25 | Input Register |  | 1 |  |  |  |  | 1423 | 41424 | uint16 |  |  | temperature_t2 | [11 empty] | /components/pcs_info | pcs_temperature_t2 | Yes | Real value = Modbus value
Temperature T3 |  | SV9.26 | Input Register |  | 1 |  |  |  |  | 1424 | 41425 | uint16 |  |  | temperature_t3 | [11 empty] | /components/pcs_info | pcs_temperature_t3 | Yes | Real value = Modbus value
Module Visualization Parameters
Module 1 Status |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5000 | 45001 | uint16 |  |  | module_1_status | [13 empty] | Yes | Real value = Modbus value
Module 1 Current R |  | SV9.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 5001 | 45002 | int16 |  |  | module_1_current_r | [13 empty] | Yes | Real value = (Modbus value / 10)
Module 1 Current S |  | SV9.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 5002 | 45003 | int16 |  |  | module_1_current_s | [13 empty] | Yes | Real value = (Modbus value / 10)
Module 1 Current T |  | SV9.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 5003 | 45004 | int16 |  |  | module_1_current_t | [13 empty] | Yes | Real value = (Modbus value / 10)
Module 1 DC current |  | SV9.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 5004 | 45005 | int16 |  |  | module_1_dc_current | [13 empty] | Yes | Real value = (Modbus value / 10)
Module 1 DC voltage (P) |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5005 | 45006 | uint16 |  |  | module_1_dc_voltage_p | [13 empty] | Yes | Real value = Modbus value
Module 1 DC voltage (N) |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5006 | 45007 | uint16 |  |  | module_1_dc_voltage_n | [13 empty] | Yes | Real value = Modbus value
Module 1 DC voltage |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5007 | 45008 | uint16 |  |  | module_1_dc_voltage | [13 empty] | Yes | Real value = Modbus value
Module 1 P |  | SV9.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 5008 | 45009 | int16 |  |  | module_1_p | [13 empty] | Yes | Real value = (Modbus value / 10)
Module 1 Q |  | SV9.2 | Input Register |  | 1 | 10 |  |  | 0.1 | 5009 | 45010 | int16 |  |  | module_1_q | [13 empty] | Yes | Real value = (Modbus value / 10)
Module 1 Ambient temperature |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5010 | 45011 | uint16 |  |  | module_1_ambient_temp | [13 empty] | Yes | Real value = Modbus value
Module 1 Max temperature |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5011 | 45012 | uint16 |  |  | module_1_max_temp | [13 empty] | Yes | Real value = Modbus value
Module 1 I/O status |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5012 | 45013 | uint16 |  |  | module_1_i_o_status | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature R1 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5022 | 45023 | uint16 |  |  | module_1_temp_r1 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature R2 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5023 | 45024 | uint16 |  |  | module_1_temp_r2 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature R3 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5024 | 45025 | uint16 |  |  | module_1_temp_r3 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature S1 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5025 | 45026 | uint16 |  |  | module_1_temp_s1 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature S2 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5026 | 45027 | uint16 |  |  | module_1_temp_s2 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature S3 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5027 | 45028 | uint16 |  |  | module_1_temp_s3 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature T1 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5028 | 45029 | uint16 |  |  | module_1_temp_t1 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature T2 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5029 | 45030 | uint16 |  |  | module_1_temp_t2 | [13 empty] | Yes | Real value = Modbus value
Module 1 Temperature T3 |  | SV9.2 | Input Register |  | 1 |  |  |  |  | 5030 | 45031 | uint16 |  |  | module_1_temp_t3 | [13 empty] | Yes | Real value = Modbus value
module_1 |  | SV9.2 | Input Register |  | 30 |  |  |  |  | 5032 | 45033 | repeat |  | 5000 | module_2 | [13 empty] | Yes
module_1 |  | SV9.2 | Input Register |  | 30 |  |  |  |  | 5064 | 45065 | repeat |  | 5000 | module_3 | [13 empty] | Yes
module_1 |  | SV9.2 | Input Register |  | 30 |  |  |  |  | 5096 | 45097 | repeat |  | 5000 | module_4 | [13 empty] | Yes
module_1 |  | SV9.2 | Input Register |  | 30 |  |  |  |  | 5128 | 45129 | repeat |  | 5000 | module_5 | [13 empty] | Yes
module_1 |  | SV9.2 | Input Register |  | 30 |  |  |  |  | 5160 | 45161 | repeat |  | 5000 | module_6
DU
DU Feedback Status |  | SV10.10 | Input Register |  | 1 |  |  |  |  | 7423 | 47424 | uint16 |  |  | du_feedback_status | [11 empty] | /components/pcs_info | pcs_du_feedback_status | Yes | Real value = Modbus value
BMS Summary
BMS Status |  | SV15.1.1 | Input Register |  | 1 |  |  |  |  | 7450 | 47451 | uint16 |  |  | bms1_status | [11 empty] | /components/pcs_info | pcs_bms1_status | Yes | Real value = Modbus value
Strings In Service |  | SV15.1.2 | Input Register |  | 1 |  |  |  |  | 7451 | 47452 | uint16 |  |  | bms1_strings_in_service | [11 empty] | /components/pcs_info | pcs_bms1_strings_in_service | Yes | Real value = Modbus value
Total Strings Count |  | SV15.1.3 | Input Register |  | 1 |  |  |  |  | 7452 | 47453 | uint16 |  |  | bms1_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms1_total_strings_count | Yes | Real value = Modbus value
System Voltage |  | SV15.1.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 7453 | 47454 | uint16 |  |  | bms1_system_voltage | [11 empty] | /components/pcs_info | pcs_bms1_system_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV15.1.5 | Input Register |  | 1 |  |  |  |  | 7454 | 47455 | uint16 |  |  | bms1_system_current | [11 empty] | /components/pcs_info | pcs_bms1_system_current | Yes | Real value = Modbus value
System SOC |  | SV15.1.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 7455 | 47456 | uint16 |  |  | bms1_system_soc | [11 empty] | /components/pcs_info | pcs_bms1_system_soc | Yes | Real value = (Modbus value / 10)
BMS Status |  | SV15.2.1 | Input Register |  | 1 |  |  |  |  | 7456 | 47457 | uint16 |  |  | bms2_status | [11 empty] | /components/pcs_info | pcs_bms2_status | Yes | Real value = Modbus value
Strings In Service |  | SV15.2.2 | Input Register |  | 1 |  |  |  |  | 7457 | 47458 | uint16 |  |  | bms2_strings_in_service | [11 empty] | /components/pcs_info | pcs_bms2_strings_in_service | Yes | Real value = Modbus value
Total Strings Count |  | SV15.2.3 | Input Register |  | 1 |  |  |  |  | 7458 | 47459 | uint16 |  |  | bms2_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms2_total_strings_count | Yes | Real value = Modbus value
System Voltage |  | SV15.2.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 7459 | 47460 | uint16 |  |  | bms2_system_voltage | [11 empty] | /components/pcs_info | pcs_bms2_system_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV15.2.5 | Input Register |  | 1 |  |  |  |  | 7460 | 47461 | uint16 |  |  | bms2_system_current | [11 empty] | /components/pcs_info | pcs_bms2_system_current | Yes | Real value = Modbus value
System SOC |  | SV15.2.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 7461 | 47462 | uint16 |  |  | bms2_system_soc | [11 empty] | /components/pcs_info | pcs_bms2_system_soc | Yes | Real value = (Modbus value / 10)
BMS Status |  | SV15.3.1 | Input Register |  | 1 |  |  |  |  | 7462 | 47463 | uint16 |  |  | bms3_status | [11 empty] | /components/pcs_info | pcs_bms3_status | Yes | Real value = Modbus value
Strings In Service |  | SV15.3.2 | Input Register |  | 1 |  |  |  |  | 7463 | 47464 | uint16 |  |  | bms3_strings_in_service | [11 empty] | /components/pcs_info | pcs_bms3_strings_in_service | Yes | Real value = Modbus value
Total Strings Count |  | SV15.3.3 | Input Register |  | 1 |  |  |  |  | 7464 | 47465 | uint16 |  |  | bms3_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms3_total_strings_count | Yes | Real value = Modbus value
System Voltage |  | SV15.3.4 | Input Register |  | 1 | 10 |  |  | 0.1 | 7465 | 47466 | uint16 |  |  | bms3_system_voltage | [11 empty] | /components/pcs_info | pcs_bms3_system_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV15.3.5 | Input Register |  | 1 | 10 |  |  | 0.1 | 7466 | 47467 | uint16 |  |  | bms3_system_current | [11 empty] | /components/pcs_info | pcs_bms3_system_current | Yes | Real value = (Modbus value / 10)
System SOC |  | SV15.3.6 | Input Register |  | 1 |  |  |  |  | 7467 | 47468 | uint16 |  |  | bms3_system_soc | [11 empty] | /components/pcs_info | pcs_bms3_system_soc | Yes | Real value = Modbus value
BMS Information
BMS Select |  | SV16.1.1 | Input Register |  | 1 | 10 |  |  | 0.1 | 7500 | 47501 | uint16 |  |  | bms_select | [11 empty] | /components/pcs_info | pcs_bms_select | Yes | Real value = (Modbus value / 10)
Sys heartbeat |  | SV16.1.2 | Input Register |  | 1 |  |  |  |  | 7501 | 47502 | uint16 |  |  | bms_sys_heartbeat | [11 empty] | /components/pcs_info | pcs_bms_sys_heartbeat | Yes | Real value = Modbus value
Strings In Service |  | SV16.1.3 | Input Register |  | 1 |  |  |  |  | 7502 | 47503 | uint16 |  |  | bms_strings_service | [11 empty] | /components/pcs_info | pcs_bms_strings_service | Yes | Real value = Modbus value
Total Strings Count |  | SV16.1.4 | Input Register |  | 1 |  |  |  |  | 7503 | 47504 | uint16 |  |  | bms_total_strings_count | [11 empty] | /components/pcs_info | pcs_bms_total_strings_count | Yes | Real value = Modbus value
Service Voltage |  | SV16.1.5 | Input Register |  | 1 | 10 |  |  | 0.1 | 7504 | 47505 | uint16 |  |  | bms_service_voltage | [11 empty] | /components/pcs_info | pcs_bms_service_voltage | Yes | Real value = (Modbus value / 10)
Service SOC |  | SV16.1.6 | Input Register |  | 1 | 10 |  |  | 0.1 | 7505 | 47506 | uint16 |  |  | bms_service_soc | [11 empty] | /components/pcs_info | pcs_bms_service_soc | Yes | Real value = (Modbus value / 10)
System Voltage |  | SV16.1.7 | Input Register |  | 1 | 10 |  |  | 0.1 | 7506 | 47507 | uint16 |  |  | bms_voltage | [11 empty] | /components/pcs_info | pcs_bms_voltage | Yes | Real value = (Modbus value / 10)
System Current |  | SV16.1.8 | Input Register |  | 1 |  |  |  |  | 7507 | 47508 | uint16 |  |  | bms_current | [11 empty] | /components/pcs_info | pcs_bms_current | Yes | Real value = Modbus value
System SOC |  | SV16.1.9 | Input Register |  | 1 | 10 |  |  | 0.1 | 7508 | 47509 | uint16 |  |  | bms_soc | [11 empty] | /components/pcs_info | pcs_bms_soc | Yes | Real value = (Modbus value / 10)
System SOH |  | SV16.1.10 | Input Register |  | 1 | 10 |  |  | 0.1 | 7509 | 47510 | uint16 |  |  | bms_soh | [11 empty] | /components/pcs_info | pcs_bms_soh | Yes | Real value = (Modbus value / 10)
System Mode |  | SV16.1.11 | Input Register |  | 1 |  |  |  |  | 7510 | 47511 | uint16 |  |  | bms_mode | [11 empty] | /components/pcs_info | pcs_bms_mode | Yes | Real value = Modbus value
Max Cell Volt Sys |  | SV16.1.12 | Input Register |  | 1 |  |  |  |  | 7511 | 47512 | uint16 |  |  | bms_max_v | [11 empty] | /components/pcs_info | pcs_bms_max_v | Yes | Real value = Modbus value
Min Cell Volt Sys |  | SV16.1.13 | Input Register |  | 1 |  |  |  |  | 7512 | 47513 | uint16 |  |  | bms_min_v | [11 empty] | /components/pcs_info | pcs_bms_min_v | Yes | Real value = Modbus value
Max Cell Temp Sys |  | SV16.1.14 | Input Register |  | 1 | 100 |  |  | 0.01 | 7513 | 47514 | uint16 |  |  | bms_max_temp | [11 empty] | /components/pcs_info | pcs_bms_max_temp | Yes | Real value = (Modbus value / 100)
Min Cell Temp Sys |  | SV16.1.15 | Input Register |  | 1 | 100 |  |  | 0.01 | 7514 | 47515 | uint16 |  |  | bms_min_temp | [11 empty] | /components/pcs_info | pcs_bms_min_temp | Yes | Real value = (Modbus value / 100)
Min. Partial String |  | SV16.1.16 | Input Register |  | 1 |  |  |  |  | 7515 | 47516 | uint16 |  |  | bms_min_partial_strings | [11 empty] | /components/pcs_info | pcs_bms_min_partial_strings | Yes | Real value = Modbus value
Partial Diff Voltage |  | SV16.1.17 | Input Register |  | 1 |  |  |  |  | 7516 | 47517 | uint16 |  |  | bms_partial_voltage | [11 empty] | /components/pcs_info | pcs_bms_partial_voltage | Yes | Real value = Modbus value
Sys Config Status |  | SV16.1.18 | Input Register |  | 1 |  |  |  |  | 7517 | 47518 | uint16 |  |  | bms_config_status | [11 empty] | /components/pcs_info | pcs_bms_config_status | Yes | Real value = Modbus value
Protection #4 |  | SV16.1.19 | Input Register |  | 1 |  |  |  |  | 7518 | 47519 | uint16 |  |  | bms_protection_4 | [11 empty] | /components/pcs_info | pcs_bms_protection_4 | Yes | Real value = Modbus value
Protection #3 |  | SV16.1.20 | Input Register |  | 1 |  |  |  |  | 7519 | 47520 | uint16 |  |  | bms_protection_3 | [11 empty] | /components/pcs_info | pcs_bms_protection_3 | Yes | Real value = Modbus value
Protection #2 |  | SV16.1.21 | Input Register |  | 1 |  |  |  |  | 7520 | 47521 | uint16 |  |  | bms_protection_2 | [11 empty] | /components/pcs_info | pcs_bms_protection_2 | Yes | Real value = Modbus value
Protection #1 |  | SV16.1.22 | Input Register |  | 1 |  |  |  |  | 7521 | 47522 | uint16 |  |  | bms_protection_1 | [11 empty] | /components/pcs_info | pcs_bms_protection_1 | Yes | Real value = Modbus value
Alarm #4 |  | SV16.1.23 | Input Register |  | 1 |  |  |  |  | 7522 | 47523 | uint16 |  |  | bms_alarm_4 | [11 empty] | /components/pcs_info | pcs_bms_alarm_4 | Yes | Real value = Modbus value
Alarm #3 |  | SV16.1.24 | Input Register |  | 1 |  |  |  |  | 7523 | 47524 | uint16 |  |  | bms_alarm_3 | [11 empty] | /components/pcs_info | pcs_bms_alarm_3 | Yes | Real value = Modbus value
Alarm #2 |  | SV16.1.25 | Input Register |  | 1 |  |  |  |  | 7524 | 47525 | uint16 |  |  | bms_alarm_2 | [11 empty] | /components/pcs_info | pcs_bms_alarm_2 | Yes | Real value = Modbus value
Alarm #1 |  | SV16.1.26 | Input Register |  | 1 |  |  |  |  | 7525 | 47526 | uint16 |  |  | bms_alarm_1 | [11 empty] | /components/pcs_info | pcs_bms_alarm_1 | Yes | Real value = Modbus value
DCL |  | SV16.1.27 | Input Register |  | 1 | 10 |  |  | 0.1 | 7526 | 47527 | uint16 |  |  | bms_dcl | [11 empty] | /components/pcs_info | pcs_bms_dcl | Yes | Real value = (Modbus value / 10)
CCL |  | SV16.1.28 | Input Register |  | 1 | 10 |  |  | 0.1 | 7527 | 47528 | uint16 |  |  | bms_ccl | [11 empty] | /components/pcs_info | pcs_bms_ccl | Yes | Real value = (Modbus value / 10)
Watchdog response |  | SV16.1.29 | Input Register |  | 1 |  |  |  |  | 7528 | 47529 | uint16 |  |  | bms_watchdog_response | [11 empty] | /components/pcs_info | pcs_bms_watchdog_response | Yes | Real value = Modbus value
Digital Input Status |  | SV16.1.30 | Input Register |  | 1 |  |  |  |  | 7529 | 47530 | uint16 |  |  | bms_dio_status | [11 empty] | /components/pcs_info | pcs_bms_dio_status | Yes | Real value = Modbus value
System Alarm Status |  | SV16.1.31 | Input Register |  | 1 |  |  |  |  | 7530 | 47531 | uint16 |  |  | bms_alarm_status | [11 empty] | /components/pcs_info | pcs_bms_alarm_status | Yes | Real value = Modbus value
BMS Enclosure
Door Contact |  | SV17.1 | Input Register |  | 1 |  |  |  |  | 7650 | 47651 | uint16 |  |  | bmsenc_door_contact | [11 empty] | /components/pcs_info | pcs_bmsenc_door_contact | Yes | Real value = Modbus value
FCP Alarm |  | SV17.2 | Input Register |  | 1 |  |  |  |  | 7651 | 47652 | uint16 |  |  | bmsenc_fcp_alarm | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_alarm | Yes | Real value = Modbus value
FCP Predischarge |  | SV17.3 | Input Register |  | 1 |  |  |  |  | 7652 | 47653 | uint16 |  |  | bmsenc_fcp_predischarge | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_predischarge | Yes | Real value = Modbus value
FCP Agent Release |  | SV17.4 | Input Register |  | 1 |  |  |  |  | 7653 | 47654 | uint16 |  |  | bmsenc_fcp_release | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_release | Yes | Real value = Modbus value
FCP Trouble Sup |  | SV17.5 | Input Register |  | 1 |  |  |  |  | 7654 | 47655 | uint16 |  |  | bmsenc_fcp_sup | [11 empty] | /components/pcs_info | pcs_bmsenc_fcp_sup | Yes | Real value = Modbus value
DC 1 Disconnected |  | SV17.6 | Input Register |  | 1 |  |  |  |  | 7655 | 47656 | uint16 |  |  | bmsenc_dc_disconnected_1 | [11 empty] | /components/pcs_info | pcs_bmsenc_dc_disconnected_1 | Yes | Real value = Modbus value
DC 2 Disconnected |  | SV17.7 | Input Register |  | 1 |  |  |  |  | 7656 | 47657 | uint16 |  |  | bmsenc_dc_disconnected_2 | [11 empty] | /components/pcs_info | pcs_bmsenc_dc_disconnected_2 | Yes | Real value = Modbus value
Emergency Stop |  | SV17.8 | Input Register |  | 1 |  |  |  |  | 7657 | 47658 | uint16 |  |  | bmsenc_emergency_stop | [11 empty] | /components/pcs_info | pcs_bmsenc_emergency_stop | Yes | Real value = Modbus value
UPS Battery Failure |  | SV17.9 | Input Register |  | 1 |  |  |  |  | 7658 | 47659 | uint16 |  |  | bmsenc_ups_failure | [11 empty] | /components/pcs_info | pcs_bmsenc_ups_failure | Yes | Real value = Modbus value
UPS DC OK |  | SV17.10 | Input Register |  | 1 |  |  |  |  | 7659 | 47660 | uint16 |  |  | bmsenc_ups_ok | [11 empty] | /components/pcs_info | pcs_bmsenc_ups_ok | Yes | Real value = Modbus value
Temp Humidity T |  | SV17.11 | Input Register |  | 1 |  |  |  |  | 7660 | 47661 | uint16 |  |  | bmsenc_temp_humidity_t | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_humidity_t | Yes | Real value = Modbus value
Temp Humidity H |  | SV17.12 | Input Register |  | 1 |  |  |  |  | 7661 | 47662 | uint16 |  |  | bmsenc_temp_humidity_h | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_humidity_h | Yes | Real value = Modbus value
Temp 1 |  | SV17.13 | Input Register |  | 1 | 10 |  |  | 0.1 | 7662 | 47663 | uint16 |  |  | bmsenc_temp_1 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_1 | Yes | Real value = (Modbus value / 10)
Temp 2 |  | SV17.14 | Input Register |  | 1 | 10 |  |  | 0.1 | 7663 | 47664 | uint16 |  |  | bmsenc_temp_2 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_2 | Yes | Real value = (Modbus value / 10)
Temp 3 |  | SV17.15 | Input Register |  | 1 | 10 |  |  | 0.1 | 7664 | 47665 | uint16 |  |  | bmsenc_temp_3 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_3 | Yes | Real value = (Modbus value / 10)
Temp 4 |  | SV17.16 | Input Register |  | 1 | 10 |  |  | 0.1 | 7665 | 47666 | uint16 |  |  | bmsenc_temp_4 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_4 | Yes | Real value = (Modbus value / 10)
Temp 5 |  | SV17.17 | Input Register |  | 1 | 10 |  |  | 0.1 | 7666 | 47667 | uint16 |  |  | bmsenc_temp_5 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_5 | Yes | Real value = (Modbus value / 10)
Temp 6 |  | SV17.18 | Input Register |  | 1 | 10 |  |  | 0.1 | 7667 | 47668 | uint16 |  |  | bmsenc_temp_6 | [11 empty] | /components/pcs_info | pcs_bmsenc_temp_6 | Yes | Real value = (Modbus value / 10)
BMS Transformer
Transformer Alarms |  | SV18.1 | Input Register |  | 1 |  |  |  |  | 7680 | 47681 | uint16 |  |  | transformer_alarms | [11 empty] | /components/pcs_info | pcs_transformer_alarms | Yes | Real value = Modbus value
BMS HVAC
HVAC signals 1 |  | SV19.1 | Input Register |  | 1 |  |  |  |  | 7690 | 47691 | uint16 |  |  | hvac_signals_1 | [11 empty] | /components/pcs_info | pcs_hvac_signals_1 | Yes | Real value = Modbus value
HVAC signals 2 |  | SV19.2 | Input Register |  | 1 |  |  |  |  | 7691 | 47692 | uint16 |  |  | hvac_signals_2 | [11 empty] | /components/pcs_info | pcs_hvac_signals_2 | Yes | Real value = Modbus value
HVAC signals 3 |  | SV19.3 | Input Register |  | 1 |  |  |  |  | 7692 | 47693 | uint16 |  |  | hvac_signals_3 | [11 empty] | /components/pcs_info | pcs_hvac_signals_3 | Yes | Real value = Modbus value
HVAC signals 4 |  | SV19.4 | Input Register |  | 1 |  |  |  |  | 7693 | 47694 | uint16 |  |  | hvac_signals_4 | [11 empty] | /components/pcs_info | pcs_hvac_signals_4 | Yes | Real value = Modbus value
Note on A5: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A6: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A14: Tony Olivo: Do not add rows below this line, the script will break
Note on A15: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B15: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D15: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E15: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F15: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G15: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H15: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J15: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on L15: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on M15: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on N15: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on O15: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on P15: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on Z15: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AA15: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AB15: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AC15: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AD15: Tony Olivo: Yes/No whether to include in the client/server config
Note on AE15: Tony Olivo: For humans
Note on AF15: Tony Olivo: For humans
Note on AG15: Tony Olivo: Ranges are for humans only
Note on AK15: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with