## HybridOS Server
Device Name | FlexGen HybridOS
Device Protocol | DNP3
Device Protocol Version | 0.2 |  |  | Notes:
Device ID String | ##SITE_NAME##_dnp3_server
Device IP Address (if TCP) | 0.0.0.0
Device Port (502 typical) | 20000
local_uri | /local_server
frequency | 5000
Name | Source Device | Type | Version | Register Type | Address | Unit | Words | Scale | Variation | Data Type | Range Start | Range End | Engineering Range Start | Engineering Range End | Description | Control Narrative for Register | Reg ID | URI | ID | Include | Repeat | Bit
Site - Active Power Total Gross | HybridOS | Status | 0.2 | analog | 0 | kW |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Power produced as measured by BESS Inverter |  | ess_total_active_power | /assets/ess/summary | ess_total_active_power | Yes
Site - Reactive Power Total Gross | HybridOS | Status | 0.2 | analog | 1 | kVAR |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Reactive Power produced as measued by BESS Inverter |  | ess_total_reactive_power | /assets/ess/summary | ess_total_reactive_power | Yes
Site - Apparent Power Total Gross | HybridOS | Status | 0.2 | analog | 2 | kVA |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Apparent Power as measured by the BESS Inverter |  | ess_total_apparent_power | /assets/ess/summary | ess_total_apparent_power | Yes
Site - Active Power Total Net | SEL-735 | Status | 0.2 | analog | 3 | kW |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Aggregated Active Power exported after Aux loads |  | active_power | /components/sel_735 | active_power | Yes
Site - Reactive Power Total Net | SEL-735 | Status | 0.2 | analog | 4 | kVAR |  |  | Group30Var5 | uint32 | -32768 | 32767 |  |  | Aggregated Reactive Power exported after Aux loads |  | reactive_power | /components/sel_735 | reactive_power | Yes
Site - Apparent Power Total Net | SEL-735 | Status | 0.2 | analog | 5 | kVA |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Aggregated Apparent Power exported after Aux Loads |  | apparent_power | /components/sel_735 | apparent_power | Yes
Site - Frequency | SEL-735 | Status | 0.2 | analog | 6 | Hz |  |  | Group30Var5 | uint32 |  |  |  |  | Bus frequency |  | frequency | /components/sel_735 | frequency | Yes
Site - Voltage L1-L2 | SEL-651R | Status | 0.2 | analog | 7 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L1 |  | grid_voltage_l1 | /components/sel_651r | grid_voltage_l1 | Yes
Site - Voltage L2-L3 | SEL-651R | Status | 0.2 | analog | 8 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L2 |  | grid_voltage_l2 | /components/sel_651r | grid_voltage_l2 | Yes
Site - Voltage L3-L1 | SEL-651R | Status | 0.2 | analog | 9 | V |  |  | Group30Var5 | uint32 |  |  |  |  | Bus voltage L3 |  | grid_voltage_l3 | /components/sel_651r | grid_voltage_l3 | Yes
Battery - State of Charge % | HybridOS | Status | 0.2 | analog | 10 | % |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | State of charge expressed as % of MWh capacity based on current health |  | ess_average_soc | /assets/ess/summary | ess_average_soc | Yes
Battery - Chargable energy kWh | HybridOS | Status | 0.2 | analog | 11 | kWh |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | State of charge expressed as kWh of charge below 100 |  | ess_chargeable_energy | /metrics/ess | ess_chargeable_energy | Yes
Battery - Dischargeable energy kWh | HybridOS | Status | 0.2 | analog | 12 | kWh |  |  | Group30Var5 | uint32 |  |  |  |  | State of charge expressed as kWh of discharge above 0 |  | ess_dischargeable_energy | /metrics/ess | ess_dischargeable_energy | Yes
Battery - Chargeable power | HybridOS | Status | 0.2 | analog | 13 | kW |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | kW available to Charge |  | ess_chargeable_power | /assets/ess/summary | ess_chargeable_power | Yes
Battery - Dischargeable power | HybridOS | Status | 0.2 | analog | 14 | kW |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | kW available to discharge |  | ess_dischargeable_power | /assets/ess/summary | ess_dischargeable_power | Yes
Battery - Number ESS Available | HybridOS | Status | 0.2 | analog | 15 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | BESS Units that are currently able to be connected to grid |  | available_ess_num | /assets/ess/summary | available_ess_num | Yes
Battery - Number ESS Online | HybridOS | Status | 0.2 | analog | 16 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | BESS Units that are currently connected to grid |  | running_ess_num | /assets/ess/summary | running_ess_num | Yes
Heartbeat Counter | HybridOS | Status | 0.2 | analog | 20 | # |  |  | Group30Var5 | uint32 | 0 | 65535 |  |  | Incrementing counter to indicate functional communications from Server |  | heartbeat_counter | /features/site_operation | heartbeat_counter | Yes
BESS Container #1 System Mode | HybridOS | Status | 0.2 | analog | 30 |  |  |  | Group30Var5 | uint32 | 0 | 4294967295 | 0 | 10 | BESS Container #1 System mode of operation |  | status | /assets/ess/ess_01 | status | Yes
BESS Container #1 System SOC | HybridOS | Status | 0.2 | analog | 31 | % |  |  | Group30Var5 | uint32 | 0 | 65535 | 0 | 100 | BESS Container #1 State of Charge |  | soc | /assets/ess/ess_01 | soc | Yes
BESS Container #1 Number of Active Racks | HybridOS | Status | 0.2 | analog | 32 | # |  |  | Group30Var5 | uint32 | 0 | 65535 | 0 | 38 | BESS Container #1 Number of Active Racks |  | racks | /assets/ess/ess_01 | local_bms_status | Yes
BESS Container #2 System Mode | HybridOS | Status | 0.2 | analog | 35 |  |  |  | Group30Var5 | uint32 | 0 | -1227049253.5714 | 0 | 91.5429 | BESS Container #2 System mode of operation |  | status | /assets/ess/ess_02 | status | Yes
BESS Container #2 System SOC | HybridOS | Status | 0.2 | analog | 36 | % |  |  | Group30Var5 | uint32 | 0 | -4908393619.2857 | 0 | 123.7714 | BESS Container #2 State of Charge |  | soc | /assets/ess/ess_02 | soc | Yes
BESS Container #2 Number of Active Racks | HybridOS | Status | 0.2 | analog | 37 | # |  |  | Group30Var5 | uint32 | 0 | -6135508407.8572 | 0 | 134.5143 | BESS Container #2 Number of Active Racks |  | racks | /assets/ess/ess_02 | local_bms_status | Yes
BESS Container #3 System Mode | HybridOS | Status | 0.2 | analog | 40 |  |  |  | Group30Var5 | uint32 | 0 | -8589737985 | 0 | 156 | BESS Container #3 System mode of operation |  | status | /assets/ess/ess_03 | status | Yes
BESS Container #3 System SOC | HybridOS | Status | 0.2 | analog | 41 | % |  |  | Group30Var5 | uint32 | 0 | -12271082350.7143 | 0 | 188.2286 | BESS Container #3 State of Charge |  | soc | /assets/ess/ess_03 | soc | Yes
BESS Container #3 Number of Active Racks | HybridOS | Status | 0.2 | analog | 42 | # |  |  | Group30Var5 | uint32 | 0 | -13498197139.2858 | 0 | 198.9714 | BESS Container #3 Number of Active Racks |  | racks | /assets/ess/ess_03 | local_bms_status | Yes
BESS Container #4 System Mode | HybridOS | Status | 0.2 | analog | 45 |  |  |  | Group30Var5 | uint32 | 0 | -14725311927.8572 | 0 | 209.7143 | BESS Container #4 System mode of operation |  | status | /assets/ess/ess_04 | status | Yes
BESS Container #4 System SOC | HybridOS | Status | 0.2 | analog | 46 | % |  |  | Group30Var5 | uint32 | 0 | -18406656293.5716 | 0 | 241.9429 | BESS Container #4 State of Charge |  | soc | /assets/ess/ess_04 | soc | Yes
BESS Container #4 Number of Active Racks | HybridOS | Status | 0.2 | analog | 47 | # |  |  | Group30Var5 | uint32 | 0 | -19633771082.143 | 0 | 252.6857 | BESS Container #4 Number of Active Racks |  | racks | /assets/ess/ess_04 | local_bms_status | Yes
Site - kWh Delivered | ? |  |  | analog | 48 |  |  |  | Group30Var5 | [7 empty] | kwh_delivered | /components/sel_735 | kwh_delivered | Yes
Site - kWh Received |  |  |  | analog | 49 |  |  |  | Group30Var5 | [7 empty] | kwh_received | /components/sel_735 | kwh_received | Yes
Fleet Manager Metrics Timestamp Response |  |  |  | analog | 50 |  |  |  | Group30Var5 | [7 empty] | FM_timestamp | /metrics/timestamp | FM_timestamp | Yes
Yes
Watchdog Pet | HybridOS | Command | 0.2 | AnOPF32 | 0 |  |  |  |  | uint32 |  |  |  |  | Client will write this register with unique integer periodically |  | watchdog_pet | /features/site_operation | watchdog_pet | Yes
Baseload Power Cmd | HybridOS | Command | 0.2 | AnOPF32 | 1 | kW |  |  |  | uint32 |  |  |  |  | Baseload kW setpoint (always active) |  | fr_baseload_kW_cmd | /features/active_power | fr_baseload_kW_cmd | Yes
Inactive Baseload Power Cmd | HybridOS | Command | 0.2 | AnOPF32 | 2 | kW |  |  |  | uint32 |  |  |  |  | Inactive Baseload kW setpoint (only active when no frequency event triggered) |  | fr_inactive_kW_cmd | /features/active_power | fr_inactive_kW_cmd | Yes
Under Frequency Power Command | HybridOS | Command | 0.2 | AnOPF32 | 10 | kW |  |  |  | uint32 |  |  |  |  | power output target when UF event is trigged |  | fr_UF_active_kW_cmd | /features/active_power | fr_UF_active_kW_cmd | Yes
Under Frequency Slew Rate | HybridOS | Command | 0.2 | AnOPF32 | 11 | kW/s |  |  |  | uint32 |  |  |  |  | slew rate |  | fr_UF_slew_rate | /features/active_power | fr_UF_slew_rate | Yes
Under Frequency Trigger Percentage | HybridOS | Command | 0.2 | AnOPF32 | 12 | % |  |  |  | uint32 |  |  |  |  | trigger frequency setpoint (percent of nominal Hz) |  | fr_UF_hz_trigger_percent | /features/active_power | fr_UF_hz_trigger_percent | Yes
Under Frequency Recover Percentage | HybridOS | Command | 0.2 | AnOPF32 | 13 | % |  |  |  | uint32 |  |  |  |  | recovery frequency setpoint (percent of nominal Hz) |  | fr_UF_hz_recover_percent | /features/active_power | fr_UF_hz_recover_percent | Yes
Under Frequency Instant Recover Percentage | HybridOS | Command | 0.2 | AnOPF32 | 14 | % |  |  |  | uint32 |  |  |  |  | instant recovery frequency setpoint (percent of nominal Hz) |  | fr_UF_hz_instant_recover_percent | /features/active_power | fr_UF_hz_instant_recover_percent | Yes
Under Frequency Trigger Time | HybridOS | Command | 0.2 | AnOPF32 | 15 | s |  |  |  | uint32 |  |  |  |  | time for event to last after crossing trigger threshold |  | fr_UF_trigger_time | /features/active_power | fr_UF_trigger_time | Yes
Under Frequency Recover Time | HybridOS | Command | 0.2 | AnOPF32 | 16 | s |  |  |  | uint32 |  |  |  |  | time for event to last after crrossing recover threshold |  | fr_UF_recover_time | /features/active_power | fr_UF_recover_time | Yes
Under Frequency Cooldown Time | HybridOS | Command | 0.2 | AnOPF32 | 17 | s |  |  |  | uint32 |  |  |  |  | time for event to be disabled after ending |  | fr_UF_cooldown_time | /features/active_power | fr_UF_cooldown_time | Yes
Under Frequency Droop Percentage | HybridOS | Command | 0.2 | AnOPF32 | 18 | % |  |  |  | uint32 |  |  |  |  | 100 percent power output at this frequency setpoint (percent of nominal Hz) |  | fr_UF_droop_percent | /features/active_power | fr_UF_droop_percent | Yes
Over Frequency Power Command | HybridOS | Command | 0.2 | AnOPF32 | 20 | kW |  |  |  | uint32 |  |  |  |  | power output target when OF event is trigged |  | fr_OF_active_kW_cmd | /features/active_power | fr_OF_active_kW_cmd | Yes
Over Frequency Slew Rate | HybridOS | Command | 0.2 | AnOPF32 | 21 | kW/s |  |  |  | uint32 |  |  |  |  | slew rate |  | fr_OF_slew_rate | /features/active_power | fr_OF_slew_rate | Yes
Over Frequency Trigger Percentage | HybridOS | Command | 0.2 | AnOPF32 | 22 | % |  |  |  | uint32 |  |  |  |  | trigger frequency setpoint (percent of nominal Hz) |  | fr_OF_hz_trigger_percent | /features/active_power | fr_OF_hz_trigger_percent | Yes
Over Frequency Recover Percentage | HybridOS | Command | 0.2 | AnOPF32 | 23 | % |  |  |  | uint32 |  |  |  |  | recovery frequency setpoint (percent of nominal Hz) |  | fr_OF_hz_recover_percent | /features/active_power | fr_OF_hz_recover_percent | Yes
Over Frequency Instant Recover Percentage | HybridOS | Command | 0.2 | AnOPF32 | 24 | % |  |  |  | uint32 |  |  |  |  | instant recovery frequency setpoint (percent of nominal Hz) |  | fr_OF_hz_instant_recover_percent | /features/active_power | fr_OF_hz_instant_recover_percent | Yes
Over Frequency Trigger Time | HybridOS | Command | 0.2 | AnOPF32 | 25 | s |  |  |  | uint32 |  |  |  |  | time for event to last after crossing trigger threshold |  | fr_OF_trigger_time | /features/active_power | fr_OF_trigger_time | Yes
Over Frequency Recover Time | HybridOS | Command | 0.2 | AnOPF32 | 26 | s |  |  |  | uint32 |  |  |  |  | time for event to last after crrossing recover threshold |  | fr_OF_recover_time | /features/active_power | fr_OF_recover_time | Yes
Over Frequency Cooldown Time | HybridOS | Command | 0.2 | AnOPF32 | 27 | s |  |  |  | uint32 |  |  |  |  | time for event to be disabled after ending |  | fr_OF_cooldown_time | /features/active_power | fr_OF_cooldown_time | Yes
Over Frequency Droop Percentage | HybridOS | Command | 0.2 | AnOPF32 | 28 | % |  |  |  | uint32 |  |  |  |  | 100 percent power output at this frequency setpoint (percent of nominal Hz) |  | fr_OF_droop_percent | /features/active_power | fr_OF_droop_percent | Yes
Fleet Manager Metrics Timestamp | ? |  |  | AnOPF32 | 29 | [11 empty] | FM_timestamp | /metrics/timestamp |  | Yes
Main Breaker Closed | SEL-651 | Status | 0.2 | binary | 0 |  |  |  |  | uint32 | 0 | 65535 | 5 |  | Main Breaker Closed | Bit 5 = MAIN BREAKER OPEN STATUS ¦ 1 = breaker closed, 0 = breaker open | breaker_status | /components/sel_651r | breaker_status | Yes
Running Status | HybridOS | Status | 0.2 | binary | 1 |  |  |  |  | bool | 0 | 65535 |  |  | BESS Plant running status, feeder closed, at least one ESS or PV on | 0 = Not running, 1 = Running | running_status_flag | /site/operation | running_status_flag | Yes
Alarm Status | HybridOS | Status | 0.2 | binary | 2 |  |  |  |  | bool | 0 | 65535 |  |  | If any alarm is present, performance may be degraded and site requires attention | 0 = No alarms present, 1 = Alarms present | alarm_status_flag | /site/operation | alarm_status_flag | Yes
Fault Status | HybridOS | Status | 0.2 | binary | 3 |  |  |  |  | bool | 0 | 65535 |  |  | If any fault is present that prevents BESS plant from running on grid. | 0 = No faults present, 1 = Faults present | fault_status_flag | /site/operation | fault_status_flag | Yes
Under Frequency Status | HybridOS | Status | 0.2 | binary | 4 |  |  |  |  | bool |  |  |  |  | under frequency event status (true when triggered until event ends) |  | fr_UF_status_flag | /features/active_power | fr_UF_status_flag | Yes
Under Frequency Cooldown Status | HybridOS | Status | 0.2 | binary | 5 |  |  |  |  | bool |  |  |  |  | under frequency cooldown status (true when triggered until event ends) |  | fr_UF_cooldown_status | /features/active_power | fr_UF_cooldown_status | Yes
Over Frequency Status | HybridOS | Status | 0.2 | binary | 6 |  |  |  |  | bool |  |  |  |  | over frequency event status (true when triggered until event ends) |  | fr_OF_status_flag | /features/active_power | fr_OF_status_flag | Yes
Over Frequency Cooldown Status | HybridOS | Status | 0.2 | binary | 7 |  |  |  |  | bool |  |  |  |  | over frequency cooldown status (true when triggered until event ends) |  | fr_OF_cooldown_status | /features/active_power | fr_OF_cooldown_status | Yes
BESS Container #1 Fault Flag | HybridOS | Status | 0.2 | binary | 10 |  |  |  |  | bool |  |  |  |  | BESS Container #1 Fault Flag |  | faults | /assets/ess/ess_01 | faults | Yes
BESS Container #1 Alarm Flag | HybridOS | Status | 0.2 | binary | 11 |  |  |  |  | bool | 0 | 4294967295 | 0 | 100 | BESS Container #1 Alarm Flag |  | alarms | /assets/ess/ess_01 | alarms | Yes
BESS Container #2 Fault Flag | HybridOS | Status | 0.2 | binary | 15 |  |  |  |  | bool |  | -2454164042.1428 |  | 102.2857 | BESS Container #2 Fault Flag |  | faults | /assets/ess/ess_02 | faults | Yes
BESS Container #2 Alarm Flag | HybridOS | Status | 0.2 | binary | 16 |  |  |  |  | bool | 0 | -3681278830.7143 | 0 | 113.0286 | BESS Container #2 Alarm Flag |  | alarms | /assets/ess/ess_02 | alarms | Yes
BESS Container #3 Fault Flag | HybridOS | Status | 0.2 | binary | 20 |  |  |  |  | bool |  | -9816852773.5715 |  | 166.7429 | BESS Container #3 Fault Flag |  | faults | /assets/ess/ess_03 | faults | Yes
BESS Container #3 Alarm Flag | HybridOS | Status | 0.2 | binary | 21 |  |  |  |  | bool | 0 | -11043967562.1429 | 0 | 177.4857 | BESS Container #3 Alarm Flag |  | alarms | /assets/ess/ess_03 | alarms | Yes
BESS Container #4 Fault Flag | HybridOS | Status | 0.2 | binary | 25 |  |  |  |  | bool |  | -15952426716.4287 |  | 220.4571 | BESS Container #4 Fault Flag |  | faults | /assets/ess/ess_04 | faults | Yes
BESS Container #4 Alarm Flag | HybridOS | Status | 0.2 | binary | 26 |  |  |  |  | bool | 0 | -17179541505.0001 | 0 | 231.2 | BESS Container #4 Alarm Flag |  | alarms | /assets/ess/ess_04 | alarms | Yes
Start Site Command | HybridOS | Command | 0.2 | CROB | 0 |  |  |  |  | uint32 |  |  |  |  | start site when true |  | remote_enable_flag | /site/operation | remote_enable_flag | Yes
Disable Site Command | HybridOS | Command | 0.2 | CROB | 1 |  |  |  |  | uint32 |  |  |  |  | disable site when true (blocks start site command) |  | remote_disable_flag | /site/operation | remote_disable_flag | Yes
Clear Faults Command | HybridOS | Command | 0.2 | CROB | 2 |  |  |  |  | uint32 |  |  |  |  | clear faults when true |  | remote_clear_faults | /site/operation | remote_clear_faults | Yes
Under Frequency Enable Flag | HybridOS | Command | 0.2 | CROB | 10 |  |  |  |  | uint32 |  |  |  |  | enable command for underr frequency event |  | fr_UF_enable_flag | /features/active_power | fr_UF_enable_flag | Yes
Under Frequency Slew Bypass Flag | HybridOS | Command | 0.2 | CROB | 11 |  |  |  |  | uint32 |  |  |  |  | when true, asset slew rate (assets.json) will be bypassed |  | fr_UF_slew_override_flag | /features/active_power | fr_UF_slew_override_flag | Yes
Under Frequency Droop Bypass Flag | HybridOS | Command | 0.2 | CROB | 12 |  |  |  |  | uint32 |  |  |  |  | disable droop percentage response (for block responses such as FRRS) |  | fr_UF_droop_bypass_flag | /features/active_power | fr_UF_droop_bypass_flag | Yes
Under Frequency Droop Limit Flag | HybridOS | Command | 0.2 | CROB | 13 |  |  |  |  | uint32 |  |  |  |  | when true, limit power output to 100% when frequency exceeds droop percentage |  | fr_UF_droop_limit_flag | /features/active_power | fr_UF_droop_limit_flag | Yes
Over Frequency Enable Flag | HybridOS | Command | 0.2 | CROB | 14 |  |  |  |  | uint32 |  |  |  |  | enable command for over frequency event |  | fr_OF_enable_flag | /features/active_power | fr_OF_enable_flag | Yes
Over Frequency Slew Bypass Flag | HybridOS | Command | 0.2 | CROB | 15 |  |  |  |  | uint32 |  |  |  |  | when true, asset slew rate (assets.json) will be bypassed |  | fr_OF_slew_override_flag | /features/active_power | fr_OF_slew_override_flag | Yes
Over Frequency Droop Bypass Flag | HybridOS | Command | 0.2 | CROB | 16 |  |  |  |  | uint32 |  |  |  |  | disable droop percentage response (for block responses such as FRRS) |  | fr_OF_droop_bypass_flag | /features/active_power | fr_OF_droop_bypass_flag | Yes
Over Frequency Droop Limit Flag | HybridOS | Command | 0.2 | CROB | 17 |  |  |  |  | uint32 |  |  |  |  | when true, limit power output to 100% when frequency exceeds droop percentage |  | fr_OF_droop_limit_flag | /features/active_power | fr_OF_droop_limit_flag | Yes