## 9-2-2022
Connection Name | m_bess_aux_acuvim
device_id | 1
ip_address | 172.3.27.102
port | 10000
frequency | 500
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address Off by One | Address | Address Original2 | Data Type | Bit | Repeat | Reg ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
Low Speed | [16 empty] | m_bess_aux_acuvim | [5 empty] | 500 | 0 | [5 empty] | Yes
frequency |  |  | Holding Register |  | 2 |  |  |  |  | 16383 | 16384 |  | float32 |  |  | frequency | [13 empty] | Yes
voltage_l1 |  |  | Holding Register |  | 2 |  |  |  |  | 16385 | 16386 |  | float32 |  |  | voltage_l1 | [13 empty] | Yes
voltage_l2 |  |  | Holding Register |  | 2 |  |  |  |  | 16387 | 16388 |  | float32 |  |  | voltage_l2 | [13 empty] | Yes
voltage_l3 |  |  | Holding Register |  | 2 |  |  |  |  | 16389 | 16390 |  | float32 |  |  | voltage_l3 | [13 empty] | Yes
voltage_ln_rms |  |  | Holding Register |  | 2 |  |  |  |  | 16391 | 16392 |  | float32 |  |  | voltage_ln_rms | [13 empty] | Yes
voltage_l1_l2 |  |  | Holding Register |  | 2 |  |  |  |  | 16393 | 16394 |  | float32 |  |  | voltage_l1_l2 | [13 empty] | Yes
voltage_l2_l3 |  |  | Holding Register |  | 2 |  |  |  |  | 16395 | 16396 |  | float32 |  |  | voltage_l2_l3 | [13 empty] | Yes
voltage_l3_l1 |  |  | Holding Register |  | 2 |  |  |  |  | 16397 | 16398 |  | float32 |  |  | voltage_l3_l1 | [13 empty] | Yes
voltage_ll_rms |  |  | Holding Register |  | 2 |  |  |  |  | 16399 | 16400 |  | float32 |  |  | voltage_ll_rms | [13 empty] | Yes
current_l1 |  |  | Holding Register |  | 2 |  |  |  |  | 16401 | 16402 |  | float32 |  |  | current_l1 | [13 empty] | Yes
current_l2 |  |  | Holding Register |  | 2 |  |  |  |  | 16403 | 16404 |  | float32 |  |  | current_l2 | [13 empty] | Yes
current_l3 |  |  | Holding Register |  | 2 |  |  |  |  | 16405 | 16406 |  | float32 |  |  | current_l3 | [13 empty] | Yes
current_rms |  |  | Holding Register |  | 2 |  |  |  |  | 16407 | 16408 |  | float32 |  |  | current_rms | [13 empty] | Yes
current_n |  |  | Holding Register |  | 2 |  |  |  |  | 16409 | 16410 |  | float32 |  |  | current_n | [13 empty] | Yes
active_power_l1 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16411 | 16412 |  | float32 |  |  | active_power_l1 | [13 empty] | Yes
active_power_l2 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16413 | 16414 |  | float32 |  |  | active_power_l2 | [13 empty] | Yes
active_power_l3 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16415 | 16416 |  | float32 |  |  | active_power_l3 | [13 empty] | Yes
active_power |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16417 | 16418 |  | float32 |  |  | active_power | [13 empty] | Yes
reactive_power_l1 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16419 | 16420 |  | float32 |  |  | reactive_power_l1 | [13 empty] | Yes
reactive_power_l2 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16421 | 16422 |  | float32 |  |  | reactive_power_l2 | [13 empty] | Yes
reactive_power_l3 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16423 | 16424 |  | float32 |  |  | reactive_power_l3 | [13 empty] | Yes
reactive_power |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16425 | 16426 |  | float32 |  |  | reactive_power | [13 empty] | Yes
apparent_power_l1 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16427 | 16428 |  | float32 |  |  | apparent_power_l1 | [13 empty] | Yes
apparent_power_l2 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16429 | 16430 |  | float32 |  |  | apparent_power_l2 | [13 empty] | Yes
apparent_power_l3 |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16431 | 16432 |  | float32 |  |  | apparent_power_l3 | [13 empty] | Yes
apparent_power |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16433 | 16434 |  | float32 |  |  | apparent_power | [13 empty] | Yes
power_factor_l1 |  |  | Holding Register |  | 2 |  |  |  |  | 16435 | 16436 |  | float32 |  |  | power_factor_l1 | [13 empty] | Yes
power_factor_l2 |  |  | Holding Register |  | 2 |  |  |  |  | 16437 | 16438 |  | float32 |  |  | power_factor_l2 | [13 empty] | Yes
power_factor_l3 |  |  | Holding Register |  | 2 |  |  |  |  | 16439 | 16440 |  | float32 |  |  | power_factor_l3 | [13 empty] | Yes
power_factor |  |  | Holding Register |  | 2 |  |  |  |  | 16441 | 16442 |  | float32 |  |  | power_factor | [13 empty] | Yes
active_power_demand |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16449 | 16450 |  | float32 |  |  | active_power_demand | [13 empty] | Yes
reactive_power_demand |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16451 | 16452 |  | float32 |  |  | reactive_power_demand | [13 empty] | Yes
apparent_power_demand |  |  | Holding Register |  | 2 | 1000 |  |  |  | 16453 | 16454 |  | float32 |  |  | apparent_power_demand | [13 empty] | Yes
kwh_received |  |  | Holding Register |  | 2 | 10 |  |  |  | 16455 | 16456 |  |  |  |  | kwh_received | [13 empty] | Yes
kwh_delivered |  |  | Holding Register |  | 2 | 10 |  |  |  | 16457 | 16458 |  |  |  |  | kwh_delivered | [13 empty] | Yes
kvarh_received |  |  | Holding Register |  | 2 | 10 |  |  |  | 16459 | 16460 |  |  |  |  | kvarh_received | [13 empty] | Yes
kvarh_delivered |  |  | Holding Register |  | 2 | 10 |  |  |  | 16461 | 16462 |  |  |  |  | kvarh_delivered | [13 empty] | Yes
Note on A2: Tony Olivo: These are not automatically parsed yet, but included here for human convenience
Note on A6: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B6: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D6: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E6: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F6: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G6: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H6: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J6: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on M6: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on N6: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on O6: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on P6: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on Q6: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on AA6: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AB6: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AC6: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AD6: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AE6: Tony Olivo: Yes/No whether to include in the client/server config
Note on AF6: Tony Olivo: For humans
Note on AG6: Tony Olivo: For humans
Note on AH6: Tony Olivo: Ranges are for humans only