## 9-2-2022
Connection Name | APC SMT Smart-UPS
ip_address | 172.3.27.102
port | 10001
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address Off by One | Address | Address Original2 | Data Type | Bit | Repeat | Reg ID | Echo ID | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
[18 empty] | apc_ups | [5 empty] | 100 | 0 | 1
UPS Status |  |  | Holding Register |  | 2 |  |  |  |  | -1 | 0 |  | bitfield |  |  | status | /components/twins_apc_ups/s1 | [13 empty] | Yes
StatusChange-Modifier |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 0 | [16 empty] | Yes
State = Online |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 1 | [16 empty] | Yes
State = On Battery |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 2 | [16 empty] | Yes
State = Bypass |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 3 | [16 empty] | Yes
State = Output Off |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 4 | [16 empty] | Yes
Fault / Alarm |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 5 | [16 empty] | Yes
Input Bad |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 6 | [16 empty] | Yes
Test |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 7 | [16 empty] | Yes
Pending Output On |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 8 | [16 empty] | Yes
Pending Output Off |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 9 | [16 empty] | Yes
Commanded |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 10 | [16 empty] | Yes
Reserved Address:0 Bit:11 |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 11 | [16 empty] | Yes
Reserved Address:0 Bit:12 |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 12 | [16 empty] | Yes
High Efficency |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 13 | [16 empty] | Yes
Informational Alert |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 14 | [16 empty] | Yes
Fault |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 15 | [16 empty] | Yes
Reserved Address:0 Bit:16 |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 16 | [16 empty] | Yes
Reserved Address:0 Bit:17 |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 17 | [16 empty] | Yes
Reserved Address:0 Bit:18 |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 18 | [16 empty] | Yes
Mains Bad State |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 19 | [16 empty] | Yes
Fault Recovery State |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 20 | [16 empty] | Yes
Overload State |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 21 | [16 empty] | Yes
Maintenance Mode |  |  | Holding Register | [6 empty] | -1 | 0 |  | bit | 22 | [16 empty] | Yes
UPS Status Change Cause |  |  | Holding Register | [6 empty] | 1 | 2 |  | enum |  |  | status_change_cause | /components/twins_apc_ups/sc | [13 empty] | Yes
System Initialization |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 0 | [16 empty] | Yes
High Input Voltage |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 1 | [16 empty] | Yes
Low Input Voltage |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 2 | [16 empty] | Yes
Distorted Input |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 3 | [16 empty] | Yes
Rapid Change Of Input Voltage |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 4 | [16 empty] | Yes
High Input Frequency |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 5 | [16 empty] | Yes
Low Input Frequency |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 6 | [16 empty] | Yes
Freq And Or Phase Difference |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 7 | [16 empty] | Yes
Acceptable Input |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 8 | [16 empty] | Yes
Automatic Test |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 9 | [16 empty] | Yes
Test Ended |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 10 | [16 empty] | Yes
Local UI Command |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 11 | [16 empty] | Yes
Protocol Command |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 12 | [16 empty] | Yes
Low Battery Voltage |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 13 | [16 empty] | Yes
General Error |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 14 | [16 empty] | Yes
Power System Error |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 15 | [16 empty] | Yes
Battery System Error |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 16 | [16 empty] | Yes
Error Cleared |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 17 | [16 empty] | Yes
Automatic Restart |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 18 | [16 empty] | Yes
Distorted Inverter Output |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 19 | [16 empty] | Yes
Inverter Output Acceptable |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 20 | [16 empty] | Yes
EPO Interface |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 21 | [16 empty] | Yes
Input Phase Delta Out Of Range |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 22 | [16 empty] | Yes
Input Neutral Not Connected |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 23 | [16 empty] | Yes
ATS Transfer |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 24 | [16 empty] | Yes
Configuration Change |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 25 | [16 empty] | Yes
Alert Asserted |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 26 | [16 empty] | Yes
Alert Cleared |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 27 | [16 empty] | Yes
Plug Rating Exceeded |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 28 | [16 empty] | Yes
Outlet Group State Change |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 29 | [16 empty] | Yes
Failure Bypass Expired |  |  | Holding Register | [6 empty] | 1 | 2 |  | bit | 30 | [16 empty] | Yes
MOG outlet status |  |  | Holding Register |  | 2 |  |  |  |  | 2 | 3 |  | bitfield |  |  | main_outlet_group_status | /components/twins_apc_ups/sm | [13 empty] | Yes
State = On |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 0 | [16 empty] | Yes
State = Off |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 1 | [16 empty] | Yes
Process Reboot |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 2 | [16 empty] | Yes
Process Shutdow |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 3 | [16 empty] | Yes
Process Sleep |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 4 | [16 empty] | Yes
Reserved Address:3 Bit:5 |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 5 | [16 empty] | Yes
Reserved Address:3 Bit:6 |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 6 | [16 empty] | Yes
Pending Load Shed |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 7 | [16 empty] | Yes
Pending On Delay |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 8 | [16 empty] | Yes
Pending Off Delay |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 9 | [16 empty] | Yes
Pending On AC Presence |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 10 | [16 empty] | Yes
Pending On Min Runtime |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 11 | [16 empty] | Yes
Member Group Process 1 |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 12 | [16 empty] | Yes
Member Group Process 2 |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 13 | [16 empty] | Yes
Low Runtime |  |  | Holding Register | [6 empty] | 2 | 3 |  | bit | 14 | [16 empty] | Yes
Secondary Outle group outlet status |  |  | Holding Register |  | 2 |  |  |  |  | 5 | 6 |  | bitfield |  |  | secondary_group_status | /components/twins_apc_ups/s2 | [13 empty] | Yes
State = On |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 0 | [16 empty] | Yes
State = Off |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 1 | [16 empty] | Yes
Process Reboot |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 2 | [16 empty] | Yes
Process Shutdow |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 3 | [16 empty] | Yes
Process Sleep |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 4 | [16 empty] | Yes
Reserved Address:6 Bit:5 |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 5 | [16 empty] | Yes
Reserved Address:6 Bit:6 |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 6 | [16 empty] | Yes
Pending Load Shed |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 7 | [16 empty] | Yes
Pending On Delay |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 8 | [16 empty] | Yes
Pending Off Delay |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 9 | [16 empty] | Yes
Pending On AC Presence |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 10 | [16 empty] | Yes
Pending On Min Runtime |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 11 | [16 empty] | Yes
Member Group Process 1 |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 12 | [16 empty] | Yes
Member Group Process 2 |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 13 | [16 empty] | Yes
Low Runtime |  |  | Holding Register | [6 empty] | 5 | 6 |  | bit | 14 | [16 empty] | Yes
Pole status |  |  | Holding Register | [6 empty] | 17 | 18 |  | bitfield |  |  | simple_status | /components/twins_apc_ups/ss | [13 empty] | Yes
Power Failure |  |  | Holding Register | [6 empty] | 17 | 18 |  | bit | 0 | [16 empty] | Yes
Shutdown Imminent |  |  | Holding Register | [6 empty] | 17 | 18 |  | bit | 1 | [16 empty] | Yes
General Error |  |  | Holding Register | [6 empty] | 18 | 19 |  | bitfield |  |  | error | /components/twins_apc_ups/e | [13 empty] | Yes
Site Wiring |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 0 | [16 empty] | Yes
EEPROM |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 1 | [16 empty] | Yes
AD Converter |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 2 | [16 empty] | Yes
Logic Power Supply |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 3 | [16 empty] | Yes
Internal Communication |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 4 | [16 empty] | Yes
UI Button |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 5 | [16 empty] | Yes
Needs Factory Setup |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 6 | [16 empty] | Yes
EPO Active |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 7 | [16 empty] | Yes
Firmware Mismatch |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 8 | [16 empty] | Yes
Oscillator |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 9 | [16 empty] | Yes
Measurement Mismatch |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 10 | [16 empty] | Yes
Subsystem |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 11 | [16 empty] | Yes
Logic Power Supply Relay |  |  | Holding Register | [6 empty] | 18 | 19 |  | bit | 12 | [16 empty] | Yes
Power System Error |  |  | Holding Register |  | 2 |  |  |  |  | 19 | 20 |  | bitfield |  |  | ps_error | /components/twins_apc_ups/es | [13 empty] | Yes
Output Overload |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 0 | [16 empty] | Yes
Output Short Circuit |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 1 | [16 empty] | Yes
Output Overvoltage |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 2 | [16 empty] | Yes
Transformer DC Imalance |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 3 | [16 empty] | Yes
Over Temperature |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 4 | [16 empty] | Yes
Backfeed Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 5 | [16 empty] | Yes
AVR Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 6 | [16 empty] | Yes
PFC Input Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 7 | [16 empty] | Yes
Output Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 8 | [16 empty] | Yes
Bypass Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 9 | [16 empty] | Yes
Fan |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 10 | [16 empty] | Yes
PFC |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 11 | [16 empty] | Yes
DC Bus Overvoltage |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 12 | [16 empty] | Yes
Inverter |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 13 | [16 empty] | Yes
Over Current |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 14 | [16 empty] | Yes
Bypass PFC Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 15 | [16 empty] | Yes
Bus Soft Start |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 16 | [16 empty] | Yes
Green Relay |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 17 | [16 empty] | Yes
DC Output |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 18 | [16 empty] | Yes
DC Bus Converter |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 19 | [16 empty] | Yes
Sensor |  |  | Holding Register | [6 empty] | 19 | 20 |  | bit | 20 | [16 empty] | Yes
Battery System Error |  |  | Holding Register | [6 empty] | 21 | 22 |  | bitfield |  |  | batt_error | /components/twins_apc_ups/eb | [13 empty] | Yes
Disconnected |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 0 | [16 empty] | Yes
Overvoltage |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 1 | [16 empty] | Yes
Needs Replacement |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 2 | [16 empty] | Yes
Over Temperature Critical |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 3 | [16 empty] | Yes
Charger |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 4 | [16 empty] | Yes
Temperature Sensor |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 5 | [16 empty] | Yes
Bus Soft Start |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 6 | [16 empty] | Yes
Over Temperature Warning |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 7 | [16 empty] | Yes
General Error |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 8 | [16 empty] | Yes
Communication |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 9 | [16 empty] | Yes
Disconnected Frame |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 10 | [16 empty] | Yes
Firmware Mismatch |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 11 | [16 empty] | Yes
Voltage Sense Error |  |  | Holding Register | [6 empty] | 21 | 22 |  | bit | 12 | [16 empty] | Yes
Replace Battery Test Status |  |  | Holding Register | [6 empty] | 22 | 23 |  | bitfield |  |  | batt_test_status | /components/twins_apc_ups/sb1 | [13 empty] | Yes
Pending |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 0 | [16 empty] | Yes
In Progress |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 1 | [16 empty] | Yes
Passed |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 2 | [16 empty] | Yes
Failed |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 3 | [16 empty] | Yes
Refused |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 4 | [16 empty] | Yes
Aborted |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 5 | [16 empty] | Yes
Aborted from Protocol Source |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 6 | [16 empty] | Yes
Aborted from Local UI |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 7 | [16 empty] | Yes
Aborted from Internal |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 8 | [16 empty] | Yes
Invalid State |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 9 | [16 empty] | Yes
Internal Fault |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 10 | [16 empty] | Yes
State of Charge not acceptable |  |  | Holding Register | [6 empty] | 22 | 23 |  | bit | 11 | [16 empty] | Yes
Run Time Calibration Status |  |  | Holding Register | [6 empty] | 23 | 24 |  | bitfield |  |  | run_time_cal_status | /components/twins_apc_ups/srt | [13 empty] | Yes
Pending |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 0 | [16 empty] | Yes
In Progress |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 1 | [16 empty] | Yes
Passed |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 2 | [16 empty] | Yes
Failed |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 3 | [16 empty] | Yes
Refused |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 4 | [16 empty] | Yes
Aborted |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 5 | [16 empty] | Yes
Aborted from Protocol Source |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 6 | [16 empty] | Yes
Aborted from Local UI |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 7 | [16 empty] | Yes
Aborted from Internal |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 8 | [16 empty] | Yes
Invalid State |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 9 | [16 empty] | Yes
Internal Fault |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 10 | [16 empty] | Yes
State of Charge not acceptable |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 11 | [16 empty] | Yes
Load Change |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 12 | [16 empty] | Yes
AC Input Not Acceptable |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 13 | [16 empty] | Yes
Load Too Low |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 14 | [16 empty] | Yes
Over Charge In Progress |  |  | Holding Register | [6 empty] | 23 | 24 |  | bit | 15 | [16 empty] | Yes
Battery Life Time Status |  |  | Holding Register | [6 empty] | 24 | 25 |  | bitfield |  |  | batt_lifetime_status | /components/twins_apc_ups/sb2 | [13 empty] | Yes
Life Time Status OK |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 0 | [16 empty] | Yes
Life Time Near End |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 1 | [16 empty] | Yes
Life Time Exceeded |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 2 | [16 empty] | Yes
Life Time Near End Acknowledged |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 3 | [16 empty] | Yes
Life Time Exceeded Acknowledged |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 4 | [16 empty] | Yes
Measured Life Time Near End |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 5 | [16 empty] | Yes
Measured Life Time Near End Acknowledged |  |  | Holding Register | [6 empty] | 24 | 25 |  | bit | 6 | [16 empty] | Yes
User Interface Status |  |  | Holding Register | [6 empty] | 25 | 26 |  | bitfield |  |  | ui_status | /components/twins_apc_ups/sui | [13 empty] | Yes
Continious Test In Progress |  |  | Holding Register | [6 empty] | 25 | 26 |  | bit | 0 | [16 empty] | Yes
Audible Alarm In Progress |  |  | Holding Register | [6 empty] | 25 | 26 |  | bit | 1 | [16 empty] | Yes
Audible Alarm Muted |  |  | Holding Register | [6 empty] | 25 | 26 |  | bit | 2 | [16 empty] | Yes
Any Button Pressed Recently |  |  | Holding Register | [6 empty] | 25 | 26 |  | bit | 3 | [16 empty] | Yes
Run Time Remaining |  |  | Holding Register |  | 2 |  |  |  |  | 127 | 128 |  | uint16 |  |  | run_time | /components/twins_apc_ups/rt | [13 empty] | Yes
State of Charge |  |  | Holding Register |  |  | 512 |  |  |  | 129 | 130 |  | uint16 |  |  | soc | /components/twins_apc_ups/soc | [13 empty] | Yes
Positive Voltage DC |  |  | Holding Register |  |  | 32 |  |  |  | 130 | 131 |  | int16 |  |  | voltage_dc_pos | /components/twins_apc_ups/vdcp | [13 empty] | Yes
Negative Voltage DC |  |  | Holding Register |  |  | 32 |  |  |  | 131 | 132 |  | int16 |  |  | voltage_dc_neg | /components/twins_apc_ups/vdcn | [13 empty] | Yes
Battery Replacement Date |  |  | Holding Register | [6 empty] | 132 | 133 |  | uint16 |  |  | batt_date | /components/twins_apc_ups/bd | [13 empty] | Yes
Battery Temperature |  |  | Holding Register |  |  | 128 |  |  |  | 134 | 135 |  | int16 |  |  | battery_temperature | /components/twins_apc_ups/bt | [13 empty] | Yes
Active Power |  |  | Holding Register |  |  | 189600 |  |  |  | 135 | 136 |  | uint16 |  |  | active_power | /components/twins_apc_ups/a1 | [13 empty] | Yes
Active Power Phase 2 |  |  | Holding Register |  |  | 189600 |  |  |  | 136 | 137 |  | uint16 |  |  | active_power_2 | /components/twins_apc_ups/a2 | [13 empty] | Yes
Apparent Power |  |  | Holding Register |  |  | 177700 |  |  |  | 137 | 138 |  | uint16 |  |  | apparent_power | /components/twins_apc_ups/ap | [13 empty] | Yes
Apparent Power Phase 2 |  |  | Holding Register |  |  | 177700 |  |  |  | 138 | 139 |  | uint16 |  |  | apparent_power_2 | /components/twins_apc_ups/ap2 | [13 empty] | Yes
Output Current |  |  | Holding Register |  |  | 32 |  |  |  | 139 | 140 |  | uint16 |  |  | output_current | /components/twins_apc_ups/oc | [13 empty] | Yes
Current Phase 2 |  |  | Holding Register |  |  | 32 |  |  |  | 140 | 141 |  | uint16 |  |  | output_current_2 | /components/twins_apc_ups/oc2 | [13 empty] | Yes
Output Voltage |  |  | Holding Register |  |  | 64 |  |  |  | 141 | 142 |  | uint16 |  |  | output_voltage_ac | /components/twins_apc_ups/ov | [13 empty] | Yes
Voltage Phase 2 |  |  | Holding Register |  |  | 64 |  |  |  | 142 | 143 |  | uint16 |  |  | output_voltage_ac_2 | /components/twins_apc_ups/ov2 | [13 empty] | Yes
Output frequency |  |  | Holding Register |  |  | 128 |  |  |  | 143 | 144 |  | uint16 |  |  | output_frequency | /components/twins_apc_ups/of | [13 empty] | Yes
Output energy |  |  | Holding Register |  | 2 |  |  |  |  | 144 | 145 |  | uint16 |  |  | output_engery | /components/twins_apc_ups/oe | [13 empty] | Yes
Input Status |  |  | Holding Register | [6 empty] | 149 | 150 |  | bitfield |  |  | input_status | /components/twins_apc_ups/si | [13 empty] | Yes
Acceptable Input |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 0 | [16 empty] | Yes
Pending Acceptance |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 1 | [16 empty] | Yes
Voltage Too Low |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 2 | [16 empty] | Yes
Voltage Too High |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 3 | [16 empty] | Yes
Distorted |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 4 | [16 empty] | Yes
Boost |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 5 | [16 empty] | Yes
Trim |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 6 | [16 empty] | Yes
Frequency Too Low |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 7 | [16 empty] | Yes
Frequency Too High |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 8 | [16 empty] | Yes
Freq And Phase Not Locked |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 9 | [16 empty] | Yes
Phase Delta Out of Range |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 10 | [16 empty] | Yes
Neutral Not Connected |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 11 | [16 empty] | Yes
Reserved Address:150 Bit:12 |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 12 | [16 empty] | Yes
Reserved Address:150 Bit:13 |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 13 | [16 empty] | Yes
Reserved Address:150 Bit:14 |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 14 | [16 empty] | Yes
Powering Load |  |  | Holding Register | [6 empty] | 149 | 150 |  | bit | 15 | [16 empty] | Yes
Input Voltage AC |  |  | Holding Register |  |  | 64 |  |  |  | 150 | 151 |  | uint16 |  |  | input_voltage_ac | /components/twins_apc_ups/iv | [13 empty] | Yes
Note on A6: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B6: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D6: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E6: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F6: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G6: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H6: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J6: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on M6: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on N6: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on O6: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on P6: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on Q6: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on AB6: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AC6: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AD6: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AE6: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AF6: Tony Olivo: Yes/No whether to include in the client/server config
Note on AG6: Tony Olivo: For humans
Note on AH6: Tony Olivo: For humans
Note on AI6: Tony Olivo: Ranges are for humans only