## 9-2-2022
Connection Name | SEL 3530 RTAC
ip_address | 172.3.27.102
port | 10005
device_id | 1
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address Off by One | Address | Address Original2 | Data Type | Bit | Repeat | Reg ID | echo id | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
[18 empty] | sel_3530_rtac | [5 empty] | 8 | 0 | [5 empty] | Yes
Frequency 3 Cycle |  |  | Holding Register |  | 2 | 1000 |  |  |  | -1 | 0 |  | uint16 |  |  | frequency_3 | /components/twins_sel_3530_rtac/f1 | [13 empty] | Yes
Note on A5: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B5: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D5: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E5: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F5: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G5: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H5: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J5: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on M5: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on N5: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on O5: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on P5: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on Q5: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on AB5: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AC5: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AD5: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AE5: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AF5: Tony Olivo: Yes/No whether to include in the client/server config
Note on AG5: Tony Olivo: For humans
Note on AH5: Tony Olivo: For humans
Note on AI5: Tony Olivo: Ranges are for humans only