## 9-2-2022
Connection Name | SEL 651R Relay
ip_address | 172.3.27.102
port | 10003
off_by_one | TRUE
Name | Type | Ref | Register Type | Unit | Words | Scale | FIMS Scale | hexAddress | Bus Scale | Address Off by One | Address | Address Original2 | Data Type | Bit | Repeat | Reg ID | echo_id | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | web_ui Display Type | web_ui Options | URI | ID | Include | Description | Control Narrative for Register | Range Start | Range End | Engineering Range Start | Engineering Range End
[18 empty] | sel_651r | [5 empty] | 1000 | 0
Breaker Control |  |  | Holding Register | [6 empty] | 0 | 1 |  | uint16 |  |  | breaker_control | [14 empty] | Yes
Battery Voltage |  |  | Holding Register |  |  | 10 |  |  |  | 1 | 2 |  | int16 |  |  | battery_voltage | [14 empty] | Yes
Battery Temperature |  |  | Holding Register |  |  | 10 |  |  |  | 2 | 3 |  | int16 |  |  | battery_temperature | [14 empty] | Yes
Frequency |  |  | Holding Register |  |  | 100 |  |  |  | 3 | 4 |  |  |  |  | frequency | [14 empty] | Yes
Power Factor direction |  |  | Holding Register | [6 empty] | 4 | 5 |  |  |  |  | ldpf3 | [14 empty] | Yes
Power Factor |  |  | Holding Register |  |  | 100 |  |  |  | 5 | 6 |  | int16 |  |  | pf | [14 empty] | Yes
Current L1 |  |  | Holding Register | [6 empty] | 6 | 7 |  |  |  |  | current_l1 | [14 empty] | Yes
Current L2 |  |  | Holding Register | [6 empty] | 7 | 8 |  |  |  |  | current_l2 | [14 empty] | Yes
Current L3 |  |  | Holding Register | [6 empty] | 8 | 9 |  |  |  |  | current_l3 | [14 empty] | Yes
Current Neutral |  |  | Holding Register | [6 empty] | 9 | 10 |  |  |  |  | current_n | [14 empty] | Yes
Voltage L1 |  |  | Holding Register |  | 2 |  |  |  |  | 10 | 11 |  |  |  |  | voltage_l1 | [14 empty] | Yes
Voltage L2 |  |  | Holding Register |  | 2 |  |  |  |  | 12 | 13 |  |  |  |  | voltage_l2 | [14 empty] | Yes
Voltage L3 |  |  | Holding Register |  | 2 |  |  |  |  | 14 | 15 |  |  |  |  | voltage_l3 | [14 empty] | Yes
Grid Voltage L1 |  |  | Holding Register |  | 2 |  |  |  |  | 16 | 17 |  |  |  |  | grid_voltage_l1 | [14 empty] | Yes
Grid Voltage L2 |  |  | Holding Register |  | 2 |  |  |  |  | 18 | 19 |  |  |  |  | grid_voltage_l2 | [14 empty] | Yes
Grid Voltage L3 |  |  | Holding Register |  | 2 |  |  |  |  | 20 | 21 |  |  |  |  | grid_voltage_l3 | [14 empty] | Yes
Active Power |  |  | Holding Register |  | 2 |  |  |  |  | 22 | 23 |  | int16 |  |  | active_power | [14 empty] | Yes
Apparent Power |  |  | Holding Register |  | 2 |  |  |  |  | 24 | 25 |  | int16 |  |  | apparent_power | [14 empty] | Yes
Reactive Power |  |  | Holding Register |  | 2 |  |  |  |  | 26 | 27 |  | int16 |  |  | reactive_power | [14 empty] | Yes
Instantaneous Over Current |  |  | Holding Register | [6 empty] | 28 | 29 |  | individual_bits |  |  | instantaneous_overcurrent_status | [14 empty] | Yes
inst_overcurrent |  |  | Holding Register | [6 empty] | 28 | 29 |  | bit | 4 | [16 empty] | Yes
inst_overcurrent_l3 |  |  | Holding Register | [6 empty] | 28 | 29 |  | bit | 5 | [16 empty] | Yes
inst_overcurrent_l2 |  |  | Holding Register | [6 empty] | 28 | 29 |  | bit | 6 | [16 empty] | Yes
inst_overcurrent_l1 |  |  | Holding Register | [6 empty] | 28 | 29 |  | bit | 7 | [16 empty] | Yes
Time Over Current |  |  | Holding Register | [6 empty] | 29 | 30 |  | individual_bits |  |  | time_overcurrent_status | [14 empty] | Yes
time_overcurrent_l2 |  |  | Holding Register | [6 empty] | 29 | 30 |  | bit | 1 | [16 empty] | Yes
time_overcurrent_l1 |  |  | Holding Register | [6 empty] | 29 | 30 |  | bit | 13 | [16 empty] | Yes
Time Over Current 2 |  |  | Holding Register | [6 empty] | 30 | 31 |  | individual_bits |  |  | time_overcurrent_status_2 | [14 empty] | Yes
time_overcurrent |  |  | Holding Register | [6 empty] | 30 | 31 |  | bit | 0 | [16 empty] | Yes
time_overcurrent_l3 |  |  | Holding Register | [6 empty] | 30 | 31 |  | bit | 5 | [16 empty] | Yes
Ground Fault Over Current |  |  | Holding Register | [6 empty] | 31 | 32 |  | individual_bits |  |  | ground_fault_status | [14 empty] | Yes
ground_fault_overcurrent |  |  | Holding Register | [6 empty] | 31 | 32 |  | bit | 4 | [16 empty] | Yes
Definite Time Over Current |  |  | Holding Register | [6 empty] | 32 | 33 |  | individual_bits |  |  | definite_time_overcurrent | [14 empty] | Yes
definite_time_overcurrent |  |  | Holding Register | [6 empty] | 32 | 33 |  | bit | 4 | [16 empty] | Yes
definite_overcurrent_l3 |  |  | Holding Register | [6 empty] | 32 | 33 |  | bit | 5 | [16 empty] | Yes
definite_overcurrent_l2 |  |  | Holding Register | [6 empty] | 32 | 33 |  | bit | 6 | [16 empty] | Yes
definite_overcurrent_l1 |  |  | Holding Register | [6 empty] | 32 | 33 |  | bit | 7 | [16 empty] | Yes
Pole status |  |  | Holding Register | [6 empty] | 33 | 34 |  | individual_bits |  |  | pole_status | [14 empty] | Yes
single_pole_open |  |  | Holding Register | [6 empty] | 33 | 34 |  | bit | 0 | [16 empty] | Yes
breaker_status |  |  | Holding Register | [6 empty] | 33 | 34 |  | bit | 4 | [16 empty] | Yes
status_l3 |  |  | Holding Register | [6 empty] | 33 | 34 |  | bit | 5 | [16 empty] | Yes
status_l2 |  |  | Holding Register | [6 empty] | 33 | 34 |  | bit | 6 | [16 empty] | Yes
status_l1 |  |  | Holding Register | [6 empty] | 33 | 34 |  | bit | 7 | [16 empty] | Yes
Electrical Fault |  |  | Holding Register | [6 empty] | 34 | 35 |  | individual_bits |  |  | electrical_fault | [14 empty] | Yes
electrical_fault |  |  | Holding Register | [6 empty] | 34 | 35 |  | bit | 3 | [16 empty] | Yes
Over Voltage 1 |  |  | Holding Register | [6 empty] | 35 | 36 |  | individual_bits |  |  | overvoltage_relay_1 | [14 empty] | Yes
overvolt_l2 |  |  | Holding Register | [6 empty] | 35 | 36 |  | bit | 0 | [16 empty] | Yes
overvolt_l1 |  |  | Holding Register | [6 empty] | 35 | 36 |  | bit | 1 | [16 empty] | Yes
Over Voltage 2 |  |  | Holding Register | [6 empty] | 36 | 37 |  | individual_bits |  |  | overvoltage_relay_2 | [14 empty] | Yes
overvolt_l3 |  |  | Holding Register | [6 empty] | 36 | 37 |  | bit | 7 | [16 empty] | Yes
Over Voltage 3 |  |  | Holding Register | [6 empty] | 37 | 38 |  | individual_bits |  |  | overvoltage_relay_3 | [14 empty] | Yes
overvolt |  |  | Holding Register | [6 empty] | 37 | 38 |  | bit | 7 | [16 empty] | Yes
Grid Overvoltage |  |  | Holding Register | [6 empty] | 38 | 39 |  | individual_bits |  |  | overvoltage_relay_grid | [14 empty] | Yes
overvolt_grid_l2 |  |  | Holding Register | [6 empty] | 38 | 39 |  | bit | 0 | [16 empty] | Yes
overvolt_grid_l1 |  |  | Holding Register | [6 empty] | 38 | 39 |  | bit | 1 | [16 empty] | Yes
undervolt_grid_l3 |  |  | Holding Register | [6 empty] | 38 | 39 |  | bit | 5 | [16 empty] | Yes
undervolt_grid_l2 |  |  | Holding Register | [6 empty] | 38 | 39 |  | bit | 6 | [16 empty] | Yes
undervolt_grid_l1 |  |  | Holding Register | [6 empty] | 38 | 39 |  | bit | 7 | [16 empty] | Yes
Grid Overvoltage 2 |  |  | Holding Register | [6 empty] | 39 | 40 |  | individual_bits |  |  | overvoltage_relay_grid_2 | [14 empty] | Yes
overvolt_grid_l3 |  |  | Holding Register | [6 empty] | 39 | 40 |  | bit | 7 | [16 empty] | Yes
Grid Overvoltage 3 |  |  | Holding Register | [6 empty] | 40 | 41 |  | individual_bits |  |  | overvoltage_relay_grid_3 | [14 empty] | Yes
grid_overvolt |  |  | Holding Register | [6 empty] | 40 | 41 |  | bit | 0 | [16 empty] | Yes
grid_undervolt |  |  | Holding Register | [6 empty] | 40 | 41 |  | bit | 1 | [16 empty] | Yes
Aux Contacts |  |  | Holding Register | [6 empty] | 41 | 42 |  | individual_bits |  |  | aux_contacts | [14 empty] | Yes
aux_contact_l1 |  |  | Holding Register | [6 empty] | 41 | 42 |  | bit | 0 | [16 empty] | Yes
aux_contact_l2 |  |  | Holding Register | [6 empty] | 41 | 42 |  | bit | 1 | [16 empty] | Yes
aux_contact_l3 |  |  | Holding Register | [6 empty] | 41 | 42 |  | bit | 2 | [16 empty] | Yes
lockout_handle |  |  | Holding Register | [6 empty] | 41 | 42 |  | bit | 3 | [16 empty] | Yes
Remote commands |  |  | Holding Register | [6 empty] | 42 | 43 |  | individual_bits |  |  | remote_commands | [14 empty] | Yes
remote_open_cmd |  |  | Holding Register | [6 empty] | 42 | 43 |  | bit | 0 | [16 empty] | Yes
remote_close_cmd |  |  | Holding Register | [6 empty] | 42 | 43 |  | bit | 4 | [16 empty] | Yes
Trip Issued Status |  |  | Holding Register | [6 empty] | 43 | 44 |  | individual_bits |  |  | trip_status | [14 empty] | Yes
trip_status |  |  | Holding Register | [6 empty] | 43 | 44 |  | bit | 0 | [16 empty] | Yes
Voltage Swell |  |  | Holding Register | [6 empty] | 44 | 45 |  | individual_bits |  |  | voltage_swell | [14 empty] | Yes
volt_swell |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 0 | [16 empty] | Yes
volt_swell_l3 |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 1 | [16 empty] | Yes
volt_swell_l2 |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 2 | [16 empty] | Yes
volt_swell_l1 |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 3 | [16 empty] | Yes
volt_sag |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 4 | [16 empty] | Yes
volt_sag_l3 |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 5 | [16 empty] | Yes
volt_sag_l2 |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 6 | [16 empty] | Yes
volt_sag_l1 |  |  | Holding Register | [6 empty] | 44 | 45 |  | bit | 7 | [16 empty] | Yes
Voltage Interuption |  |  | Holding Register | [6 empty] | 45 | 46 |  | individual_bits |  |  | voltage_interruption | [14 empty] | Yes
test_relay |  |  | Holding Register | [6 empty] | 45 | 46 |  | bit | 0 | [16 empty] | Yes
volt_int |  |  | Holding Register | [6 empty] | 45 | 46 |  | bit | 4 | [16 empty] | Yes
volt_int_l3 |  |  | Holding Register | [6 empty] | 45 | 46 |  | bit | 5 | [16 empty] | Yes
volt_int_l2 |  |  | Holding Register | [6 empty] | 45 | 46 |  | bit | 6 | [16 empty] | Yes
volt_int_l1 |  |  | Holding Register | [6 empty] | 45 | 46 |  | bit | 7 | [16 empty] | Yes
Open Push Button Pushed |  |  | Holding Register | [6 empty] | 46 | 47 |  | individual_bits |  |  | open_push | [14 empty] | Yes
open_button_pushed |  |  | Holding Register | [6 empty] | 46 | 47 |  | bit | 5 | [16 empty] | Yes
Voltage ABZ |  |  | Holding Register |  | 2 |  |  |  |  | 47 | 48 |  | uint16 |  |  | grid_voltage_l1_l2 | [14 empty] | Yes
Voltage BCZ |  |  | Holding Register |  | 2 |  |  |  |  | 49 | 50 |  | uint16 |  |  | grid_voltage_l2_l3 | [14 empty] | Yes
Voltage CAZ |  |  | Holding Register |  | 2 |  |  |  |  | 51 | 52 |  | uint16 |  |  | grid_voltage_l3_l1 | [14 empty] | Yes
Relay Row 32 |  |  | Holding Register | [6 empty] | 53 | 54 |  | individual_bits |  |  | frequency_timeout | [14 empty] | Yes
overfreq_time_1 |  |  | Holding Register | [6 empty] | 53 | 54 |  | bit | 7 | [16 empty] | Yes
overfreq_time_2 |  |  | Holding Register | [6 empty] | 53 | 54 |  | bit | 8 | [16 empty] | Yes
underfreq_time_1 |  |  | Holding Register | [6 empty] | 53 | 54 |  | bit | 9 | [16 empty] | Yes
underfreq_time_2 |  |  | Holding Register | [6 empty] | 53 | 54 |  | bit | 10 | [16 empty] | Yes
Relay Row 48 |  |  | Holding Register | [6 empty] | 54 | 55 |  | individual_bits |  |  | voltage_timeout_1 | [14 empty] | Yes
undervolt_time_1 |  |  | Holding Register | [6 empty] | 54 | 55 |  | bit | 1 | [16 empty] | Yes
undervolt_time_2 |  |  | Holding Register | [6 empty] | 54 | 55 |  | bit | 2 | [16 empty] | Yes
Relay Row 49 |  |  | Holding Register | [6 empty] | 55 | 56 |  | individual_bits |  |  | voltage_timeout_2 | [14 empty] | Yes
undervolt_time_3 |  |  | Holding Register | [6 empty] | 55 | 56 |  | bit | 3 | [16 empty] | Yes
overvolt_time_1 |  |  | Holding Register | [6 empty] | 55 | 56 |  | bit | 4 | [16 empty] | Yes
overvolt_time_2 |  |  | Holding Register | [6 empty] | 55 | 56 |  | bit | 5 | [16 empty] | Yes
overvolt_time_3 |  |  | Holding Register | [6 empty] | 55 | 56 |  | bit | 6 | [16 empty] | Yes
Relay Row 88 |  |  | Holding Register | [6 empty] | 56 | 57 |  | individual_bits |  |  | power_limit_element | [14 empty] | Yes
pos_power_limit |  |  | Holding Register | [6 empty] | 56 | 57 |  | bit | 4 | [16 empty] | Yes
neg_power_limit |  |  | Holding Register | [6 empty] | 56 | 57 |  | bit | 5 | [16 empty] | Yes
Note on A6: Tony Olivo: Modbus client/server do not use this field, but it is included in the output json for humans and easier cross referencing. For "bits": ussed as "bit_string" For "repeats": used as a template string to match
Note on B6: Tony Olivo: Not used by the script, but for humans to be really explicit about if something is status or control. Maybe useful later
Note on D6: Tony Olivo: Valid inputs: Input Register Holding Register Discrete Input Coil
Note on E6: Tony Olivo: It is best to put in the manufacturer specified unit here, another column uses it to work out internal FIMS scaling
Note on F6: Tony Olivo: Number of words to read for register. May be omitted if 1 For "repeat": Number of registers to copy, starting from the address in the Repeat column
Note on G6: Tony Olivo: Input manufacturer specified scale here, used in calculation with FIMS scale
Note on H6: Tony Olivo: Coerce same scales into FIMS ranges, such as W having a scale of 1000 to get to kW, used internally
Note on J6: Tony Olivo: Client: divide by this number to get to the specified unit from the raw binary value Server:
Note on M6: Tony Olivo: 0 refenced address. You generally do not expect to see 30000 or 40000 range here. If the manufacturer specified addresses are in those ranges, paste them in another column and manipulate them into this column with LEFT() and FIND() if needed For bits within a bitfield, specify the address of the bitfield the bit is associated with
Note on N6: Tony Olivo: Valid inputs: uint uint16 uint32 int int16 int32 float float16 float32 float64 bool bitfield (indicates the address and id of the bitfield) bit (indicates a bit within bitfield) repeat (looks at a few different fields to repeat ranges)
Note on O6: Tony Olivo: 0 referenced bit position within a bitfield. Bits may be skipped and will automatically be filled with "Reserved".
Note on P6: Tony Olivo: Indicates the starting address of the range to be repeated. The "Words" column indicates how many words to repeat
Note on Q6: Tony Olivo: For modbus client. Will name the id published under /components/device_id
Note on AB6: Desmond Mullen: if not a number or boolean. Valid inputs: enum enum_button enum_slider Must include Options in the next column
Note on AC6: Desmond Mullen: enter as return_value/name pairs separated by commas, e.g. `0 = On Grid, 1 = Off Grid` Must include Display Type in the previous column
Note on AD6: Tony Olivo: For modbus server, the URI from which to read/set the field of ID
Note on AE6: Tony Olivo: For modbus server, ID of register to read from "URI" column
Note on AF6: Tony Olivo: Yes/No whether to include in the client/server config
Note on AG6: Tony Olivo: For humans
Note on AH6: Tony Olivo: For humans
Note on AI6: Tony Olivo: Ranges are for humans only