## sheet1
Connection Name | Sungrow Local Controller |  |  |  | YOU MUST HAND TRIM THE JSON AFTER RUNNING THIS THROUGH Excel-to-JSON SCRIPT
ip_address | 172.3.27.202
port | 10005
Device ID | 1
Name | Reg ID | Register Type | Include | Address | Repeat | Bit | Words | Data Type | Unit | Scale | Range Start | Range End | Bus Range Start | Bus Range End | Component ID | Heartbeat Enabled | Component Heartbeat Read URI | Component Heartbeat Write URI | Add | Modbus Heartbeat Timeout ms | Component Heartbeat Timeout ms | Frequency | Offset Time | Device ID | Description
first component |  |  | Yes | [11 empty] | sungrow_ess_01_hs | TRUE | toggle_bit | toggle_bit |  | 1000 | 1000 | 50 | 0 | 1
System time: Year | system_time_year | Holding Register | No | 10050 |  |  | 1 | uint16 | Y | [15 empty] | -
System time: Month | system_time_month | Holding Register | No | 10051 |  |  | 1 | uint16 | M | [15 empty] | -
System time: Day | system_time_day | Holding Register | No | 10052 |  |  | 1 | uint16 | D | [15 empty] | -
System time: Hour | system_time_hour | Holding Register | No | 10053 |  |  | 1 | uint16 | H | [15 empty] | -
System time: Minute | system_time_minute | Holding Register | No | 10054 |  |  | 1 | uint16 | M | [15 empty] | -
System time: Second | system_time_second | Holding Register | No | 10055 |  |  | 1 | uint16 | S | [15 empty] | -
Start/Stop | start_stop | Holding Register | Yes | 10056 |  |  | 1 | uint16 | [16 empty] | 1:Start 2:Stop
BMS Close/Open/Reset | bms_close_open_reset | Holding Register | Yes | 10057 |  |  | 1 | uint16 | [16 empty] | 1:Open 2:Close 3:Reset
Selection of active/Passive mode | selection_of_active_passive_mode | Holding Register | No | 10059 |  |  | 1 | uint16 | [16 empty] | 0:Active mode 1:Passive mode Active mode attempts to restart if fault condition clears, passive stays shut down
Selection of reactive power mode | reactive_power_mode | Holding Register | Yes | 10060 |  |  | 1 | uint16 | [16 empty] | 0x55:Off 0xA1:Power factor Mode 0xA2:reactive power mode 0xA4:Volt-var mode
PCS standby cmd | standby_mode | Holding Register | Yes | 10061 |  |  | 1 | uint16 | [16 empty] | 0xAA:PCS standby 0x55:PCS exit standby
Remote/Local | remote_local | Holding Register | Yes | 10062 |  |  | 1 | uint16 | [16 empty] | 0:Remote&local 1:Remote 2:local
Voltage control mode | voltage_control_mode | Holding Register | No | 10063 |  |  | 1 | uint16 | [16 empty] | 0xAA:Enable 0x55:Disable
SOC control mode | soc_control_mode | Holding Register | No | 10064 |  |  | 1 | uint16 | [16 empty] | 0xAA:Enable 0x55:Disable
HVAC temperature set 1 | hvac_low_temp_setpoint | Holding Register | Yes | 10065 |  |  | 1 | int16 | °C | 10 | [14 empty] | -
HVAC temperature set 2 | hvac_high_temp_setpoint | Holding Register | Yes | 10066 |  |  | 1 | int16 | °C | 10 | [14 empty] | -
HVAC On/Off | hvac_on_off | Holding Register | Yes | 10067 |  |  | 1 | uint16 | [16 empty] | 0:Off 1:On
HVAC setting temperature | hvac_setting_temp | Holding Register | Yes | 10068 |  |  | 1 | uint16 | °C | 10
Output1 Ctrl cmd | output1_ctrl_cmd | Holding Register | No | 10070 |  |  | 1 | uint16 | [16 empty] | 0x55: Switch Off 0xAA: Switch On
Output2 Ctrl cmd | output2_ctrl_cmd | Holding Register | No | 10071 |  |  | 1 | uint16 | [16 empty] | -
Output3 Ctrl cmd | output3_ctrl_cmd | Holding Register | No | 10072 |  |  | 1 | uint16 | [16 empty] | -
Output4 Ctrl cmd | output4_ctrl_cmd | Holding Register | No | 10073 |  |  | 1 | uint16 | [16 empty] | -
UPS Reboot | ups_reboot | Holding Register | No | 10074 |  |  | 1 | uint16 | [16 empty] | 0xAA: UPS Reboot
Off grid voltage slope | off_grid_voltage_slope | Holding Register | Yes | 10075 |  |  | 1 | uint16 | % | 10 | [14 empty] | Per second
Power factor | power_factor_setpoint | Holding Register | Yes | 10103 |  |  | 1 | int16 |  | 1000 | [14 empty] | 1.Only response when the corresponding mode is enable 2.Negative represents lagging,and positive represents leading
Reactive power | reactive_power_setpoint | Holding Register | Yes | 10104 |  |  | 1 | int16 |  | -1 | [14 empty] | -
Toggle bit | toggle_bit | Holding Register | Yes | 10113 |  |  | 1 | uint16 | [16 empty] | Client should set different value in Toggle time, otherwise a fault accurs.
Toggle time | toggle_time | Holding Register | Yes | 10114 |  |  | 1 | uint16 | [16 empty] | 0: Disable function Other values: Enable function, the toggle bit value should change in this time
Grid/Off grid | set_grid_mode | Holding Register | Yes | 10125 |  |  | 1 | uint16 | [16 empty] | 0:Grid mode 1:Off grid mode
Active power | active_power_setpoint | Holding Register | Yes | 10127 |  |  | 1 | int16 | kW | [15 empty] | Negative represents charging, and otherwise represents discharing
Primary Frequency control enabled | prime_freq_cnt_enable | Holding Register | Yes | 10128 |  |  | 1 | uint16
Upper limit DC voltage level 2 | upper_limit_dc_voltage_level_2 | Holding Register | No | 10301 |  |  | 1 | uint16 | V | 10 | [14 empty] | Mutually exclusive with SOC limits
Upper limit DC voltage level 1 | upper_limit_dc_voltage_level_1 | Holding Register | No | 10302 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Upper limit DC voltage level 2 recovery | upper_limit_dc_voltage_level_2_recovery | Holding Register | No | 10303 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Upper limit DC voltage level 1 recovery | upper_limit_dc_voltage_level_1_recovery | Holding Register | No | 10304 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Lower limit DC voltage level 1 | lower_limit_dc_voltage_level_1 | Holding Register | No | 10305 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Lower limit DC voltage level 2 | lower_limit_dc_voltage_level_2 | Holding Register | No | 10306 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Lower limit DC voltage level 1 recovery | lower_limit_dc_voltage_level_1_recovery | Holding Register | No | 10307 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Lower limit DC voltage level 2 recovery | lower_limit_dc_voltage_level_2_recovery | Holding Register | No | 10308 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Voltage level trigger time | voltage_level_trigger_time | Holding Register | No | 10310 |  |  | 1 | uint16 | s | [15 empty] | -
Voltage level exit time | voltage_level_exit_time | Holding Register | No | 10311 |  |  | 1 | uint16 | s | [15 empty] | -
SOC level trigger time | soc_level_trigger_time | Holding Register | No | 10322 |  |  | 1 | uint16 | s | [15 empty] | -
SOC level exit time | soc_level_exit_time | Holding Register | No | 10323 |  |  | 1 | uint16 | s | [15 empty] | -
PCS On-grid mode control enable | on_grid_ctrl_enable | Holding Register | No | 10400 |  |  | 1 | uint16
PCS On-grid mode setting | on_grid_mode | Holding Register | No | 10401 |  |  | 1 | uint16 | [16 empty] | 0x00:CC mode, 0x01:CV mode, 0x02:CP(DC) mode, 0x03:CP(AC) mode
On-grid constant current mode current limit value | cc_cur_limit | Holding Register | No | 10402 |  |  | 1 | int16 | A
On-grid constant voltage mode charge uplimit voltage | cv_charge_volt_limit | Holding Register | No | 10403 |  |  | 1 | uint16 | V
On-grid constant voltage mode discharge lowlimit voltage | cv_discharge_volt_limit | Holding Register | No | 10404 |  |  | 1 | uint16 | V
On-grid constant voltage mode current limit value | cv_cur_limit | Holding Register | No | 10405 |  |  | 1 | int16 | A
On-grid constant DC power mode power value | const_power_dc_setpoint | Holding Register | No | 10406 |  |  | 1 | int16 | kW
On-grid constant AC power mode power value | const_power_ac_setpoint | Holding Register | No | 10407 |  |  | 1 | int16 | kW
Offgrid_Active_Passtive_mode | off_grid_active_pasive_mode | Holding Register | No | 10408 |  |  | 1 | uint16
Chargecurrent_limit | charge_cur_limit | Holding Register | No | 10409 |  |  | 1 | int16 | A
Dischargecurrent_limit | discharge_cur_limit | Holding Register | No | 10410 |  |  | 1 | uint16 | A
Protocol no. | protocol_no | Input Register | No | 10000 |  |  | 2 | uint32
Protocol ver. | protocol_ver | Input Register | No | 10002 |  |  | 2 | uint32
Software version | software_version | Input Register | No | 10004 |  |  | 18 | uint32 | [16 empty] | Unknown encoding
Device model | device_model | Input Register | No | 10022 |  |  | 8 | uint16 | [16 empty] | UTF-8 encoded
Device ver. | device_ver | Input Register | No | 10030 |  |  | 10 | uint16 | [16 empty] | UTF-8 encoded
SN | sn | Input Register | No | 10040 |  |  | 10 | uint16 | [16 empty] | UTF-8 encoded
Device type code | device_type_code | Input Register | No | 10050 |  |  | 1 | uint16 | [16 empty] | -
Rated system power | rated_system_power | Input Register | No | 10051 |  |  | 2 | uint32 | kW | [15 empty] | -
AC bus voltage | voltage_ac | Input Register | Yes | 10053 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
AC bus frequency | frequency | Input Register | Yes | 10054 |  |  | 1 | uint16 | Hz | 100 | [14 empty] | -
System chargeable power | chargeable_power | Input Register | Yes | 10055 |  |  | 2 | uint32 | kW | [15 empty] | -
System dischargeable power | dischargeable_power | Input Register | Yes | 10057 |  |  | 2 | uint32 | kW | [15 empty] | -
System chargeable energy | chargeable_energy | Input Register | Yes | 10059 |  |  | 2 | uint32 | kWh | [15 empty] | -
System dischargeable energy | dischargeable_energy | Input Register | Yes | 10061 |  |  | 2 | uint32 | kWh | [15 empty] | -
System running time | system_running_time | Input Register | No | 10063 |  |  | 2 | uint32 | h | [15 empty] | -
Charging Discharging State | charge_discharge_state | Input Register | No | 10065 |  |  | 1 | bitfield
Charging |  | Input Register | No | 10065 |  | 0 |  | bit
Discharging |  | Input Register | No | 10065 |  | 1 |  | bit
Non-operating mode |  | Input Register | No | 10065 |  | 2 |  | bit
Rated Reactive Power | rated_reactive_power | Input Register | No | 10066 |  |  | 2 | uint32 | kVar
modbus heartbeat | heartbeat | Input Register | Yes | 10070 |  |  | 1 | uint16 | [16 empty] | Increment 1 per second, recount when reaching 1000
Grid/Off-grid mode | grid_mode | Input Register | Yes | 10071 |  |  | 1 | uint16 | [16 empty] | 0:Grid mode 1:Off-grid mode
Grid status | grid_status | Input Register | Yes | 10072 |  |  | 1 | uint16 | [16 empty] | 0:Grid abnormal 1:Grid normal
System status | system_state | Input Register | Yes | 10073 |  |  | 2 | bitfield | [16 empty] | -
Self-checking |  | Input Register | Yes | 10073 |  | 0 |  | bit
Microgrid power supply starting |  | Input Register | Yes | 10073 |  | 1 |  | bit
Grid power supply starting |  | Input Register | Yes | 10073 |  | 2 |  | bit
Microgrid power supply running |  | Input Register | Yes | 10073 |  | 3 |  | bit
Grid power supply running |  | Input Register | Yes | 10073 |  | 4 |  | bit
Fault |  | Input Register | Yes | 10073 |  | 5 |  | bit
Stopping |  | Input Register | Yes | 10073 |  | 6 |  | bit
Stop |  | Input Register | Yes | 10073 |  | 7 |  | bit
Emergency Stop |  | Input Register | Yes | 10073 |  | 8 |  | bit
Fault state | faults | Input Register | Yes | 10075 |  |  | 4 | bitfield | [16 empty] | -
PCS Fault |  | Input Register | Yes | 10075 |  | 0 |  | bit
PCS Communication Fault |  | Input Register | Yes | 10075 |  | 1 |  | bit
PCS Address Conflict |  | Input Register | Yes | 10075 |  | 2 |  | bit
Self Check Fail |  | Input Register | Yes | 10075 |  | 15 |  | bit
Self Check Timeout |  | Input Register | Yes | 10075 |  | 16 |  | bit
Micro Grid Start Timeout |  | Input Register | Yes | 10075 |  | 17 |  | bit
Micro Grid Start Fail |  | Input Register | Yes | 10075 |  | 18 |  | bit
Grid Start Timeout |  | Input Register | Yes | 10075 |  | 19 |  | bit
Grid Start Fail |  | Input Register | Yes | 10075 |  | 20 |  | bit
Stop Timeout |  | Input Register | Yes | 10075 |  | 23 |  | bit
Host PCS setting abnormal |  | Input Register | Yes | 10075 |  | 28 |  | bit
PC Comm Fault |  | Input Register | Yes | 10075 |  | 29 |  | bit
PCS not ready fault |  | Input Register | Yes | 10075 |  | 30 |  | bit
Node 1 Fault |  | Input Register | Yes | 10075 |  | 32 |  | bit
Node 2 Fault |  | Input Register | Yes | 10075 |  | 33 |  | bit
Node 3 Fault |  | Input Register | Yes | 10075 |  | 34 |  | bit
Node 4 Fault |  | Input Register | Yes | 10075 |  | 35 |  | bit
Node 5 Fault |  | Input Register | Yes | 10075 |  | 36 |  | bit
Node 6 Fault |  | Input Register | Yes | 10075 |  | 37 |  | bit
Node 7 Fault |  | Input Register | Yes | 10075 |  | 38 |  | bit
Node 8 Fault |  | Input Register | Yes | 10075 |  | 39 |  | bit
Node 9 Fault |  | Input Register | Yes | 10075 |  | 40 |  | bit
Node 10 Fault |  | Input Register | Yes | 10075 |  | 41 |  | bit
Node 11 Fault |  | Input Register | Yes | 10075 |  | 42 |  | bit
Node 12 Fault |  | Input Register | Yes | 10075 |  | 43 |  | bit
Node 13 Fault |  | Input Register | Yes | 10075 |  | 44 |  | bit
Node 14 Fault |  | Input Register | Yes | 10075 |  | 45 |  | bit
Node 15 Fault |  | Input Register | Yes | 10075 |  | 46 |  | bit
Node 16 Fault |  | Input Register | Yes | 10075 |  | 47 |  | bit
Control Box Node Fault |  | Input Register | Yes | 10075 |  | 48 |  | bit
Alarm State | alarms | Input Register | Yes | 10079 |  |  | 4 | bitfield | [16 empty] | -
PCS Fault / Alarm / Emergency Stop |  | Input Register | Yes | 10079 |  | 0 |  | bit
PCS Communication Fault Alarm |  | Input Register | Yes | 10079 |  | 1 |  | bit
PCS Grid-side Contact Alarm |  | Input Register | Yes | 10079 |  | 6 |  | bit
One or More Low Battery Level 1 |  | Input Register | Yes | 10079 |  | 7 |  | bit
One or More High Battery Level 1 |  | Input Register | Yes | 10079 |  | 8 |  | bit
BMS/BCP Communication Fault Alarm |  | Input Register | Yes | 10079 |  | 9 |  | bit
BMS Fault Alarm |  | Input Register | Yes | 10079 |  | 10 |  | bit
BMS Alarm |  | Input Register | Yes | 10079 |  | 11 |  | bit
Ammeter Communication Fault Alarm |  | Input Register | Yes | 10079 |  | 15 |  | bit
Node Collector Communication Fault Alarm |  | Input Register | Yes | 10079 |  | 19 |  | bit
Node 1 Alarm |  | Input Register | Yes | 10079 |  | 20 |  | bit
Node 2 Alarm |  | Input Register | Yes | 10079 |  | 21 |  | bit
Node 3 Alarm |  | Input Register | Yes | 10079 |  | 22 |  | bit
Node 4 Alarm |  | Input Register | Yes | 10079 |  | 23 |  | bit
Node 5 Alarm |  | Input Register | Yes | 10079 |  | 24 |  | bit
Node 6 Alarm |  | Input Register | Yes | 10079 |  | 25 |  | bit
Node 7 Alarm |  | Input Register | Yes | 10079 |  | 26 |  | bit
Node 8 Alarm |  | Input Register | Yes | 10079 |  | 27 |  | bit
One or More Low Battery Level 2 |  | Input Register | Yes | 10079 |  | 28 |  | bit
One or More High Battery Level 2 |  | Input Register | Yes | 10079 |  | 29 |  | bit
BCP Fault / Alarm / Emergency Stop |  | Input Register | Yes | 10079 |  | 30 |  | bit
Node Collector Node Abnormal |  | Input Register | Yes | 10079 |  | 31 |  | bit
Battery Disconnected |  | Input Register | Yes | 10079 |  | 32 |  | bit
PCS not ready |  | Input Register | Yes | 10079 |  | 33 |  | bit
Battery DC voltage difference abnormal in group |  | Input Register | Yes | 10079 |  | 34 |  | bit
HVAC Temp Abnormal |  | Input Register | Yes | 10079 |  | 35 |  | bit
Host PCS setting abnormal |  | Input Register | Yes | 10079 |  | 36 |  | bit
Low online rack num |  | Input Register | Yes | 10079 |  | 37 |  | bit
Battery system stop alarm |  | Input Register | Yes | 10079 |  | 38 |  | bit
HVAC comm fault alarm |  | Input Register | Yes | 10079 |  | 39 |  | bit
HVAC fault alarm |  | Input Register | Yes | 10079 |  | 40 |  | bit
TTC comm fault alarm |  | Input Register | Yes | 10079 |  | 41 |  | bit
BSC comm fault alarm |  | Input Register | Yes | 10079 |  | 42 |  | bit
BSC fault/alarm |  | Input Register | Yes | 10079 |  | 43 |  | bit
UPS comm fault alarm |  | Input Register | Yes | 10079 |  | 44 |  | bit
TEMP & HUM comm fault alarm |  | Input Register | Yes | 10079 |  | 45 |  | bit
Measurement and control fault alarm |  | Input Register | Yes | 10079 |  | 46 |  | bit
Control Box Node Alarm |  | Input Register | Yes | 10079 |  | 47 |  | bit
Node 9 Alarm |  | Input Register | Yes | 10079 |  | 56 |  | bit
Node 10 Alarm |  | Input Register | Yes | 10079 |  | 57 |  | bit
Node 11 Alarm |  | Input Register | Yes | 10079 |  | 58 |  | bit
Node 12 Alarm |  | Input Register | Yes | 10079 |  | 59 |  | bit
Node 13 Alarm |  | Input Register | Yes | 10079 |  | 60 |  | bit
Node 14 Alarm |  | Input Register | Yes | 10079 |  | 61 |  | bit
Node 15 Alarm |  | Input Register | Yes | 10079 |  | 62 |  | bit
Node 16 Alarm |  | Input Register | Yes | 10079 |  | 63 |  | bit
Input node status | input_node_status | Input Register | No | 10083 |  |  | 1 | uint16 | [16 empty] | See Note 2
System nameplate power | system_nameplate_power | Input Register | No | 10084 |  |  | 1 | uint16 | kW | [15 empty] | -
System nameplate capacity | system_nameplate_capacity | Input Register | No | 10085 |  |  | 2 | uint32 | kWh | [15 empty] | -
Total PCS number | total_pcs_number | Input Register | No | 10087 |  |  | 1 | uint16 | [16 empty] | -
Total BMS/battery number | total_bms_battery_number | Input Register | No | 10088 |  |  | 1 | uint16 | [16 empty] | -
PCS communication status | pcs_comm_bitword | Input Register | Yes | 10100 |  |  | 2 | uint32
BCS communication status | bms_comm_bitword | Input Register | Yes | 10102 |  |  | 2 | uint32
Online PCS number/Unit number | online_pcs_number_unit_number | Input Register | No | 10144 |  |  | 1 | uint16 | [16 empty] | -
Total rated PCS power | total_rated_pcs_power | Input Register | No | 10145 |  |  | 2 | uint32 | kW | 10 | [14 empty] | -
Total PCS active power | active_power | Input Register | Yes | 10147 |  |  | 2 | int32 | kW | 10 | [14 empty] | -
Total PCS reactive power | reactive_power | Input Register | Yes | 10149 |  |  | 2 | int32 | kVAR | -10 | [14 empty] | -
Total PCS power factor | power_factor | Input Register | Yes | 10151 |  |  | 1 | int16 |  | 1000 | [14 empty] | -
[15 empty] | sungrow_ess_01 | [6 empty] | 1000
Upper limit SOC level 2 | upper_soc_limit_2 | Holding Register | Yes | 10313 |  |  | 1 | uint16 | % | 10 | [14 empty] | Mutually exclusive with DC voltage limits
Upper limit SOC level 1 | upper_soc_limit_1 | Holding Register | Yes | 10314 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Upper limit SOC level 2 recovery | upper_soc_recovery_limit_2 | Holding Register | Yes | 10315 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Upper limit SOC level 1 recovery | upper_soc_recovery_limit_1 | Holding Register | Yes | 10316 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Lower limit SOC level 1 | lower_soc_limit_1 | Holding Register | Yes | 10317 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Lower limit SOC level 2 | lower_soc_limit_2 | Holding Register | Yes | 10318 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Lower limit SOC level 1 recovery | lower_soc_recovery_limit_1 | Holding Register | Yes | 10319 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Lower limit SOC level 2 recovery | lower_soc_recovery_limit_2 | Holding Register | Yes | 10320 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Lower limit SOC level2 timeout delay | soc_limit_2_timeout | Holding Register | Yes | 10324 |  |  | 1 | uint16 | min | [15 empty] | 0: Turn off the lower limit stop function Other values: SOC below the lower limit level 2 and exceeding the set time, PCS shutdown
Active power rising slop | active_power_up_rate | Holding Register | Yes | 10411 |  |  | 1 | uint16 | %/s
Active power drop slop | active_power_down_rate | Holding Register | Yes | 10412 |  |  | 1 | uint16 | %/s
Reactive power rising slop | reactive_power_up_rate | Holding Register | Yes | 10413 |  |  | 1 | uint16 | %/s
Reactive power drop slop | reactive_power_down_rate | Holding Register | Yes | 10414 |  |  | 1 | uint16 | %/s
Total PCS charge capacity | total_pcs_charge_capacity | Input Register | No | 10152 |  |  | 2 | uint32 | kWh | [15 empty] | -
Total PCS discharge capacity | total_pcs_discharge_capacity | Input Register | No | 10154 |  |  | 2 | uint32 | kWh | [15 empty] | -
Total PCS charge today | PCS_charge_today | Input Register | Yes | 10156 |  |  | 2 | int32 | kWh | 10 | [14 empty] | -
Total PCS discharge today | PCS_discharge_today | Input Register | Yes | 10158 |  |  | 2 | int32 | kWh | 10 | [14 empty] | -
Online BMS number | online_bms_number | Input Register | No | 10181 |  |  | 1 | uint16 | [16 empty] | -
Maximum DC voltage of system | maximum_dc_voltage_of_system | Input Register | No | 10182 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Minimum DC voltage of system | minimum_dc_voltage_of_system | Input Register | No | 10183 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Average DC voltage of system | voltage_dc | Input Register | Yes | 10184 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Maximum SOC of system | maximum_soc_of_system | Input Register | No | 10185 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Minimum SOC of system | minimum_soc_of_system | Input Register | No | 10186 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Average SOC of system | soc | Input Register | Yes | 10187 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Maximum SOH of system | maximum_soh_of_system | Input Register | No | 10188 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Minimum SOH of system | minimum_soh_of_system | Input Register | No | 10189 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Average SOH of system | soh | Input Register | Yes | 10190 |  |  | 1 | uint16 | % | 10 | [14 empty] | -
Device type code | pcs_device_type_code | Input Register | No | 10225 |  |  | 1 | uint16 | [16 empty] | -
Rated power | pcs_rated_power | Input Register | No | 10226 |  |  | 1 | uint16 | kW | 10 | [14 empty] | -
Overall grid voltage VAB | voltage_l1_l2 | Input Register | Yes | 10227 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Overall grid voltage VBC | voltage_l2_l3 | Input Register | Yes | 10228 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Overall grid voltage VCA | voltage_l3_l1 | Input Register | Yes | 10229 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
Overall phase A current | current_l1 | Input Register | Yes | 10230 |  |  | 1 | uint16 | A | 10 | [14 empty] | -
Overall phase B current | current_l2 | Input Register | Yes | 10231 |  |  | 1 | uint16 | A | 10 | [14 empty] | -
Overall phase C current | current_l3 | Input Register | Yes | 10232 |  |  | 1 | uint16 | A | 10 | [14 empty] | -
Overall DC power | dc_power | Input Register | Yes | 10233 |  |  | 1 | int16 | kW | 10 | [14 empty] | -
Overall active power | active_power | Input Register | No | 10234 |  |  | 1 | int16 | kW | 10 | [14 empty] | -
Overall reactive power | reactive_power | Input Register | No | 10235 |  |  | 1 | int16 | kVAR | 10 | [14 empty] | -
Overall Apparent Power | apparent_power | Input Register | Yes | 10236 |  |  | 1 | int16 | kVA | 10
Overall Power Factor | power_factor | Input Register | No | 10237 |  |  | 1 | uint16 |  | 1000
Overall charging | charging_kwh_total | Input Register | Yes | 10238 |  |  | 2 | uint32 | kWh | [15 empty] | -
Overall discharging | discharging_kwh_total | Input Register | Yes | 10240 |  |  | 2 | uint32 | kWh | [15 empty] | -
Overall daily charging | overall_daily_charging | Input Register | No | 10242 |  |  | 2 | uint32 | kWh | 10 | [14 empty] | -
Overall daily discharging | overall_daily_discharging | Input Register | No | 10244 |  |  | 2 | uint32 | kWh | 10 | [14 empty] | -
Overall daily running minutes | daily_running_mins | Input Register | No | 10246 |  |  | 1 | uint16 | min
Overall running hours | running_hrs | Input Register | Yes | 10247 |  |  | 2 | uint32 | hr
Positive Insulation | pos_gnd_insulation_ohm | Input Register | Yes | 10249 |  |  | 2 | uint32 | kohm | 100
Negative Insulation | neg_gnd_insulation_ohm | Input Register | Yes | 10251 |  |  | 2 | uint32 | kohm | 100
Battery Alarm | pcs_bat_alarm | Input Register | No | 10253 |  |  | 1 | uint16
Battery Fault | pcs_bat_fault | Input Register | No | 10254 |  |  | 1 | uint16
Temperature | pcs_amb_temp | Input Register | Yes | 10255 |  |  | 1 | int16 | C | 10
Humidity | pcs_amb_humidity | Input Register | Yes | 10256 |  |  | 1 | uint16 | %rh | 10
Overall Work Mode | pcs_mode | Input Register | Yes | 10257 |  |  | 1 | bitfield
On-Grid Constant Current |  | Input Register | Yes | 10257 |  | 0 |  | bit
On-Grid Constant Voltage |  | Input Register | Yes | 10257 |  | 1 |  | bit
On-Grid Constant Power (AC) |  | Input Register | Yes | 10257 |  | 2 |  | bit
On-Grid Constant Power (DC) |  | Input Register | Yes | 10257 |  | 3 |  | bit
On-Grid |  | Input Register | Yes | 10257 |  | 9 |  | bit
Off-Grid |  | Input Register | Yes | 10257 |  | 10 |  | bit
Overall Work state | pcs_status | Input Register | Yes | 10258 |  |  | 2 | bitfield | [16 empty] | -
Running |  | Input Register | Yes | 10258 |  | 0 |  | bit
Key Stop |  | Input Register | Yes | 10258 |  | 3 |  | bit
Standby |  | Input Register | Yes | 10258 |  | 4 |  | bit
Emergency Stop |  | Input Register | Yes | 10258 |  | 5 |  | bit
Starting |  | Input Register | Yes | 10258 |  | 6 |  | bit
Stopping |  | Input Register | Yes | 10258 |  | 7 |  | bit
Fault Stop |  | Input Register | Yes | 10258 |  | 9 |  | bit
Alarm Running |  | Input Register | Yes | 10258 |  | 10 |  | bit
Derating Running |  | Input Register | Yes | 10258 |  | 11 |  | bit
DSP Comunication error |  | Input Register | Yes | 10258 |  | 15 |  | bit
Charging/Discharging state | charging_status | Input Register | No | 10260 |  |  |  | bitfield | [16 empty] | 0:Charging 1:Discharging 2:Non-operating mode
Charging |  | Input Register | No | 10260 |  | 0 |  | bit
Discharging |  | Input Register | No | 10260 |  | 1 |  | bit
Non-operating mode |  | Input Register | No | 10260 |  | 2 |  | bit
Overall Fault state | pcs_faults | Input Register | Yes | 10261 |  |  | 1 | bitfield
Smoke alarm |  | Input Register | Yes | 10261 |  | 2 |  | bit
Door-opening protection |  | Input Register | Yes | 10261 |  | 3 |  | bit
AC power distribution alarm | power_dist_alarm | Input Register | Yes | 10262 |  |  | 1 | bitfield
Internal Power Supply over voltage |  | Input Register | Yes | 10262 |  | 3 |  | bit
Internal Power Supply under voltage |  | Input Register | Yes | 10262 |  | 4 |  | bit
Overall Alarm | pcs_alarm | Input Register | Yes | 10263 |  |  | 2 | bitfield
Temperture & Humidity board communication error |  | Input Register | Yes | 10263 |  | 0 |  | bit
Switch Board Communication Error |  | Input Register | Yes | 10263 |  | 1 |  | bit
Tributary board communication error |  | Input Register | Yes | 10263 |  | 2 |  | bit
PCS Heartbeat count | pcs_heartbeat_count | Input Register | No | 10265 |  |  | 1 | uint16 | [16 empty] | -
Overall grid frequency | pcs_frequency | Input Register | No | 10266 |  |  | 1 | uint16 | hz | 100
Node State of Transformer | pcs_transformer_status | Input Register | Yes | 10267 |  |  | 2 | bitfield
Transformer oil temperature alarm |  | Input Register | Yes | 10267 |  | 2 |  | bit
Transformer oil temperature tripping |  | Input Register | Yes | 10267 |  | 3 |  | bit
Pressure relief valve tripping |  | Input Register | Yes | 10267 |  | 4 |  | bit
Low oil temperature alarm (tripping) |  | Input Register | Yes | 10267 |  | 5 |  | bit
Gas relay alarm |  | Input Register | Yes | 10267 |  | 6 |  | bit
Gas relay tripping |  | Input Register | Yes | 10267 |  | 7 |  | bit
Pressure alarm |  | Input Register | Yes | 10267 |  | 8 |  | bit
Low oil level alarm |  | Input Register | Yes | 10267 |  | 9 |  | bit
Disconnector node |  | Input Register | Yes | 10267 |  | 10 |  | bit
Overcurrent protection signal |  | Input Register | Yes | 10267 |  | 11 |  | bit
Switchgear load switch node 1 |  | Input Register | Yes | 10267 |  | 12 |  | bit
HV cabinet door travel switch |  | Input Register | Yes | 10267 |  | 13 |  | bit
Switchgear load switch node 2 |  | Input Register | Yes | 10267 |  | 14 |  | bit
Circuit breaker node |  | Input Register | Yes | 10267 |  | 15 |  | bit
PCS 1 DC voltage | pcs1_dc_voltage | Input Register | Yes | 10269 |  |  | 1 | int16 | V | 10 | [14 empty] | -
PCS 1 DC current | pcs1_dc_current | Input Register | Yes | 10270 |  |  | 1 | int16 | A | 10 | [14 empty] | -
PCS 1 DC power | pcs1_dc_power | Input Register | Yes | 10271 |  |  | 1 | int16 | kW | 10 | [14 empty] | -
PCS 1 Grid voltage VAB | pcs1_voltage_l1_l2 | Input Register | Yes | 10272 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
PCS 1 Grid voltage VBC | pcs1_voltage_l2_l3 | Input Register | Yes | 10273 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
PCS 1 Grid voltage VCA | pcs1_voltage_l3_l1 | Input Register | Yes | 10274 |  |  | 1 | uint16 | V | 10 | [14 empty] | -
PCS 1 Phase-A current | pcs1_current_l1 | Input Register | Yes | 10275 |  |  | 1 | uint16 | A | 10 | [14 empty] | -
PCS 1 Phase-B current | pcs1_current_l2 | Input Register | Yes | 10276 |  |  | 1 | uint16 | A | 10 | [14 empty] | -
PCS 1 Phase-C current | pcs1_current_l3 | Input Register | Yes | 10277 |  |  | 1 | uint16 | A | 10 | [14 empty] | -
PCS 1 Active power | pcs1_active_power | Input Register | Yes | 10278 |  |  | 2 | int32 | kW | 10 | [14 empty] | -
PCS 1 Reactive power | pcs1_reactive_power | Input Register | Yes | 10280 |  |  | 2 | int32 | kVAR | 10 | [14 empty] | -
PCS 1 Alarm running state | pcs1_alarms | Input Register | Yes | 10282 |  |  | 2 | bitfield | [16 empty] | See PCS communication protocol for detail
Temperature abnormal |  | Input Register | Yes | 10282 |  | 0 |  | bit
Low Insulation resistance |  | Input Register | Yes | 10282 |  | 1 |  | bit
GFRT operation |  | Input Register | Yes | 10282 |  | 2 |  | bit
DC Fuse abnormal |  | Input Register | Yes | 10282 |  | 4 |  | bit
DC sensor abnormal |  | Input Register | Yes | 10282 |  | 6 |  | bit
DC SPD Alarm |  | Input Register | Yes | 10282 |  | 7 |  | bit
AC SPD Alarm |  | Input Register | Yes | 10282 |  | 8 |  | bit
Charging condition not met |  | Input Register | Yes | 10282 |  | 9 |  | bit
Discharging condition not met |  | Input Register | Yes | 10282 |  | 10 |  | bit
DC Switch abnormal |  | Input Register | Yes | 10282 |  | 12 |  | bit
Fan 1 abnormal |  | Input Register | Yes | 10282 |  | 13 |  | bit
AC Switch abnormal |  | Input Register | Yes | 10282 |  | 17 |  | bit
Fan 2 Abnormal |  | Input Register | Yes | 10282 |  | 18 |  | bit
AC Main Contactor Abnormal |  | Input Register | Yes | 10282 |  | 19 |  | bit
IO-LCD communication error |  | Input Register | Yes | 10282 |  | 21 |  | bit
PCS 1 Fault state | pcs1_faults | Input Register | Yes | 10284 |  |  | 4 | bitfield | [16 empty] | -
DC under-voltage |  | Input Register | Yes | 10284 |  | 0 |  | bit
DC over-voltage |  | Input Register | Yes | 10284 |  | 1 |  | bit
Grid under-voltage |  | Input Register | Yes | 10284 |  | 2 |  | bit
Grid over-voltage |  | Input Register | Yes | 10284 |  | 3 |  | bit
Grid under-frequency |  | Input Register | Yes | 10284 |  | 4 |  | bit
Grid over-frequency |  | Input Register | Yes | 10284 |  | 5 |  | bit
Grid Contactor |  | Input Register | Yes | 10284 |  | 6 |  | bit
Islanding protection |  | Input Register | Yes | 10284 |  | 7 |  | bit
PDP protection |  | Input Register | Yes | 10284 |  | 9 |  | bit
Module over temperature |  | Input Register | Yes | 10284 |  | 10 |  | bit
Reactor over temperature |  | Input Register | Yes | 10284 |  | 11 |  | bit
Transformer over temperature |  | Input Register | Yes | 10284 |  | 12 |  | bit
AC leakage current protection |  | Input Register | Yes | 10284 |  | 13 |  | bit
Overload protection |  | Input Register | Yes | 10284 |  | 15 |  | bit
Fan 1 fault |  | Input Register | Yes | 10284 |  | 17 |  | bit
DC Fuse Fault |  | Input Register | Yes | 10284 |  | 18 |  | bit
DC over-current |  | Input Register | Yes | 10284 |  | 20 |  | bit
AC over-current |  | Input Register | Yes | 10284 |  | 21 |  | bit
Ambient Over temperature |  | Input Register | Yes | 10284 |  | 23 |  | bit
Hardware fault |  | Input Register | Yes | 10284 |  | 24 |  | bit
Insulation impedance |  | Input Register | Yes | 10284 |  | 32 |  | bit
AC SPD Fault |  | Input Register | Yes | 10284 |  | 33 |  | bit
Sampling Fault |  | Input Register | Yes | 10284 |  | 34 |  | bit
Battery Polarity reversed |  | Input Register | Yes | 10284 |  | 35 |  | bit
LCD-DSP fault |  | Input Register | Yes | 10284 |  | 37 |  | bit
AC current unbalanced 1 |  | Input Register | Yes | 10284 |  | 38 |  | bit
Host Fault |  | Input Register | Yes | 10284 |  | 39 |  | bit
DC SPD fault |  | Input Register | Yes | 10284 |  | 40 |  | bit
DC Soft Failure |  | Input Register | Yes | 10284 |  | 41 |  | bit
DC Injection fault |  | Input Register | Yes | 10284 |  | 42 |  | bit
DC Switch fault |  | Input Register | Yes | 10284 |  | 43 |  | bit
Device Code Repeat Fault |  | Input Register | Yes | 10284 |  | 44 |  | bit
Parallel operation communication fault |  | Input Register | Yes | 10284 |  | 45 |  | bit
Control cabinet temperature abnormal |  | Input Register | Yes | 10284 |  | 46 |  | bit
AC Voltage unbalance |  | Input Register | Yes | 10284 |  | 48 |  | bit
Battery Communication Failure |  | Input Register | Yes | 10284 |  | 49 |  | bit
BMS Failure |  | Input Register | Yes | 10284 |  | 50 |  | bit
AC Switch Fault |  | Input Register | Yes | 10284 |  | 51 |  | bit
Soft start fault |  | Input Register | Yes | 10284 |  | 52 |  | bit
DC Voltage sampling fault |  | Input Register | Yes | 10284 |  | 53 |  | bit
AC Current unbalanced 2 |  | Input Register | Yes | 10284 |  | 55 |  | bit
AC Current unbalanced 3 |  | Input Register | Yes | 10284 |  | 56 |  | bit
Drive Board Fault |  | Input Register | Yes | 10284 |  | 57 |  | bit
Neutral point potential shift |  | Input Register | Yes | 10284 |  | 58 |  | bit
Carrier Sync Fault |  | Input Register | Yes | 10284 |  | 59 |  | bit
PCS 1 Charging/Discharging state | pcs1_charging_discharging_state | Input Register | No | 10288 |  |  | 1 | uint16 | [16 empty] | 0:Charging 1:Discharging 2:Non-operating mode
PCS 1 Daily charging | pcs1_daily_charging | Input Register | No | 10289 |  |  | 2 | uint32 | kWh | 10 | [14 empty] | -
PCS 1 Daily discharging | pcs1_daily_discharging | Input Register | No | 10291 |  |  | 2 | uint32 | kWh | 10 | [14 empty] | -
PCS 1 Total charging | pcs1_total_charging | Input Register | No | 10293 |  |  | 2 | uint32 | kWh | [15 empty] | -
PCS 1 Total discharging | pcs1_total_discharging | Input Register | No | 10295 |  |  | 2 | uint32 | kWh | [15 empty] | -
PCS 1 Work state | pcs1_status | Input Register | Yes | 10297 |  |  | 2 | bitfield | [16 empty] | See PCS communication protocol for detail
Running |  | Input Register | Yes | 10297 |  | 0 |  | bit
Key Stop |  | Input Register | Yes | 10297 |  | 3 |  | bit
Standby |  | Input Register | Yes | 10297 |  | 4 |  | bit
Emergency Stop |  | Input Register | Yes | 10297 |  | 5 |  | bit
Starting |  | Input Register | Yes | 10297 |  | 6 |  | bit
Stopping |  | Input Register | Yes | 10297 |  | 7 |  | bit
Fault Stop |  | Input Register | Yes | 10297 |  | 9 |  | bit
Alarm Running |  | Input Register | Yes | 10297 |  | 10 |  | bit
Derating Running |  | Input Register | Yes | 10297 |  | 11 |  | bit
DSP Communication Error |  | Input Register | Yes | 10297 |  | 15 |  | bit
PCS 1 Operating mode | pcs1_mode | Input Register | Yes | 10299 |  |  | 1 | bitfield | [16 empty] | -
Constant Current |  | Input Register | Yes | 10299 |  | 0 |  | bit
Constant Voltage |  | Input Register | Yes | 10299 |  | 1 |  | bit
Constant Power (AC) |  | Input Register | Yes | 10299 |  | 2 |  | bit
Constant Power (DC) |  | Input Register | Yes | 10299 |  | 3 |  | bit
On-grid Mode |  | Input Register | Yes | 10299 |  | 9 |  | bit
Off-grid Mode |  | Input Register | Yes | 10299 |  | 10 |  | bit
PCS 1 Daily running minutes | pcs1_daily_running_minutes | Input Register | No | 10300 |  |  | 1 | uint16 | MIN | [15 empty] | -
PCS 1 Total running hours | pcs1_total_running_hours | Input Register | No | 10301 |  |  | 2 | uint32 | H | [15 empty] | -
PCS 1 Grid freq | pcs1_grid_freq | Input Register | No | 10303 |  |  | 1 | uint16 | Hz | 100 | [14 empty] | -
PCS 1 Power factor | pcs1_power_factor | Input Register | No | 10304 |  |  | 1 | uint16 |  | 1000 | [14 empty] | -
PCS 1 Node | pcs1_node_status | Input Register | Yes | 10305 |  |  | 1 | bitfield
AC circuit breaker status |  | Input Register | Yes | 10305 |  | 0 |  | bit
AC main-contactor status |  | Input Register | Yes | 10305 |  | 1 |  | bit
DC switch 1 status |  | Input Register | Yes | 10305 |  | 2 |  | bit
DC switch 2 status |  | Input Register | Yes | 10305 |  | 3 |  | bit
DC switch 3 status |  | Input Register | Yes | 10305 |  | 4 |  | bit
DC switch 4 status |  | Input Register | Yes | 10305 |  | 5 |  | bit
DC fuse branch 1 status |  | Input Register | Yes | 10305 |  | 6 |  | bit
DC fuse branch 2 status |  | Input Register | Yes | 10305 |  | 7 |  | bit
DC fuse branch 3 status |  | Input Register | Yes | 10305 |  | 8 |  | bit
DC fuse branch 4 status |  | Input Register | Yes | 10305 |  | 9 |  | bit
DC auxiliary switch 1 status |  | Input Register | Yes | 10305 |  | 10 |  | bit
DC auxiliary switch 2 status |  | Input Register | Yes | 10305 |  | 11 |  | bit
DC auxiliary switch 3 status |  | Input Register | Yes | 10305 |  | 12 |  | bit
DC auxiliary switch 4 status |  | Input Register | Yes | 10305 |  | 13 |  | bit
PCS 2 Node | pcs2_node_status | Input Register | Yes | 10306 |  |  | 1 | bitield
AC circuit breaker status |  | Input Register | Yes | 10306 |  | 0 |  | bit
AC main-contactor status |  | Input Register | Yes | 10306 |  | 1 |  | bit
DC switch 1 status |  | Input Register | Yes | 10306 |  | 2 |  | bit
DC switch 2 status |  | Input Register | Yes | 10306 |  | 3 |  | bit
DC switch 3 status |  | Input Register | Yes | 10306 |  | 4 |  | bit
DC switch 4 status |  | Input Register | Yes | 10306 |  | 5 |  | bit
DC fuse branch 1 status |  | Input Register | Yes | 10306 |  | 6 |  | bit
DC fuse branch 2 status |  | Input Register | Yes | 10306 |  | 7 |  | bit
DC fuse branch 3 status |  | Input Register | Yes | 10306 |  | 8 |  | bit
DC fuse branch 4 status |  | Input Register | Yes | 10306 |  | 9 |  | bit
DC auxiliary switch 1 status |  | Input Register | Yes | 10306 |  | 10 |  | bit
DC auxiliary switch 2 status |  | Input Register | Yes | 10306 |  | 11 |  | bit
DC auxiliary switch 3 status |  | Input Register | Yes | 10306 |  | 12 |  | bit
DC auxiliary switch 4 status |  | Input Register | Yes | 10306 |  | 13 |  | bit
pcs1 | pcs2 | Input Register | Yes | 10307 | 10269 |  | 35 | repeat
Transformer oil temp | pcs_trans_oil_temp | Input Register | Yes | 10343 |  |  |  | int16 |  | 10
Leakage Current | pcs_leakage_current | Input Register | Yes | 10344 |  |  |  | uint16 | A | 100
BMS 1 Battery type | bms1_battery_type | Input Register | No | 13601 |  |  | 1 | uint16
BMS 1 Hardware version | bms1_hardware_version | Input Register | No | 13602 |  |  | 2 | uint32
BMS 1 Software version | bms1_software_version | Input Register | No | 13604 |  |  | 2 | uint32
BMS 1 system heartbeat | bms1_system_heartbeat | Input Register | No | 13606 |  |  | 1 | uint16
BMS 1 System voltage | bms1_full_dc_voltage | Input Register | Yes | 13607 |  |  | 1 | uint16 | V | 10
BMS 1 System current | bms1_dc_current | Input Register | Yes | 13608 |  |  | 1 | int16 | A
BMS 1 System SOC | bms1_full_soc | Input Register | Yes | 13609 |  |  | 1 | uint16 | % | 10
BMS 1 System SOH | bms1_soh | Input Register | Yes | 13610 |  |  | 1 | uint16 | % | 10
BMS 1 Service voltage | bms1_dc_voltage | Input Register | Yes | 13611 |  |  | 1 | uint16 | V | 10
BMS 1 Service SOC | bms1_soc | Input Register | Yes | 13612 |  |  | 1 | uint16 | % | 10
BMS 1 Number of racks in service | bms1_racks_in_service | Input Register | Yes | 13613 |  |  | 1 | uint16
BMS 1 Total rack count | bms1_total_racks | Input Register | Yes | 13614 |  |  | 1 | uint16
BMS 1 System mode | bms1_status | Input Register | Yes | 13616 |  |  | 1 | bitfield
First soc calibrate tip clear[CMD] |  | Input Register | Yes | 13616 |  | 0 |  | bit
Second soc calibrate tip clear[CMD] |  | Input Register | Yes | 13616 |  | 1 |  | bit
First soc calibrate tip clear cancel[CMD] |  | Input Register | Yes | 13616 |  | 2 |  | bit
Second soc calibrate tip clear cancel[CMD] |  | Input Register | Yes | 13616 |  | 3 |  | bit
Ready |  | Input Register | Yes | 13616 |  | 8 |  | bit
Idle |  | Input Register | Yes | 13616 |  | 9 |  | bit
Offline |  | Input Register | Yes | 13616 |  | 10 |  | bit
[CMD] Main SW Off |  | Input Register | Yes | 13616 |  | 12 |  | bit
[CMD] Main SW On |  | Input Register | Yes | 13616 |  | 13 |  | bit
Discharge |  | Input Register | Yes | 13616 |  | 14 |  | bit
Charge |  | Input Register | Yes | 13616 |  | 15 |  | bit
BMS 1 Ambient Temp 1 | bms1_amb_temp_1 | Input Register | Yes | 13618 |  |  |  | int16 | °C | 10
BMS 1 Ambient Temp 2 | bms1_amb_temp_2 | Input Register | Yes | 13619 |  |  |  | int16 | °C | 10
BMS 1 Charge limit | bms1_charge_pulse_current_limit | Input Register | Yes | 13621 |  |  | 1 | uint16 | A | 10
BMS 1 Discharge limit | bms1_discharge_pulse_current_limit | Input Register | Yes | 13622 |  |  | 1 | uint16 | A | 10
BMS 1 Charge limit | bms1_charge_current_limit | Input Register | Yes | 13623 |  |  | 1 | uint16 | A | 10
BMS 1 Discharge limit | bms1_discharge_current_limit | Input Register | Yes | 13624 |  |  | 1 | uint16 | A | 10
BMS 1 Maximum cell voltage of system | bms1_max_cell_voltage | Input Register | Yes | 13626 |  |  | 1 | uint16 | mV | 10000
BMS 1 Minimum cell voltage of system | bms1_min_cell_voltage | Input Register | Yes | 13627 |  |  | 1 | uint16 | mV | 10000
BMS 1 Max cell temperature of system | bms1_max_cell_temp | Input Register | Yes | 13628 |  |  | 1 | int16 | °C | 10
BMS 1 Min cell temperature of system | bms1_min_cell_temp | Input Register | Yes | 13629 |  |  | 1 | int16 | °C | 10
BMS 1 Cell Volt Diff | bms1_cell_voltage_diff | Input Register | Yes | 13630 |  |  | 1 | uint16 | mV | 10000
BMS 1 Cell Temp Diff | bms1_cell_temp_diff | Input Register | Yes | 13631 |  |  | 1 | uint16 | °C | 10
BMS 1 SOC Diff | bms1_soc_diff | Input Register | Yes | 13632 |  |  | 1 | uint16 | % | 10
BMS 1 Rack V diff | bms1_rack_voltage_diff | Input Register | Yes | 13633 |  |  | 1 | uint16 | V | 10
BMS 1 Rack I diff | bms1_rack_current_diff | Input Register | Yes | 13634 |  |  | 1 | uint16 | A | 10
Max Cell voltage rack num | bms1_max_cell_voltage_rack_num | Input Register | Yes | 13639 |  |  | 1 | uint16
Max Cell voltage bmu/cell | bms1_max_cell_voltage_bmu_cell | Input Register | Yes | 13640 |  |  | 1 | uint16
Min Cell Voltage rack num | bms1_min_cell_voltage_rack_num | Input Register | Yes | 13641 |  |  | 1 | uint16
Min Cell Voltage bmu/cell | bms1_min_cell_voltage_bmu_cell | Input Register | Yes | 13642 |  |  | 1 | uint16
Max Cell Temperature rack num | bms1_max_cell_temp_rack_num | Input Register | Yes | 13643 |  |  | 1 | uint16
Max Cell Temperature bmu/cell | bms1_max_cell_temp_bmu_cell | Input Register | Yes | 13644 |  |  | 1 | uint16
Min Cell Temperature rack num | bms1_min_cell_temp_rack_num | Input Register | Yes | 13645 |  |  | 1 | uint16
Min Cell Temperature bmu/cell | bms1_min_cell_temp_bmu_cell | Input Register | Yes | 13646 |  |  | 1 | uint16
max/min rack volt position | bms1_max_min_rack_volt_position | Input Register | Yes | 13647 |  |  | 1 | uint16
max/min rack current position | bms1_max_min_rack_current_position | Input Register | Yes | 13648 |  |  | 1 | uint16
Negative voltage position | bms1_negative_voltage_position | Input Register | Yes | 13649 |  |  | 1 | uint16
BMS 1 Alarm Level 1 | bms1_alarms | Input Register | Yes | 13653 |  |  | 2 | bitfield
Cell voltage high |  | Input Register | Yes | 13653 |  | 0 |  | bit
Cell voltage low |  | Input Register | Yes | 13653 |  | 1 |  | bit
Rack voltage high |  | Input Register | Yes | 13653 |  | 2 |  | bit
Rack voltage low |  | Input Register | Yes | 13653 |  | 3 |  | bit
Cell voltage difference high |  | Input Register | Yes | 13653 |  | 4 |  | bit
Cell temperature high |  | Input Register | Yes | 13653 |  | 5 |  | bit
Cell temperature low |  | Input Register | Yes | 13653 |  | 6 |  | bit
Cell temperature difference high |  | Input Register | Yes | 13653 |  | 7 |  | bit
Insulation alarm |  | Input Register | Yes | 13653 |  | 8 |  | bit
Pack communication alarm |  | Input Register | Yes | 13653 |  | 9 |  | bit
Vol exception alarm |  | Input Register | Yes | 13653 |  | 10 |  | bit
Temp exception alarm |  | Input Register | Yes | 13653 |  | 11 |  | bit
Current sample alarm |  | Input Register | Yes | 13653 |  | 12 |  | bit
Heartbeat alarm |  | Input Register | Yes | 13653 |  | 13 |  | bit
Charge OC alarm |  | Input Register | Yes | 13653 |  | 14 |  | bit
Discharge OC alarm |  | Input Register | Yes | 13653 |  | 15 |  | bit
Short error |  | Input Register | Yes | 13653 |  | 16 |  | bit
Pack voltage high |  | Input Register | Yes | 13653 |  | 18 |  | bit
Pack voltage low |  | Input Register | Yes | 13653 |  | 19 |  | bit
Pack delta voltage high |  | Input Register | Yes | 13653 |  | 20 |  | bit
bms1_alarms | bms1_alarms_2nd_level |  | Yes | 13655 | 13653 |  | 2 | repeat
bms1_alarms | bms1_alarms_3nd_level |  | Yes | 13657 | 13653 |  | 2 | repeat
BMS 1 hw Faults | bms1_faults | Input Register | Yes | 13659 |  |  | 1 | bitfield
Positive relay fault |  | Input Register | Yes | 13659 |  | 0 |  | bit
Negative relay fault |  | Input Register | Yes | 13659 |  | 1 |  | bit
Positive relay close fail |  | Input Register | Yes | 13659 |  | 2 |  | bit
Negative relay close fail |  | Input Register | Yes | 13659 |  | 3 |  | bit
Fuse open |  | Input Register | Yes | 13659 |  | 4 |  | bit
First alarm position | bms1_first_alarm_pos | Input Register | Yes | 13664 |  |  | 1 | uint16
Second alarm position | bms1_second_alarm_pos | Input Register | Yes | 13665 |  |  | 1 | uint16
Third alarm position | bms1_third_alarm_pos | Input Register | Yes | 13666 |  |  | 1 | uint16
Positive relay fault position | bms1_positive_relay_fault_pos | Input Register | Yes | 13667 |  |  | 1 | uint16
Negative relay fault position | bms1_negative_relay_fault_pos | Input Register | Yes | 13668 |  |  | 1 | uint16
Fuse fault position | bms1_fuse_fault_pos | Input Register | Yes | 13669 |  |  | 1 | uint16
R-S comm fail pisition | bms1_r_s_comm_pos | Input Register | Yes | 13670 |  |  | 1 | uint16
Soc recalibrate tips | bms1_soc_cal | Input Register | Yes | 13671 |  |  | 1 | bitfield
First SOC calibration tip |  | Input Register | Yes | 13671 |  | 0 |  | bit
Second SOC calibration tip |  | Input Register | Yes | 13671 |  | 1 |  | bit
System alarm status | bms1_alarm_status | Input Register | Yes | 13672 |  |  | 1 | bitfield
R-S comm fail |  | Input Register | Yes | 13672 |  | 0 |  | bit
Reserved |  | Input Register | Yes | 13672 |  | 1 |  | bit
Rack voltage difference high |  | Input Register | Yes | 13672 |  | 2 |  | bit
Cell voltage difference high |  | Input Register | Yes | 13672 |  | 3 |  | bit
Temperature difference high |  | Input Register | Yes | 13672 |  | 4 |  | bit
Negative voltage fault |  | Input Register | Yes | 13672 |  | 5 |  | bit
Ambient OT |  | Input Register | Yes | 13672 |  | 6 |  | bit
Ambient UT |  | Input Register | Yes | 13672 |  | 7 |  | bit
Ambient T sampling abnormal |  | Input Register | Yes | 13672 |  | 8 |  | bit
Input state alarm |  | Input Register | Yes | 13672 |  | 9 |  | bit
Input state fault |  | Input Register | Yes | 13672 |  | 10 |  | bit
Rack num. protection |  | Input Register | Yes | 13672 |  | 11 |  | bit
Rack I imbalance alarm |  | Input Register | Yes | 13672 |  | 12 |  | bit
Rack I imbalance protection |  | Input Register | Yes | 13672 |  | 13 |  | bit
Reserved |  | Input Register | Yes | 13672 |  | 14 |  | bit
System stop |  | Input Register | Yes | 13672 |  | 15 |  | bit
Digital input status | bms1_dio_status | Input Register | Yes | 13673 |  |  | 1 | bitfield
DIO 1 |  | Input Register | Yes | 13673 |  | 0 |  | bit
DIO 2 |  | Input Register | Yes | 13673 |  | 1 |  | bit
DIO 3 |  | Input Register | Yes | 13673 |  | 2 |  | bit
DIO 4 |  | Input Register | Yes | 13673 |  | 3 |  | bit
DIO 5 |  | Input Register | Yes | 13673 |  | 4 |  | bit
DIO 6 |  | Input Register | Yes | 13673 |  | 5 |  | bit
DIO 7 |  | Input Register | Yes | 13673 |  | 6 |  | bit
DIO 8 |  | Input Register | Yes | 13673 |  | 7 |  | bit
DIO 9 |  | Input Register | Yes | 13673 |  | 8 |  | bit
DIO 10 |  | Input Register | Yes | 13673 |  | 9 |  | bit
DIO 11 |  | Input Register | Yes | 13673 |  | 10 |  | bit
DIO 12 |  | Input Register | Yes | 13673 |  | 11 |  | bit
DIO 13 |  | Input Register | Yes | 13673 |  | 12 |  | bit
DIO 14 |  | Input Register | Yes | 13673 |  | 13 |  | bit
Max cell capacity | bms1_max_cell_capacity | Input Register | Yes | 13675 |  |  | 1 | uint16
Min cell capacity | bms1_min_cell_capacity | Input Register | Yes | 13676 |  |  | 1 | uint16
Max cell capacity rack | bms1_max_cell_capacity_rack_num | Input Register | Yes | 13677 |  |  | 1 | uint16
Min cell capacity rack | bms1_min_cell_capacity_rack_num | Input Register | Yes | 13679 |  |  | 1 | uint16
Max pack voltage | bms1_max_pack_voltage | Input Register | Yes | 13681 |  |  | 1 | uint16
Min pack voltage | bms1_min_pack_voltage | Input Register | Yes | 13682 |  |  | 1 | uint16
Max pack voltage rack num | bms1_max_pack_voltage_rack_num | Input Register | Yes | 13683 |  |  | 1 | uint16
Max pack voltage pack num | bms1_max_pack_voltage_pack_num | Input Register | Yes | 13684 |  |  | 1 | uint16
Min pack voltage rack num | bms1_min_pack_voltage_rack_num | Input Register | Yes | 13685 |  |  | 1 | uint16
Min pack voltage pack num | bms1_min_pack_voltage_pack_num | Input Register | Yes | 13686 |  |  | 1 | uint16
Charge/discharge Cycles | bms1_charge_discharge_cycles | Input Register | Yes | 13687 |  |  | 2 | uint32
Total charge power(GWh) | bms1_total_charge_power_gwh | Input Register | Yes | 13690 |  |  | 1 | uint16
Total charge power(MWh) | bms1_total_charge_power_mwh | Input Register | Yes | 13691 |  |  | 1 | uint16
Total charge power(kWh) | bms1_total_charge_power_kwh | Input Register | Yes | 13692 |  |  | 1 | uint16
Total discharge power(GWh) | bms1_total_discharge_power_gwh | Input Register | Yes | 13693 |  |  | 1 | uint16
Total discharge power(MWh) | bms1_total_discharge_power_mwh | Input Register | Yes | 13694 |  |  | 1 | uint16
Total discharge power(KWh) | bms1_total_discharge_power_kwh | Input Register | Yes | 13695 |  |  | 1 | uint16
Total charge capacity(GAh) | bms1_total_charge_capacity_mah | Input Register | Yes | 13696 |  |  | 1 | uint16
Total charge capacity(MAh) | bms1_total_charge_capacity_kah | Input Register | Yes | 13697 |  |  | 1 | uint16
Total charge capacity(KAh) | bms1_total_charge_capacity_ah | Input Register | Yes | 13698 |  |  | 1 | uint16
Total discharge capacity(GAh) | bms1_total_discharge_capacity_mah | Input Register | Yes | 13699 |  |  | 1 | uint16
Total discharge capacity(MAh) | bms1_total_discharge_capacity_kah | Input Register | Yes | 13700 |  |  | 1 | uint16
Total discharge capacity(KAh) | bms1_total_discharge_capacity_ah | Input Register | Yes | 13701 |  |  | 1 | uint16
bms1 | bms2 |  | Yes | 13702 | 13601 |  | 101 | repeat
BSC 1 system fault status | bsc1_faults | Input Register | Yes | 18003 |  |  | 2 | bitfield
UPS Mains Disconnect |  | Input Register | Yes | 18003 |  | 0 |  | bit
Emergency Stop |  | Input Register | Yes | 18003 |  | 1 |  | bit
Transformer Over Temperature |  | Input Register | Yes | 18003 |  | 2 |  | bit
Auxiliary Power Off |  | Input Register | Yes | 18003 |  | 3 |  | bit
AC SPD Fault |  | Input Register | Yes | 18003 |  | 4 |  | bit
DC SPD Fault |  | Input Register | Yes | 18003 |  | 5 |  | bit
DC Load Switch Off |  | Input Register | Yes | 18003 |  | 6 |  | bit
DC Fuse |  | Input Register | Yes | 18003 |  | 7 |  | bit
Travel Switch |  | Input Register | Yes | 18003 |  | 8 |  | bit
Firefighting Ventilation |  | Input Register | Yes | 18003 |  | 9 |  | bit
Firefighting Alarm |  | Input Register | Yes | 18003 |  | 10 |  | bit
Firefighting Fault |  | Input Register | Yes | 18003 |  | 11 |  | bit
Input 13 |  | Input Register | Yes | 18003 |  | 12 |  | bit
Input 14 |  | Input Register | Yes | 18003 |  | 13 |  | bit
Input 15 |  | Input Register | Yes | 18003 |  | 14 |  | bit
Input 16 |  | Input Register | Yes | 18003 |  | 15 |  | bit
BMS Communication Fault |  | Input Register | Yes | 18003 |  | 30 |  | bit
BMS Fault |  | Input Register | Yes | 18003 |  | 31 |  | bit
BSC 1 system alarm status | bsc1_alarms | Input Register | Yes | 18005 |  |  | 2 | bitfield
Input 1 |  | Input Register | Yes | 18005 |  | 0 |  | bit
Input 2 |  | Input Register | Yes | 18005 |  | 1 |  | bit
Input 3 |  | Input Register | Yes | 18005 |  | 2 |  | bit
Input 4 |  | Input Register | Yes | 18005 |  | 3 |  | bit
Input 5 |  | Input Register | Yes | 18005 |  | 4 |  | bit
Input 6 |  | Input Register | Yes | 18005 |  | 5 |  | bit
Input 7 |  | Input Register | Yes | 18005 |  | 6 |  | bit
Input 8 |  | Input Register | Yes | 18005 |  | 7 |  | bit
Input 9 |  | Input Register | Yes | 18005 |  | 8 |  | bit
Input 10 |  | Input Register | Yes | 18005 |  | 9 |  | bit
Input 11 |  | Input Register | Yes | 18005 |  | 10 |  | bit
Input 12 |  | Input Register | Yes | 18005 |  | 11 |  | bit
Input 13 |  | Input Register | Yes | 18005 |  | 12 |  | bit
Input 14 |  | Input Register | Yes | 18005 |  | 13 |  | bit
Input 15 |  | Input Register | Yes | 18005 |  | 14 |  | bit
Input 16 |  | Input Register | Yes | 18005 |  | 15 |  | bit
UPS Fault |  | Input Register | Yes | 18005 |  | 21 |  | bit
UPS communication fault alarm |  | Input Register | Yes | 18005 |  | 22 |  | bit
TEMP & HUM communication fault alarm |  | Input Register | Yes | 18005 |  | 23 |  | bit
PC Communication Fault |  | Input Register | Yes | 18005 |  | 24 |  | bit
Ammeter Communication Fault Alarm |  | Input Register | Yes | 18005 |  | 25 |  | bit
HVAC Fault |  | Input Register | Yes | 18005 |  | 26 |  | bit
HVAC Communication Fault |  | Input Register | Yes | 18005 |  | 27 |  | bit
Battery DC voltage difference abnormal in group |  | Input Register | Yes | 18005 |  | 28 |  | bit
BMS Alarm |  | Input Register | Yes | 18005 |  | 29 |  | bit
BMS Fault Alarm |  | Input Register | Yes | 18005 |  | 30 |  | bit
BMS Communication Fault |  | Input Register | Yes | 18005 |  | 31 |  | bit
BSC 1 Battery system1#HVAC work status | bsc1_hvac1_status | Input Register | Yes | 18009 |  |  | 1 | uint16
BSC 1 Battery system1#HVAC return air temperature | bsc1_hvac1_ret_temp | Input Register | Yes | 18010 |  |  | 1 | int16 | °C | 10
bsc1_hvac1 | bsc1_hvac2 | Input Register | Yes | 18011 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac3 | Input Register | Yes | 18013 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac4 | Input Register | Yes | 18015 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac5 | Input Register | No | 18017 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac6 | Input Register | No | 18019 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac7 | Input Register | No | 18021 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac8 | Input Register | No | 18023 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac9 | Input Register | No | 18025 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac10 | Input Register | No | 18027 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac11 | Input Register | No | 18029 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac12 | Input Register | No | 18031 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac13 | Input Register | No | 18033 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac14 | Input Register | No | 18035 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac15 | Input Register | No | 18037 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac16 | Input Register | No | 18039 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac17 | Input Register | No | 18041 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac18 | Input Register | No | 18043 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac19 | Input Register | No | 18045 | 18009 |  | 2 | repeat
bsc1_hvac1 | bsc1_hvac20 | Input Register | No | 18047 | 18009 |  | 2 | repeat
1#Temperature | bcs1_temp_1 | Input Register | Yes | 18049 |  |  | 1 | int16 | °C | 10
1#Humidity | bcs1_humidity_1 | Input Register | Yes | 18050 |  |  | 1 | uint16 | % | 10
2#Temperature | bcs1_temp_2 | Input Register | Yes | 18051 |  |  | 1 | int16 | °C | 10
2#Humidity | bcs1_humidity_2 | Input Register | Yes | 18052 |  |  | 1 | uint16 | % | 10
UPS Battery_current | bcs1_ups_bat_current | Input Register | No | 18053 |  |  | 1 | uint16 | A | 10
UPS Line_voltage | bcs1_ups_in_volt | Input Register | Yes | 18054 |  |  | 1 | uint16 | V | 10
UPS Input_frequency | bsc1_ups_in_freq | Input Register | Yes | 18055 |  |  | 1 | uint16 | Hz | 10
UPS Output_voltage | bcs1_ups_out_volt | Input Register | No | 18056 |  |  | 1 | uint16 | V | 10
UPS Output_frequency | bcs1_ups_out_freq | Input Register | No | 18057 |  |  | 1 | uint16 | Hz | 100
UPS Output_current | bcs1_ups_out_current | Input Register | No | 18058 |  |  | 1 | uint16 | A | 100
UPS Output_load_percent | bcs1_ups_load_per | Input Register | Yes | 18059 |  |  | 1 | uint16 | % | 10
UPS P_battery_voltage | bcs1_ups_bat_volt | Input Register | No | 18060 |  |  | 1 | uint16 | V | 10
UPS_internal_temperature | bcs1_ups_internal_temp | Input Register | No | 18061 |  |  | 1 | uint16 | °C | 10
UPS_status_word_1 | bcs1_ups_status_1 | Input Register | Yes | 18062 |  |  | 1 | bitfield
UPS Failed |  | Input Register | Yes | 18062 |  | 4 |  | bit
Utility Fail |  | Input Register | Yes | 18062 |  | 7 |  | bit
UPS_status_word_2 | bcs1_ups_status_2 | Input Register | Yes | 18063 |  |  | 1 | bitfield
Battery Test Ok |  | Input Register | Yes | 18063 |  | 14 |  | bit
Battery Test Fail |  | Input Register | Yes | 18063 |  | 15 |  | bit
UPS Battery_capacity | bsc1_ups_soc | Input Register | Yes | 18064 |  |  | 1 | uint16 | % | 10
UPS_mode_inquiry | bcs1_ups_mode | Input Register | Yes | 18065 |  |  | 1 | bitfield
Power on mode |  | Input Register | Yes | 18065 |  | 0 |  | bit
Standby |  | Input Register | Yes | 18065 |  | 1 |  | bit
Bypass |  | Input Register | Yes | 18065 |  | 2 |  | bit
Line |  | Input Register | Yes | 18065 |  | 3 |  | bit
Battery |  | Input Register | Yes | 18065 |  | 4 |  | bit
Battery test |  | Input Register | Yes | 18065 |  | 5 |  | bit
Fault |  | Input Register | Yes | 18065 |  | 6 |  | bit
HE/ECO mode |  | Input Register | Yes | 18065 |  | 7 |  | bit
Converter |  | Input Register | Yes | 18065 |  | 8 |  | bit
Shutdown |  | Input Register | Yes | 18065 |  | 9 |  | bit
Meter Grid Freq | bsc1_grid_freq | Input Register | Yes | 18066 |  |  | 1 | uint16 | Hz | 100
Meter Active Power | bsc1_active_power | Input Register | Yes | 18067 |  |  | 2 | int32
Meter Reactive Power | bsc1_reactive_power | Input Register | Yes | 18069 |  |  | 2 | int32
Meter power factor | bsc1_power_factor | Input Register | Yes | 18071 |  |  | 1 | int16 |  | 1000
Meter KWh delivered | bcs1_kwh_delivered | Input Register | Yes | 18072 |  |  | 2 | uint32 | kWh
Meter KWh received | bcs1_kwh_received | Input Register | Yes | 18074 |  |  | 2 | uint32 | kWh
Meter KVARh delivered | bsc1_kvarh_delivered | Input Register | Yes | 18076 |  |  | 2 | uint32 | kVARh
Meter KVARh received | bsc1_kvarh_received | Input Register | Yes | 18078 |  |  | 2 | uint32 | kVARh
Rack Capcity | rack1_capacity | Input Register | Yes | 30000 |  |  | 1 | uint16 |  | 100
Rack Voltage | rack1_voltage | Input Register | Yes | 30001 |  |  | 1 | uint16 |  | 10
Rack Current | rack1_current | Input Register | Yes | 30002 |  |  | 1 | int16 |  | 10
Rack SOC | rack1_soc | Input Register | Yes | 30003 |  |  | 1 | uint16 |  | 100
Rack SOH | rack1_soh | Input Register | Yes | 30004 |  |  | 1 | uint16 |  | 100
Rack Service Voltage | rack1_service_voltage | Input Register | Yes | 30005 |  |  | 1 | uint16 |  | 10
Rack Service SOC | rack1_service_soc | Input Register | Yes | 30006 |  |  | 1 | uint16 |  | 100
Rack Sum of voltages | rack1_sum_of_volt | Input Register | Yes | 30007 |  |  | 1 | uint16 |  | 10
Rack Bus voltage | rack1_bus_volt | Input Register | Yes | 30008 |  |  | 1 | uint16 |  | 10
Rack Work status | rack1_work_status | Input Register | Yes | 30009 |  |  | 1 | uint16
Rack Max cell voltage | rack1_max_cell_volt | Input Register | Yes | 30010 |  |  | 1 | uint16 |  | 10
Rack Max cell voltage position | rack1_max_cell_volt_pos | Input Register | Yes | 30011 |  |  | 1 | uint16
Rack Min cell voltage | rack1_min_cell_volt | Input Register | Yes | 30012 |  |  | 1 | uint16 |  | 10
Rack Min cell voltage position | rack1_min_cell_volt_pos | Input Register | Yes | 30013 |  |  | 1 | uint16
Rack Max cell temperature | rack1_max_cell_temp | Input Register | Yes | 30014 |  |  | 1 | uint16 |  | 10
Rack Max cell temperature position | rack1_max_cell_temp_pos | Input Register | Yes | 30015 |  |  | 1 | uint16
Rack Min cell temperature | rack1_min_cell_temp | Input Register | Yes | 30016 |  |  | 1 | uint16 |  | 10
Rack Min cell temperature position | rack1_min_cell_temp_pos | Input Register | Yes | 30017 |  |  | 1 | uint16
Rack Average voltage | rack1_avg_volt | Input Register | Yes | 30018 |  |  | 1 | uint16 |  | 10
Rack Average temperature | rack1_avg_temp | Input Register | Yes | 30019 |  |  | 1 | uint16 |  | 10
Rack Insulation resistance | rack1_insul_res | Input Register | Yes | 30020 |  |  | 2 | uint32 |  | 10
Rack Max pulse charge current | rack1_max_pulse_charge_cur | Input Register | Yes | 30022 |  |  | 1 | uint16 |  | 10
Rack Max pulse discharge current | rack1_max_pulse_discharge_cur | Input Register | Yes | 30023 |  |  | 1 | uint16 |  | 10
Rack Max charge current | rack1_max_charge_cur | Input Register | Yes | 30024 |  |  | 1 | uint16 |  | 10
Rack Max discharge current | rack1_max_discharge_cur | Input Register | Yes | 30025 |  |  | 1 | uint16 |  | 10
Rack First alarm word | rack1_first_alarm | Input Register | Yes | 30026 |  |  | 2 | uint32
Rack Second alarm word | rack1_second_alarm | Input Register | Yes | 30028 |  |  | 2 | uint32
Rack Third alarm word | rack1_third_alarm | Input Register | Yes | 30030 |  |  | 2 | uint32
Rack Hardware State | rack1_hardware_state | Input Register | Yes | 30032 |  |  | 1 | uint16
Rack BMU comm chip number | rack1_bmu_comm_chip_num | Input Register | Yes | 30034 |  |  | 1 | uint16
Rack Pack exception id | rack1_pack_excp_id | Input Register | Yes | 30035 |  |  | 1 | uint16
RackVoltage exception id | rack1_volt_excp_id | Input Register | Yes | 30036 |  |  | 1 | uint16
Rack Temperature exception id | rack1_temp_excp_id | Input Register | Yes | 30037 |  |  | 1 | uint16
Rack Total cells number | rack1_total_cell_num | Input Register | Yes | 30040 |  |  | 1 | uint16
Rack Total temperature number | rack1_total_tem_num | Input Register | Yes | 30041 |  |  | 1 | uint16
Rack Charge/discharge Cycles | rack1_charge_discharge_cycles | Input Register | Yes | 30042 |  |  | 2 | uint32 |  | 10
Rack Fan start temperature | rack1_fan_start_temp | Input Register | Yes | 30045 |  |  | 1 | uint16 |  | 10
Rack Fan stop temperature | rack1_fan_stop_temp | Input Register | Yes | 30046 |  |  | 1 | uint16 |  | 10
Rack Board temperature | rack1_board_temp | Input Register | Yes | 30047 |  |  | 1 | uint16 |  | 10
Rack Power voltage | rack1_power_volt | Input Register | Yes | 30048 |  |  | 1 | uint16 |  | 10
Rack Ambient temperature 1 | rack1_amb_temp_1 | Input Register | Yes | 30051 |  |  | 1 | uint16 |  | 10
Rack Ambient temperature 2 | rack1_amb_temp_2 | Input Register | Yes | 30052 |  |  | 1 | uint16 |  | 10
Rack BCU reset type | rack1_bcu_reset_type | Input Register | Yes | 30053 |  |  | 1 | uint16
Rack Inside voltage(signed) | rack1_inside_volt | Input Register | Yes | 30054 |  |  | 1 | uint16 |  | 10
Rack Bus voltage(signed) | rack1_bus_volt_signed | Input Register | Yes | 30055 |  |  | 1 | uint16 |  | 10
Rack Voltage sign | rack1_volt_sign | Input Register | Yes | 30056 |  |  | 1 | uint16
Rack Bus Voltage sign | rack1_bus_volt_sign | Input Register | Yes | 30057 |  |  | 1 | uint16
Rack Max cell capacity | rack1_max_cell_cap | Input Register | Yes | 30060 |  |  | 1 | uint16 |  | 100
Rack Min cell capacity | rack1_min_cell_cap | Input Register | Yes | 30061 |  |  | 1 | uint16 |  | 100
Rack Calc SOC | rack1_calc_soc | Input Register | Yes | 30062 |  |  | 1 | uint16 |  | 100
Rack Max pack voltage | rack1_max_pack_volt | Input Register | Yes | 30064 |  |  | 1 | uint16
Rack Min pack voltage | rack1_min_pack_volt | Input Register | Yes | 30065 |  |  | 1 | uint16
Rack Max pack voltage position | rack1_max_pack_volt_pos | Input Register | Yes | 30066 |  |  | 1 | uint16
Rack Min pack voltage position | rack1_min_pack_volt_pos | Input Register | Yes | 30067 |  |  | 1 | uint16
Rack Total charge power | rack1_total_charge_power | Input Register | Yes | 30089 |  |  | 2 | uint32
Rack Total discharge power | rack1_total_discharge_power | Input Register | Yes | 30091 |  |  | 2 | uint32
Rack Total charge capacity | rack1_total_charge_cap | Input Register | Yes | 30093 |  |  | 2 | uint32 |  | 10
Rack Total discharge capacity | rack1_total_discharge_cap | Input Register | Yes | 30095 |  |  | 2 | uint32 |  | 10
Rack Software version | rack1_software_version | Input Register | Yes | 30097 |  |  | 2 | uint32
Rack id | rack1_id | Input Register | Yes | 30099 |  |  | 1 | uint16
rack1 | rack2 |  | Yes | 30100 | 30000 |  | 100 | repeat
rack1 | rack3 |  | Yes | 30200 | 30000 |  | 100 | repeat
rack1 | rack4 |  | Yes | 30300 | 30000 |  | 100 | repeat
rack1 | rack5 |  | Yes | 30400 | 30000 |  | 100 | repeat
rack1 | rack6 |  | Yes | 30500 | 30000 |  | 100 | repeat
rack1 | rack7 |  | Yes | 30600 | 30000 |  | 100 | repeat
rack1 | rack8 |  | Yes | 30700 | 30000 |  | 100 | repeat